{"text_format":"1","workbook":"xlsx","n_sheets":12,"sheets":["Auslegetool","Legende","Legende_Abkürzungen","Rohdaten_Messwerte_Kühlen","Auswertung_Leistung","BG;WT2,5;k","BG;WT2,5;k 100kg_h","BG;WT2,5;h","Auslegung_BG800_kondensierend","Eurocoil","Ausw_Vergleich_sf_vs_S5","Tabelle2"],"not_rendered":{"charts":64,"images":18,"macros":1,"external_links":2,"defined_names":84,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Auslegetool","index":0,"n_rows":100,"n_cols":90,"rows_kept":100,"cut":false,"hidden":false,"merged":[[61,0,62,0],[1,45,1,48],[7,7,7,8],[4,7,4,10],[23,0,24,0],[42,0,43,0]]}
[null,"  Tel.  +49 (0)711 8201-100   Fax: -720",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Email:","Raumluft@LTG.de",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(AND(IF(OR(C45<C56,C46<C56,C52<C56,C53<C56,C45>C57,C46>C57,C52>C57,C53>C57),,),COUNT(C45:C53)=4),\"Grenzwerte\",\"\")","v":""},"Primärdruck","Primärvol.","Volumenstrom","Drehzahl",null,null,null,null,null,"Auslegung  ",1,2,3,4,null,"Raumluft","Passwort eingeben, um Adminbereich einzublenden",null,null,{"$f":"AV21","v":"Baugröße 630"},null,null,{"$f":"CONCATENATE(X6,\"  -  nicht kondensierend - \",I17,\" \",J17,\" \", K17)","v":"Baugröße 800  -  nicht kondensierend - Primärdruck 120 Pa"},{"$f":"IF(BL1=BM1,1,IF(BL2=BM1,2,IF(BL3=BM1,3,IF(BL4=BM1,4,0))))","v":1},"Deutsch","Deutsch",null,"Akustik-Zielwertsuche ausführen","Volumenströme zurücksetzen",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Vergleich, ob für Enthalphieberechnung Taupunkttemperatur Ansaug genommen werden kann"]
[null,"LTG Aktiengesellschaft ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Abfrage",1,"2-Leiter",null,null,null,null,null,null,null,null,null,null,"[Pa]","[m³/h]","[m³/h]","[1/min]",null,null,"Sollwert Schallleistungspegel LWA [dB(A)]           ",null,null,null,35,40,45,50,null,null,"Dialogaufforderung","In Inputbox eingetragener Text",null,{"$f":"AV40","v":"Baugröße 800"},null,null,{"$f":"CONCATENATE(X6,\"  -  kondensierend - \",I17,\" \",J17,\" \", K17)","v":"Baugröße 800  -  kondensierend - Primärdruck 120 Pa"},null,"Englisch",null,null,"calculate: target value (acoustic)","reset flow rates",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Wasservorlauf",5]
[null,{"$f":"Y3","v":"Auslegetool: HFBsf, 4L, "},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"CONCATENATE(Y5,\": \",Y6,\", \",Y7,\", \", Y8,Y9,Y10)","v":"Auslegetool: HFBsf, 4L, "},null,null,2,"4-Leiter",null,null,null,null,null,null,null,null,null,null,"Pa","m³/h",null,null,null,null,null,null,0,1,2,3,4,5,6,7,8,9,10,{"$f":"AV59","v":"Baugröße 1000"},null,null,{"$f":"CONCATENATE(X6,\"  - \",I17,\" \",J17,\" \", K17)","v":"Baugröße 800  - Primärdruck 120 Pa"},null,"Franzoesisch",null,null,"calculate: target value (acoustic)","réinitialiser le volume des flux",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"rF",50]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF($X$6=$BG$1,AV21,IF($X$6=$BG$2,AV40,IF($X$6=$BG$3,AV59,0)))","v":"Baugröße 800"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Italienisch",null,null,"calculate: target value (acoustic)","ripristino del volume dei flussi"]
[null,null,null,null,null,null,null,"Kühlfall:",null,null,null,null,null,null,"Heizfall:",null,null,null,null,null,null,null,null,"Diagramme","Auslegetool","mit Filter ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF($X$6=$BG$1,AV22,IF($X$6=$BG$2,AV41,IF($X$6=$BG$3,AV60,0)))","v":"Schieberstellung"},{"$f":"IF($X$6=$BG$1,AW22,IF($X$6=$BG$2,AW41,IF($X$6=$BG$3,AW60,0)))","v":"QPK Primärleistung"},"QSK1) Sekundärleistung","QKges1) Gesamtleistung","QSK2) Sekundärleistung","QKges2) Gesamtleistung","QPH Primärleistung","QSH Sekundärleistung","QGes Gesamtleistung","LWA - Schallleistung",null,"Abfrage",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Torr",760]
[null,"Projekt:",null,null,null,null,null,null,"Ansaugtemperatur:",26,"°C",null,null,null,null,"Ansaugtemperatur:",20,"°C",null,null,null,null,null,"Baugröße 800","HFBsf","ohne Filter",null,"Auslegungsgrenzen",null,null,null,null,null,null,null,null,null,null,null,null,null,"Auslegetool","Abfrage",null,null,"Tabellenblatt",null,{"$f":"IF($X$6=$BG$1,AV23,IF($X$6=$BG$2,AV42,IF($X$6=$BG$3,AV61,0)))","v":0},{"$f":"IF($X$6=$BG$1,AW23,IF($X$6=$BG$2,AW42,IF($X$6=$BG$3,AW61,0)))","v":0},0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,null,null,"Kühlwasservorlauf ¹:",16,"°C",null,null,null,null,"Heizwasservorlauf:",60,"°C",null,null,null,null,null,null,{"$f":"IF(AN11=2,\"4L\",\"2L\")","v":"4L"},"mit 3D-Strömung",null,null,"T_Ansaug","T_Vorlauf","T_Vorlauf2","rF [%]",null,null,null,null,null,null,2,null,1,"Volumenstrom vorgeben",2,null,null,{"$f":"MID(CELL(\"dateiname\",B1),FIND(\"]\",CELL(\"dateiname\",B1))+1,255)","v":"Auslegetool"},null,{"$f":"IF($X$6=$BG$1,AV24,IF($X$6=$BG$2,AV43,IF($X$6=$BG$3,AV62,0)))","v":"Schieberstellung"},{"$f":"IF($X$6=$BG$1,AW24,IF($X$6=$BG$2,AW43,IF($X$6=$BG$3,AW62,0)))","v":"QPK"},"QSK1)","QKges1)","QSensibel,K2)","QKges2)","QPH","QSH","Qhges","LWA",{"$f":"IF($X$6=$BG$1,BF24,IF($X$6=$BG$2,BF43,IF($X$6=$BG$3,BF62,0)))","v":"QKges2) ; QKges1)"},"Zeile","Zeile","Spalte",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Volumenstrom","Taupunkt Ansaug","Taupunkt im Kasten"]
[null,"Datum:",null,null,null,null,null,"Kühlwasservorlauf \nkondensierender Betrieb ²:",null,6,"°C",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"ohne 3D-Strömung","Taupunkt Ansaugbed.","Kühlfall",null,null,null,null,null,null,null,null,null,null,false,{"$f":"IF(AM8=TRUE,1,2)","v":2},2,"Druck vorgeben",null,null,null,null,null,{"$f":"IF($X$6=$BG$1,AV25,IF($X$6=$BG$2,AV44,IF($X$6=$BG$3,AV63,0)))","v":0},{"$f":"IF($X$6=$BG$1,AW25,IF($X$6=$BG$2,AW44,IF($X$6=$BG$3,AW63,0)))","v":"[W]"},"[W]","[W]","[W]","[W]","[W]","[W]","[W]","[dB(A)]",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"[m³/h]","[°C]","[°C]"]
[null,"Bearbeiter:",null,null,null,null,null,null,"relative Feuchte ²:",50,"%",null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(AM9=TRUE,L_mit3D,\"\")","v":""},"mit Schalldämmung","[°C]","Minimal",{"$f":"Auslegung_BG800_kondensierend!O115","v":21},16,{"$f":"Auslegung_BG800_kondensierend!Q115","v":3},{"$f":"Auslegung_BG800_kondensierend!R115","v":1},null,null,null,null,null,null,false,{"$f":"IF(AM9=TRUE,1,2)","v":2},null,null,null,null,null,null,"Für Diagramme -> Damit keine Fehlermeldung auftritt (Dias brauchen immer einen Wert)",1,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF($X$6=$BG$1,BH26,IF($X$6=$BG$2,BH45,IF($X$6=$BG$3,BH64,0)))","v":45},48,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,55.342684999032826,7.2329292237053755,7.2887355734611026]
[null,null,null,null,null,null,null,null,"projektierte Leistung:",0,"W",null,null,null,null,"projektierte Leistung:",null,"W",null,null,null,null,null,null,{"$f":"IF(AM10=TRUE,L_mitSchalld,\"\")","v":""},"ohne Schalldämmung",{"$f":"BM36","v":{"$error":"#NAME?"}},"Maximal",{"$f":"Auslegung_BG800_kondensierend!O116","v":27},24,{"$f":"Auslegung_BG800_kondensierend!Q116","v":16},{"$f":"Auslegung_BG800_kondensierend!R116","v":99},null,null,null,null,null,null,false,{"$f":"IF(AM10=TRUE,1,2)","v":2},null,null,null,null,null,null,null,{"$f":"IFERROR(CELL(\"inhalt\",INDIRECT(ADDRESS($BH9,$BI9+AV$3))),\"\")","v":5},220,411.34218578828666,631.34218578828666,765.66570947044033,985.66570947044033,0,883.73923223201757,883.73923223201757,{"$f":"IF(IFERROR(CELL(\"inhalt\",INDIRECT(ADDRESS($BH9,$BI9+BE$3))),\"\")=\"<20\",20,IFERROR(CELL(\"inhalt\",INDIRECT(ADDRESS($BH9,$BI9+BE$3))),\"\"))","v":28.283110685239627},{"$f":"IFERROR(CELL(\"inhalt\",INDIRECT(ADDRESS($BH9,$BI9+BF$3))),\"\")","v":"986W ; 631W"},null,46,48,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,109.52496612838792,9.0297886996492558,9.0598194704293746]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(AN11=1,TRUE,FALSE)","v":false},{"$f":"IF(C15=AC2,AB2,AB3)","v":2},null,null,null,null,null,null,null,{"$f":"IFERROR(CELL(\"inhalt\",INDIRECT(ADDRESS($BH11,$BI11+AV$3))),\"\")","v":4},160,263.03715133112354,423.03715133112354,501.99928693459094,661.99928693459094,0,629.03263291018038,629.03263291018038,{"$f":"IF(IFERROR(CELL(\"inhalt\",INDIRECT(ADDRESS($BH11,$BI11+BE$3))),\"\")=\"<20\",20,IFERROR(CELL(\"inhalt\",INDIRECT(ADDRESS($BH11,$BI11+BE$3))),\"\"))","v":26.913996752316265},{"$f":"IFERROR(CELL(\"inhalt\",INDIRECT(ADDRESS($BH11,$BI11+BF$3))),\"\")","v":"662W ; 423W"},null,47,48,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,163.26007066195126,10.208611359902919,10.226491431651684]
[null,null,null,null,null,null,null,null,"Nennwassermenge:",200,"kg/h",null,null,null,null,"Nennwassermenge:",100,"kg/h",null,null,null,null,null,null,null,null,null,"Heizfall",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IFERROR(CELL(\"inhalt\",INDIRECT(ADDRESS($BH13,$BI13+AV$3))),\"\")","v":3},110,216.2034877106791,326.2034877106791,414.68911569683991,524.68911569683996,0,529.8342994009106,529.8342994009106,{"$f":"IF(IFERROR(CELL(\"inhalt\",INDIRECT(ADDRESS($BH13,$BI13+BE$3))),\"\")=\"<20\",20,IFERROR(CELL(\"inhalt\",INDIRECT(ADDRESS($BH13,$BI13+BE$3))),\"\"))","v":28.350831416141009},{"$f":"IFERROR(CELL(\"inhalt\",INDIRECT(ADDRESS($BH13,$BI13+BF$3))),\"\")","v":"525W ; 326W"},null,48,48,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,216.72807000733741,11.028203519575097,11.039641507117626]
[null,null,null,null,null,null,null,null,"Wassermenge Kühlen:",200,"kg/h",null,null,null,null,"Wassermenge Heizen:",100,"kg/h",null,null,null,null,null,null,null,null,null,"Minimal",19,30,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IFERROR(CELL(\"inhalt\",INDIRECT(ADDRESS($BH15,$BI15+AV$3))),\"\")","v":2},50,124.80288994803732,174.80288994803732,241.54867778231417,291.54867778231414,0,320.44787291335092,320.44787291335092,{"$f":"IF(IFERROR(CELL(\"inhalt\",INDIRECT(ADDRESS($BH15,$BI15+BE$3))),\"\")=\"<20\",20,IFERROR(CELL(\"inhalt\",INDIRECT(ADDRESS($BH15,$BI15+BE$3))),\"\"))","v":20.854605102651437},{"$f":"IFERROR(CELL(\"inhalt\",INDIRECT(ADDRESS($BH15,$BI15+BF$3))),\"\")","v":"292W ; 175W"},null,49,48]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Maximal",27,80,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,50,48]
[null,"Wärmetauscher:","4-Leiter",null,null,null,null,null,"Raumtemperatur",26,"°C",null,null,null,null,"Raumtemperatur",20,"°C",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,51,48]
[null,null,null,null,null,null,null,null,"Primärlufttemperatur",18,"°C",null,null,null,null,"Primärlufttemperatur",20,"°C"]
[null,null,null,null,null,null,null,null,{"$f":"C24","v":"Primärdruck"},120,{"$f":"IF($AQ$7=1,$AO$3,$AN$3)","v":"Pa"},null,null,null,null,{"$f":"C24","v":"Primärdruck"},{"$f":"J17","v":120},{"$f":"K17","v":"Pa"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"INDIRECT(\"BB\"&12)","v":0}]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"L_BG630","v":"Baugröße 630"}]
[null,"Baugröße 630",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"lt. Wikipedia 15-20ml / Tropfen",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Schieberstellung","QPK Primärleistung","QSK1) Sekundärleistung","QKges1) Gesamtleistung","QSK2) Sekundärleistung","QKges2) Gesamtleistung","QPH Primärleistung","QSH Sekundärleistung","QGes Gesamtleistung","LWA - Schallleistung",null,null,null,null,null,null,null,null,null,null,{"$f":"Torr_in_Pa(760)","v":{"$error":"#NAME?"}}]
[]
["Auswahl","Schieberstellung",{"$f":"IF($AQ$7=1,$AO$1,$AN$1)","v":"Primärdruck"},{"$f":"IF($AQ$7=2,$AO$1,$AN$1)","v":"Primärvol."},{"$f":"L_primaervol","v":"Primärvol."},{"$f":"L_primaerdruck","v":"Primärdruck"},"Sekundärvolumenstrom","LWA","LA18","QPK","QSK1","QKges1","QTotal2","QSensibel,K2","QKges2","QPH","QSH","Qhges","tKWRL","tKWRL2","tWWRL","Kondensat ²","Zulufttemp.²",null,"Tropfen","Zulufttemp.","Taupunkt nach WT","qSK1)","qSH","qSK2)","qtotal2)",{"$f":"Auswertung_Leistung!AD274","v":"Primärdruck Baugröße 800; S5"},null,{"$f":"Auswertung_Leistung!AF274","v":"Kühlleistung \"mit\" Schieber im Vergleich zu \"ohne Schieber\""},"Primärvolumenstrom Minimal","Primärvolumenstrom Minimal","Primärdruck Minimal","Primärdruck Maximal",null,null,null,null,null,null,null,null,null,"Schieberstellung","QPK","QSK1)","QKges1)","QSensibel,K2)","QKges2)","QPH","QSH","Qhges","LWA","QKges2) ; QKges1)","Zeile","Zeile","Spalte",null,null,"Randparameter:",null,null,null,null,"Wassermenge Gesamt in der Luft","latente \nLeistung","Verdampfungsenthalpie",null,null,"Kondensatmenge","Volumenstrom Wasser (Ansaug)","Volumenstrom Luft (Ansaug)","Masse Luft","Masse Wasser (im Volumenstrom) - Kasten","Zulufttemperatur","Dichte Luft (Kasten)","Dichte Wasser (Kasten)","Volumenstrom Luft","Volumenstrom Wasser","Massenstrom Kasten","Volumenstrom Kasten","Dichte Misch(Kasten)","phi_x (kg_H20/kg_Gesamt Wassergehalt)","Feuchte nach WT (Kasten)","Taupunkt im Kasten"]
[null,null,{"$f":"IF($AQ$7=1,$AO$2,$AN$2)","v":"[Pa]"},{"$f":"IF($AQ$7=2,$AO$2,$AN$2)","v":"[m³/h]"},"[m³/h]","[Pa]","[m³/h]","[dB(A)]","[dB(A)]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[°C]","[°C]","[°C]","[kg/h] bzw. [l / h]","[°C]",null,"[Anzahl / min]",{"$f":"CA25","v":"[°C]"},"[°C]","[W]","[W]","[W]","[W]",{"$f":"Auswertung_Leistung!AD275","v":"[Pa]"},null,{"$f":"Auswertung_Leistung!AF275","v":0},"[m³/h]","[m³/h]","[m³/h]","[m³/h]","Grenzen der Auslegung",null,null,"Abhängig von Abfrage",null,null,null,"heizen",null,null,"[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[dB(A)]",null,null,null,null,null,null,"rel. Feuchte",{"$f":"J9","v":50},"%",null,null,"kg H20 / h","W bzw. J / s","kJ/mol","kJ/g","J/kg","kg / h bzw.l / h","[m³/h]","[m³/h]","[kg/h]","[kg/h]","[°C]","[kg/m³]","[kg/m³]","[m³/h]","[m³/h]","[kg/h]","[m³/h]","[kg/m³]",null,"rF [%]","[°C]"]
["x",5,{"$f":"$J$17","v":120},{"$f":"Auswertung_Leistung!C276","v":58.086531680690612},{"$f":"IF(C26=\"\",\"\",IF($AQ$7=1,C26,D26))","v":58.086531680690612},{"$f":"Auswertung_Leistung!H276","v":120},{"$f":"Auswertung_Leistung!K276","v":118.01757823392964},{"$f":"IFERROR(IF(OR(C26=\"\",C26=0,Auswertung_Leistung!T276<20),\"<20\",Auswertung_Leistung!T276),\"\")","v":26.853492277823904},{"$f":"IFERROR(IF(C26=\"\",\"\",H26-6.5),\"\")","v":20.353492277823904},{"$f":"ROUND(E26*1.2*1004.5*($J$16-$J$15)/3600,-1)","v":-160},{"$f":"IF(C26=\"\",\"\",IF(C26=0,,IFERROR((AB26*($J$7-$J$6)),\"\")))","v":-299.39716205419859},{"$f":"J26+K26","v":-459.39716205419859},{"$f":"IFERROR(AE26*($J$8-$J$6),\"\")","v":-850.50279170887234},{"$f":"IFERROR(AD26*($J$8-$J$6),\"\")","v":-557.29304802121783},{"$f":"J26+N26","v":-717.29304802121783},{"$f":"ROUND(E26*1.2*1004.5*($Q$16-$Q$15)/3600,-1)","v":0},{"$f":"IF(G26=0,,IFERROR((AC26*($Q$7-$Q$6)),\"\"))","v":639.79074904450044},{"$f":"Q26+P26","v":639.79074904450044},{"$f":"IF(IFERROR(IF(K26=0,,$J$7-((K26/(4.2*$J$13/3.6)))),)=0,\"\",IFERROR(IF(K26=0,,$J$7-((K26/(4.2*$J$13/3.6)))),))","v":17.283130694517993},{"$f":"IF(IFERROR(IF(N26=0,,$J$8-((N26/(4.2*$J$13/3.6)))),)=0,\"\",IFERROR(IF(N26=0,,$J$8-((N26/(4.2*$J$13/3.6)))),))","v":8.3883987772337907},{"$f":"IF(C26=\"\",\"\",IFERROR(IF(Q26=0,,($Q$7-((Q26/(4.2*$Q$13/3.6))))),))","v":54.516079293904284},{"$f":"IFERROR(BV26,\"\")","v":0.42504750072201508},{"$f":"Z26","v":11.833643012486473},null,{"$f":"IFERROR(V26*1000/15/60,\"\")","v":0.47227500080223894},{"$f":"IFERROR(CA26,\"\")","v":11.833643012486473},{"$f":"IFERROR(CK26,\"\")","v":""},{"$f":"Auswertung_Leistung!Q276","v":29.93971620541986},{"$f":"IF($AN$11=1,AB26*Auswertung_Leistung!Y276,AB26*Auswertung_Leistung!AB276)","v":15.994768726112511},{"$f":"Auswertung_Leistung!R276","v":27.864652401060891},{"$f":"Auswertung_Leistung!S276","v":42.525139585443618},{"$f":"Auswertung_Leistung!AD276","v":120.00162820198784},null,{"$f":"Auswertung_Leistung!AF276","v":-7.488003676781041E-6},{"$f":"Auswertung_Leistung!U276","v":35.829612208091895},{"$f":"Auswertung_Leistung!V276","v":91.968255671508004},{"$f":"Auswertung_Leistung!W276","v":45},{"$f":"Auswertung_Leistung!X276","v":305},{"$f":"$AM$96","v":"Primärdurck"},"Primärvolumenstrom",{"$f":"$AO$96","v":"Wassermassenstrom"},{"$f":"IF($AQ$7=1,AN26,AM26)","v":"Primärdurck"},"Einheit",{"$f":"IF($AQ$7=2,AN26,AM26)","v":"Primärvolumenstrom"},"Einheit",{"$f":"$AO$96","v":"Wassermassenstrom"},null,{"$f":"IF(OR(F26<$AM$27,F26>$AM$28),\"\",B26)","v":5},{"$f":"IF(AV26=\"\",\"\",ABS(J26))","v":160},{"$f":"IF(AV26=\"\",\"\",ABS(K26))","v":299.39716205419859},{"$f":"IF(AV26=\"\",\"\",ABS(L26))","v":459.39716205419859},{"$f":"IF(AV26=\"\",\"\",ABS(N26))","v":557.29304802121783},{"$f":"IF(AV26=\"\",\"\",(AW26+AZ26))","v":717.29304802121783},{"$f":"IF(AV26=\"\",\"\",(P26))","v":0},{"$f":"IF(AV26=\"\",\"\",ABS(Q26))","v":639.79074904450044},{"$f":"IF(AV26=\"\",\"\",(BB26+BC26))","v":639.79074904450044},{"$f":"IF(AV26=\"\",\"\",H26)","v":26.853492277823904},{"$f":"IF(AV26=\"\",\"\",CONCATENATE(ROUND(BA26,0),\" ; \",ROUND(AY26,0)))","v":"717 ; 459"},{"$f":"IF(AV26=\"\",\"\",ROW(AV26))","v":26},{"$f":"MIN(BG26:BG34)","v":26},{"$f":"COLUMN(AV26)","v":48},null,null,"Druck",760,"Torr",null,null,{"$f":"$BM$37*(G26*$BM$28)","v":{"$error":"#NAME?"}},{"$f":"M26-N26","v":-293.20974368765451},{"$f":"50.09-0.9298*(273.15+$J$8)/1000-65.19*((273.15+$J$8)/1000)^2","v":44.750533670225003},{"$f":"BS26/$BM$31","v":2.4833814467383464},{"$f":"BT26*1000000","v":2483381.4467383465},{"$f":"ABS(BR26)/BU26*3600","v":0.42504750072201508},{"$f":"BQ26/$BM$53","v":{"$error":"#NAME?"}},{"$f":"G26-BW26","v":{"$error":"#NAME?"}},{"$f":"BX26*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BQ26-BV26","v":{"$error":"#NAME?"}},{"$f":"N26*3/G26+$BM$27","v":11.833643012486473},{"$f":"dichteLuft(0,Torr_in_Pa($BM$26),CA26)","v":{"$error":"#NAME?"}},{"$f":"999.972-7*10^(-3)*(CA26-4)^2","v":999.54243826007041},{"$f":"BY26/CB26*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BZ26/CC26*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BZ26+BY26","v":{"$error":"#NAME?"}},{"$f":"CD26+CE26","v":{"$error":"#NAME?"}},{"$f":"CF26/CG26","v":{"$error":"#NAME?"}},{"$f":"BZ26/CG26/CH26","v":{"$error":"#NAME?"}},{"$f":"rf_prozent_von_T_grad_x_hf_gH2O_kg_trLuft(CA26,CI26*1000)","v":{"$error":"#NAME?"}},{"$f":"td_T_grad_rf_prozent(CA26,CJ26)","v":{"$error":"#NAME?"}}]
[null,4.5,{"$f":"C26","v":120},{"$f":"Auswertung_Leistung!C277","v":69.753007157474343},69.753007157474343,{"$f":"Auswertung_Leistung!H277","v":120},{"$f":"Auswertung_Leistung!K277","v":111.44906175414548},{"$f":"IFERROR(IF(OR(C27=\"\",C27=0,Auswertung_Leistung!T277<20),\"<20\",Auswertung_Leistung!T277),\"\")","v":26.599994934706302},{"$f":"IFERROR(IF(C27=\"\",\"\",H27-6.5),\"\")","v":20.099994934706302},{"$f":"ROUND(E27*1.2*1004.5*($J$16-$J$15)/3600,-1)","v":-190},-274.95681122999667,{"$f":"J27+K27","v":-464.95681122999667},{"$f":"IFERROR(AE27*($J$8-$J$6),\"\")","v":-787.22444979246643},{"$f":"IFERROR(AD27*($J$8-$J$6),\"\")","v":-513.52169091178416},{"$f":"J27+N27","v":-703.52169091178416},0,593.64055462779368,{"$f":"Q27+P27","v":593.64055462779368},17.178386333842845,8.2008072467647892,54.911652388904628,{"$f":"IFERROR(BV27,\"\")","v":0.39676946659345491},{"$f":"Z27","v":12.176957899082094},null,{"$f":"IFERROR(V27*1000/15/60,\"\")","v":0.44085496288161663},{"$f":"IFERROR(CA27,\"\")","v":12.176957899082094},{"$f":"IFERROR(CK27,\"\")","v":""},{"$f":"Auswertung_Leistung!Q277","v":27.495681122999667},{"$f":"IF($AN$11=1,AB27*Auswertung_Leistung!Y277,AB27*Auswertung_Leistung!AB277)","v":14.841013865694842},{"$f":"Auswertung_Leistung!R277","v":25.676084545589205},{"$f":"Auswertung_Leistung!S277","v":39.361222489623323},{"$f":"Auswertung_Leistung!AD277","v":173.99655111742987},null,{"$f":"Auswertung_Leistung!AF277","v":-0.22944094679366123},{"$f":"Auswertung_Leistung!U277","v":42.376630030042996},{"$f":"Auswertung_Leistung!V277","v":112.04833567755138},{"$f":"Auswertung_Leistung!W277","v":45},{"$f":"Auswertung_Leistung!X277","v":305},{"$f":"AM97","v":45},{"$f":"MIN(AI26:AI34)","v":8.1988950705672679},{"$f":"AO97","v":50},{"$f":"IF($AQ$7=1,AN27,AM27)","v":45},{"$f":"IF($AQ$7=1,\"m³/h\",\"Pa\")","v":"Pa"},{"$f":"IF($AQ$7=2,AN27,AM27)","v":8.1988950705672679},{"$f":"IF($AQ$7=2,\"m³/h\",\"Pa\")","v":"m³/h"},{"$f":"AT97","v":50},null,{"$f":"IF(OR(F27<$AM$27,F27>$AM$28),\"\",B27)","v":4.5},{"$f":"IF(AV27=\"\",\"\",ABS(J27))","v":190},{"$f":"IF(AV27=\"\",\"\",ABS(K27))","v":274.95681122999667},{"$f":"IF(AV27=\"\",\"\",ABS(L27))","v":464.95681122999667},{"$f":"IF(AV27=\"\",\"\",ABS(N27))","v":513.52169091178416},{"$f":"IF(AV27=\"\",\"\",(AW27+AZ27))","v":703.52169091178416},{"$f":"IF(AV27=\"\",\"\",(P27))","v":0},{"$f":"IF(AV27=\"\",\"\",ABS(Q27))","v":593.64055462779368},{"$f":"IF(AV27=\"\",\"\",(BB27+BC27))","v":593.64055462779368},26.599994934706302,{"$f":"IF(AV27=\"\",\"\",CONCATENATE(ROUND(BA27,0),\" ; \",ROUND(AY27,0)))","v":"704 ; 465"},{"$f":"IF(AV27=\"\",\"\",ROW(AV27))","v":27},{"$f":"IF(COUNTIF($BG$26:$BG$34,BH26+1)=1,BH26+1,IF(COUNTIF($BG$26:$BG$34,BH26+2)=1,BH26+2,IF(COUNTIF($BG$26:$BG$34,BH26+3)=1,BH26+3,IF(COUNTIF($BG$26:$BG$34,BH26+4)=1,BH26+4,IF(COUNTIF($BG$26:$BG$34,BH26+5)=1,BH26+5,IF(COUNTIF($BG$26:$BG$34,BH26+6)=1,BH26+6,IF(COUNTIF($BG$26:$BG$34,BH26+7)=1,BH26+7,IF(COUNTIF($BG$26:$BG$34,BH26+8)=1,BH26+8,\"\"))))))))","v":27},{"$f":"COLUMN(AV27)","v":48},null,null,"(Ansaug) Temperatur",{"$f":"J6","v":26},"°C",null,null,{"$error":"#NAME?"},{"$f":"M27-N27","v":-273.70275888068227},{"$f":"50.09-0.9298*(273.15+$J$8)/1000-65.19*((273.15+$J$8)/1000)^2","v":44.750533670225003},{"$f":"BS27/$BM$31","v":2.4833814467383464},{"$f":"BT27*1000000","v":2483381.4467383465},{"$f":"ABS(BR27)/BU27*3600","v":0.39676946659345491},{"$f":"BQ27/$BM$53","v":{"$error":"#NAME?"}},{"$error":"#NAME?"},{"$f":"BX27*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BQ27-BV27","v":{"$error":"#NAME?"}},12.176957899082094,{"$error":"#NAME?"},{"$f":"999.972-7*10^(-3)*(CA27-4)^2","v":999.50396151661641},{"$f":"BY27/CB27*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BZ27/CC27*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BZ27+BY27","v":{"$error":"#NAME?"}},{"$f":"CD27+CE27","v":{"$error":"#NAME?"}},{"$f":"CF27/CG27","v":{"$error":"#NAME?"}},{"$f":"BZ27/CG27/CH27","v":{"$error":"#NAME?"}},{"$f":"rf_prozent_von_T_grad_x_hf_gH2O_kg_trLuft(CA27,CI27*1000)","v":{"$error":"#NAME?"}},{"$f":"td_T_grad_rf_prozent(CA27,CJ27)","v":{"$error":"#NAME?"}}]
[null,4,{"$f":"C27","v":120},{"$f":"Auswertung_Leistung!C278","v":43.732137109665416},43.732137109665416,{"$f":"Auswertung_Leistung!H278","v":120},{"$f":"Auswertung_Leistung!K278","v":71.178741354162071},{"$f":"IFERROR(IF(OR(C28=\"\",C28=0,Auswertung_Leistung!T278<20),\"<20\",Auswertung_Leistung!T278),\"\")","v":25.484378344900541},{"$f":"IFERROR(IF(C28=\"\",\"\",H28-6.5),\"\")","v":18.984378344900541},-120,-192.29105929847771,-312.29105929847771,-577.11870363873777,-366.98228430179608,-486.98228430179608,0,444.5251689504056,444.5251689504056,16.824104539850619,7.5727812184362691,56.189784266139384,{"$f":"IFERROR(BV28,\"\")","v":0.30462139056670473},10.532645113413317,null,{"$f":"IFERROR(V28*1000/15/60,\"\")","v":0.33846821174078306},{"$f":"IFERROR(CA28,\"\")","v":10.532645113413317},{"$f":"IFERROR(CK28,\"\")","v":""},{"$f":"Auswertung_Leistung!Q278","v":19.229105929847769},{"$f":"IF($AN$11=1,AB28*Auswertung_Leistung!Y278,AB28*Auswertung_Leistung!AB278)","v":11.11312922376014},{"$f":"Auswertung_Leistung!R278","v":18.349114215089806},{"$f":"Auswertung_Leistung!S278","v":28.855935181936886},{"$f":"Auswertung_Leistung!AD278","v":67.444862186503812},null,{"$f":"Auswertung_Leistung!AF278","v":-6.606990840132354E-2},{"$f":"Auswertung_Leistung!U278","v":26.356312056141046},{"$f":"Auswertung_Leistung!V278","v":70.786819893433403},{"$f":"Auswertung_Leistung!W278","v":45},{"$f":"Auswertung_Leistung!X278","v":305},{"$f":"AM98","v":305},{"$f":"MAX(AJ26:AJ34)","v":112.04833567755138},{"$f":"AO98","v":300},{"$f":"IF($AQ$7=1,AN28,AM28)","v":305},{"$f":"IF($AQ$7=1,\"m³/h\",\"Pa\")","v":"Pa"},{"$f":"IF($AQ$7=2,AN28,AM28)","v":112.04833567755138},{"$f":"IF($AQ$7=2,\"m³/h\",\"Pa\")","v":"m³/h"},{"$f":"AT98","v":300},null,4,120,192.29105929847771,312.29105929847771,366.98228430179608,486.98228430179608,0,444.5251689504056,444.5251689504056,25.484378344900541,"487 ; 312",{"$f":"IF(AV28=\"\",\"\",ROW(AV28))","v":28},{"$f":"IF(COUNTIF($BG$26:$BG$34,BH27+1)=1,BH27+1,IF(COUNTIF($BG$26:$BG$34,BH27+2)=1,BH27+2,IF(COUNTIF($BG$26:$BG$34,BH27+3)=1,BH27+3,IF(COUNTIF($BG$26:$BG$34,BH27+4)=1,BH27+4,IF(COUNTIF($BG$26:$BG$34,BH27+5)=1,BH27+5,IF(COUNTIF($BG$26:$BG$34,BH27+6)=1,BH27+6,IF(COUNTIF($BG$26:$BG$34,BH27+7)=1,BH27+7,IF(COUNTIF($BG$26:$BG$34,BH27+8)=1,BH27+8,\"\"))))))))","v":28},48,null,null,"Dichte",{"$f":"dichteLuft(BM25,Torr_in_Pa(BM26),BM27)","v":{"$error":"#NAME?"}},"kg/m³",null,null,{"$error":"#NAME?"},-210.13641933694169,44.750533670225003,2.4833814467383464,2483381.4467383465,0.30462139056670473,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},10.532645113413317,{"$error":"#NAME?"},999.67327183475538,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"}]
[null,3.5,120,{"$f":"Auswertung_Leistung!C279","v":43.64437414695697},43.64437414695697,{"$f":"Auswertung_Leistung!H279","v":120},{"$f":"Auswertung_Leistung!K279","v":58.731667371128616},{"$f":"IFERROR(IF(OR(C29=\"\",C29=0,Auswertung_Leistung!T279<20),\"<20\",Auswertung_Leistung!T279),\"\")","v":26.590703565879842},{"$f":"IFERROR(IF(C29=\"\",\"\",H29-6.5),\"\")","v":20.090703565879842},-120,-148.14094692154842,-268.14094692154845,-450.89675746950945,-284.67806221540332,-404.67806221540332,0,350.33132574998086,350.33132574998086,16.634889772520921,7.2200488380660142,56.997160065000166,0.24095666161181128,11.458710353828009,null,{"$f":"IFERROR(V29*1000/15/60,\"\")","v":0.26772962401312367},{"$f":"IFERROR(CA29,\"\")","v":11.458710353828009},{"$f":"IFERROR(CK29,\"\")","v":""},{"$f":"Auswertung_Leistung!Q279","v":14.814094692154843},{"$f":"IF($AN$11=1,AB29*Auswertung_Leistung!Y279,AB29*Auswertung_Leistung!AB279)","v":8.7582831437495212},{"$f":"Auswertung_Leistung!R279","v":14.233903110770166},{"$f":"Auswertung_Leistung!S279","v":22.544837873475473},{"$f":"Auswertung_Leistung!AD279","v":67.170395260763343},null,{"$f":"Auswertung_Leistung!AF279","v":-0.28063933543970909},{"$f":"Auswertung_Leistung!U279","v":26.098235881915322},{"$f":"Auswertung_Leistung!V279","v":71.172882575979386},{"$f":"Auswertung_Leistung!W279","v":45},{"$f":"Auswertung_Leistung!X279","v":305},null,null,null,{"$f":"AVERAGE(AP27:AP28)","v":175},null,{"$f":"AVERAGE(AR27:AR28)","v":60.123615374059327},null,null,null,3.5,120,148.14094692154842,268.14094692154845,284.67806221540332,404.67806221540332,0,350.33132574998086,350.33132574998086,26.590703565879842,"405 ; 268",{"$f":"IF(AV29=\"\",\"\",ROW(AV29))","v":29},29,48,null,null,"Verdampfungsenthalpie",{"$f":"50.09-0.9298*(273.15+BM36)/1000-65.19*((273.15+BM36)/1000)^2","v":{"$error":"#NAME?"}},"kJ/mol",null,null,{"$error":"#NAME?"},{"$f":"M29-N29","v":-166.21869525410614},44.750533670225003,2.4833814467383464,{"$f":"BT29*1000000","v":2483381.4467383465},{"$f":"ABS(BR29)/BU29*3600","v":0.24095666161181128},{"$f":"BQ29/$BM$53","v":{"$error":"#NAME?"}},{"$error":"#NAME?"},{"$f":"BX29*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BQ29-BV29","v":{"$error":"#NAME?"}},11.458710353828009,{"$error":"#NAME?"},{"$f":"999.972-7*10^(-3)*(CA29-4)^2","v":999.58257347900383},{"$f":"BY29/CB29*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BZ29/CC29*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BZ29+BY29","v":{"$error":"#NAME?"}},{"$f":"CD29+CE29","v":{"$error":"#NAME?"}},{"$f":"CF29/CG29","v":{"$error":"#NAME?"}},{"$f":"BZ29/CG29/CH29","v":{"$error":"#NAME?"}},{"$f":"rf_prozent_von_T_grad_x_hf_gH2O_kg_trLuft(CA29,CI29*1000)","v":{"$error":"#NAME?"}},{"$f":"td_T_grad_rf_prozent(CA29,CJ29)","v":{"$error":"#NAME?"}}]
[null,3,120,{"$f":"Auswertung_Leistung!C280","v":28.753928827221785},28.753928827221785,{"$f":"Auswertung_Leistung!H280","v":120},{"$f":"Auswertung_Leistung!K280","v":62.130550017571608},{"$f":"IFERROR(IF(OR(C30=\"\",C30=0,Auswertung_Leistung!T280<20),\"<20\",Auswertung_Leistung!T280),\"\")","v":26.921213008725285},{"$f":"IFERROR(IF(C30=\"\",\"\",H30-6.5),\"\")","v":20.421213008725285},-80,-158.43633917108397,-238.43633917108397,-480.40366005591602,-303.88883214050088,-383.88883214050088,0,372.33684117990072,372.33684117990072,16.679012882161789,7.3023807091735753,56.808541361315136,0.25588230971528514,11.326598651329059,null,{"$f":"IFERROR(V30*1000/15/60,\"\")","v":0.28431367746142794},{"$f":"IFERROR(CA30,\"\")","v":11.326598651329059},{"$f":"IFERROR(CK30,\"\")","v":""},{"$f":"Auswertung_Leistung!Q280","v":15.843633917108397},{"$f":"IF($AN$11=1,AB30*Auswertung_Leistung!Y280,AB30*Auswertung_Leistung!AB280)","v":9.3084210294975183},{"$f":"Auswertung_Leistung!R280","v":15.194441607025043},{"$f":"Auswertung_Leistung!S280","v":24.0201830027958},{"$f":"Auswertung_Leistung!AD280","v":28.793385541619394},null,{"$f":"Auswertung_Leistung!AF280","v":0.55710581894625544},{"$f":"Auswertung_Leistung!U280","v":17.069668367746367},{"$f":"Auswertung_Leistung!V280","v":47.215440006220334},{"$f":"Auswertung_Leistung!W280","v":45},{"$f":"Auswertung_Leistung!X280","v":305},null,null,null,null,null,null,null,null,null,3,80,158.43633917108397,238.43633917108397,303.88883214050088,383.88883214050088,0,372.33684117990072,372.33684117990072,26.921213008725285,"384 ; 238",30,30,48,null,null,null,null,null,null,null,{"$error":"#NAME?"},-176.51482791541514,44.750533670225003,2.4833814467383464,2483381.4467383465,0.25588230971528514,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},11.326598651329059,{"$error":"#NAME?"},999.5962466654164,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"}]
[null,2.5,120,{"$f":"Auswertung_Leistung!C281","v":36.420801214319269},36.420801214319269,{"$f":"Auswertung_Leistung!H281","v":120},{"$f":"Auswertung_Leistung!K281","v":57.418762726552373},{"$f":"IFERROR(IF(OR(C31=\"\",C31=0,Auswertung_Leistung!T281<20),\"<20\",Auswertung_Leistung!T281),\"\")","v":24.835797468795356},18.335797468795356,-100,-145.34643007438979,-245.34643007438979,-443.03791860608357,-279.51157233338142,-379.51157233338142,0,344.56042457712834,344.56042457712834,16.622913271747386,7.1979067385716347,57.046624932196039,0.23705373467894547,11.396154894637297,null,0.26339303853216162,11.396154894637297,"",{"$f":"Auswertung_Leistung!Q281","v":14.534643007438978},{"$f":"IF($AN$11=1,AB31*Auswertung_Leistung!Y281,AB31*Auswertung_Leistung!AB281)","v":8.6140106144282083},{"$f":"Auswertung_Leistung!R281","v":13.975578616669072},{"$f":"Auswertung_Leistung!S281","v":22.151895930304178},{"$f":"Auswertung_Leistung!AD281","v":46.523140578089006},null,{"$f":"Auswertung_Leistung!AF281","v":-5.6888396478586234E-2},{"$f":"Auswertung_Leistung!U281","v":21.600169553880168},{"$f":"Auswertung_Leistung!V281","v":59.859901779086933},{"$f":"Auswertung_Leistung!W281","v":45},{"$f":"Auswertung_Leistung!X281","v":305},null,null,null,null,null,null,null,null,null,2.5,100,145.34643007438979,245.34643007438979,279.51157233338142,379.51157233338142,0,344.56042457712834,344.56042457712834,24.835797468795356,"380 ; 245",31,31,48,null,null,"molare Masse Wasser",18.02,"g/mol",null,null,{"$error":"#NAME?"},-163.52634627270214,44.750533670225003,2.4833814467383464,2483381.4467383465,0.23705373467894547,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},11.396154894637297,{"$error":"#NAME?"},999.58907824942173,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"}]
[null,2,120,{"$f":"Auswertung_Leistung!C282","v":14.185027009026168},14.185027009026168,{"$f":"Auswertung_Leistung!H282","v":120},{"$f":"Auswertung_Leistung!K282","v":45.873199940588556},{"$f":"IFERROR(IF(OR(C32=\"\",C32=0,Auswertung_Leistung!T282<20),\"<20\",Auswertung_Leistung!T282),\"\")","v":"<20"},"",-40,-92.018152444354598,-132.0181524443546,-284.06198275564429,-178.09574012396351,-218.09574012396351,0,222.92351688925447,222.92351688925447,16.394363510475806,6.7632674576741296,58.089226998092101,0.15361251650449498,14.35295507913426,null,0.17068057389388333,14.35295507913426,"",{"$f":"Auswertung_Leistung!Q282","v":9.2018152444354602},{"$f":"IF($AN$11=1,AB32*Auswertung_Leistung!Y282,AB32*Auswertung_Leistung!AB282)","v":5.5730879222313616},{"$f":"Auswertung_Leistung!R282","v":8.9047870061981751},{"$f":"Auswertung_Leistung!S282","v":14.203099137782216},{"$f":"Auswertung_Leistung!AD282","v":6.8608232203697046},null,{"$f":"Auswertung_Leistung!AF282","v":2.4812794303879917},{"$f":"Auswertung_Leistung!U282","v":8.1988950705672679},{"$f":"Auswertung_Leistung!V282","v":23.891962165052611},{"$f":"Auswertung_Leistung!W282","v":45},{"$f":"Auswertung_Leistung!X282","v":305},null,null,null,null,null,null,null,null,null,2,40,92.018152444354598,132.0181524443546,178.09574012396351,218.09574012396351,0,222.92351688925447,222.92351688925447,"<20","218 ; 132",32,32,48,null,null,"Verdampfungsenthalpie",{"$f":"BM29/BM31","v":{"$error":"#NAME?"}},"kJ/g",null,null,{"$error":"#NAME?"},-105.96624263168079,44.750533670225003,2.4833814467383464,2483381.4467383465,0.15361251650449498,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},14.35295507913426,{"$error":"#NAME?"},999.22171424790599,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"}]
[null,2,{"$f":"C32","v":120},{"$f":"Auswertung_Leistung!C283","v":14.185027009026168},14.185027009026168,{"$f":"Auswertung_Leistung!H283","v":120},{"$f":"Auswertung_Leistung!K283","v":45.873199940588556},{"$f":"IFERROR(IF(OR(C33=\"\",C33=0,Auswertung_Leistung!T283<20),\"<20\",Auswertung_Leistung!T283),\"\")","v":22.073164925331078},15.573164925331078,-40,-92.018152444354598,-132.0181524443546,-284.06198275564429,-178.09574012396351,{"$f":"J33+N33","v":-218.09574012396351},0,222.92351688925447,222.92351688925447,16.394363510475806,6.7632674576741296,58.089226998092101,{"$f":"IFERROR(BV33,\"\")","v":0.15361251650449498},14.35295507913426,null,0.17068057389388333,14.35295507913426,"",{"$f":"Auswertung_Leistung!Q283","v":9.2018152444354602},{"$f":"IF($AN$11=1,AB33*Auswertung_Leistung!Y283,AB33*Auswertung_Leistung!AB283)","v":5.5730879222313616},{"$f":"Auswertung_Leistung!R283","v":8.9047870061981751},{"$f":"Auswertung_Leistung!S283","v":14.203099137782216},null,{"$f":"IF(C33=\"\",\"\",$BH$10*F33^$BI$10)","v":2.9070844090284653E+101},null,{"$f":"Auswertung_Leistung!U283","v":8.1988950705672679},{"$f":"Auswertung_Leistung!V283","v":23.891962165052611},{"$f":"Auswertung_Leistung!W283","v":45},{"$f":"Auswertung_Leistung!X283","v":305},null,null,null,null,null,null,null,null,null,2,40,92.018152444354598,132.0181524443546,178.09574012396351,218.09574012396351,0,222.92351688925447,222.92351688925447,22.073164925331078,"218 ; 132",33,33,48,null,null,"Verdampfungsenthalpie",{"$f":"BM32*1000000","v":{"$error":"#NAME?"}},"J/kg",null,null,{"$error":"#NAME?"},-105.96624263168079,44.750533670225003,2.4833814467383464,2483381.4467383465,0.15361251650449498,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},14.35295507913426,{"$error":"#NAME?"},999.22171424790599,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"}]
[null,2,120,{"$f":"Auswertung_Leistung!C284","v":14.185027009026168},14.185027009026168,{"$f":"Auswertung_Leistung!H284","v":120},{"$f":"Auswertung_Leistung!K284","v":45.873199940588556},{"$f":"IFERROR(IF(OR(C34=\"\",C34=0,Auswertung_Leistung!T284<20),\"<20\",Auswertung_Leistung!T284),\"\")","v":22.073164925331078},{"$f":"IFERROR(IF(C34=\"\",\"\",H34-6.5),\"\")","v":15.573164925331078},-40,-92.018152444354598,-132.0181524443546,-284.06198275564429,-178.09574012396351,-218.09574012396351,0,222.92351688925447,222.92351688925447,16.394363510475806,6.7632674576741296,58.089226998092101,{"$f":"IFERROR(BV34,\"\")","v":0.15361251650449498},14.35295507913426,null,{"$f":"IFERROR(V34*1000/15/60,\"\")","v":0.17068057389388333},{"$f":"IFERROR(CA34,\"\")","v":14.35295507913426},{"$f":"IFERROR(CK34,\"\")","v":""},{"$f":"Auswertung_Leistung!Q284","v":9.2018152444354602},{"$f":"IF($AN$11=1,AB34*Auswertung_Leistung!Y284,AB34*Auswertung_Leistung!AB284)","v":5.5730879222313616},{"$f":"Auswertung_Leistung!R284","v":8.9047870061981751},{"$f":"Auswertung_Leistung!S284","v":14.203099137782216},null,{"$f":"IF(C34=\"\",\"\",$BH$10*F34^$BI$10)","v":2.9070844090284653E+101},null,{"$f":"Auswertung_Leistung!U284","v":11.395074504856202},{"$f":"Auswertung_Leistung!V284","v":23.891962165052611},{"$f":"Auswertung_Leistung!W284","v":45},{"$f":"Auswertung_Leistung!X284","v":305},null,null,null,null,null,null,null,null,null,2,40,92.018152444354598,132.0181524443546,178.09574012396351,218.09574012396351,0,222.92351688925447,222.92351688925447,22.073164925331078,"218 ; 132",34,34,48,null,null,null,null,null,null,null,{"$error":"#NAME?"},-105.96624263168079,44.750533670225003,2.4833814467383464,2483381.4467383465,0.15361251650449498,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},14.35295507913426,{"$error":"#NAME?"},999.22171424790599,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"}]
[]
[null,{"$f":"IF(OR(C26<C37,C27<C37,C28<C37,C34<C37,C26>C38,C27>C38,C28>C38,C34>C38),\"Grenzwerte\",\"\")","v":""},null,null,null,null,null,null,null,null,"DpK =",{"$f":"Auswertung_Leistung!E271","v":23.073797299680965},"[kPa]",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Taupunkttemperatur",{"$f":"td_T_grad_rf_prozent(BM27,BM25)","v":{"$error":"#NAME?"}},"°C"]
[null,"  Minimal",{"$f":"AP27","v":45},{"$f":"AQ27","v":"Pa"},null,null,null,null,null,null,"DpH =",{"$f":"Auswertung_Leistung!E272","v":1.3},"[kPa]",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"phi_x (kg_H20/kg_Gesamt Wassergehalt)",{"$f":"phi_x($BM$25,Torr_in_Pa($BM$26),$BM$27)","v":{"$error":"#NAME?"}},"kg_H20/kg_Gesamt"]
[null,"  Maximal",{"$f":"AP28","v":305},{"$f":"AQ28","v":"Pa"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"universelle Gaskonstante",8.3144597999999998,"J/ mol K"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"L_BG800","v":"Baugröße 800"}]
[null,"Baugröße 800",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Schieberstellung","QPK Primärleistung","QSK1) Sekundärleistung","QKges1) Gesamtleistung","QSK2) Sekundärleistung","QKges2) Gesamtleistung","QPH Primärleistung","QSH Sekundärleistung","QGes Gesamtleistung","LWA - Schallleistung"]
[]
[{"$f":"L_Auswahl","v":"Auswahl"},{"$f":"L_Auslegung","v":"Schieberstellung"},{"$f":"IF($AQ$7=1,$AO$1,$AN$1)","v":"Primärdruck"},{"$f":"IF($AQ$7=2,$AO$1,$AN$1)","v":"Primärvol."},{"$f":"E24","v":"Primärvol."},{"$f":"L_primaerdruck","v":"Primärdruck"},{"$f":"L_sekundaervol","v":"Sekundärvolumenstrom"},"LWA","LA18","QPK","QSK1","QKges1","QTotal2","QSensibel,K2","QKges2","QPH","QSH","Qhges","tKWRL","tKWRL2","tWWRL",{"$f":"V24","v":"Kondensat ²"},{"$f":"W24","v":"Zulufttemp.²"},null,"Tropfen","Zulufttemp.","Taupunkt nach WT","qSK1)","qSH","qSK2)","qtotal2)",{"$f":"Auswertung_Leistung!AD293","v":"Primärdruck Baugröße 800; S5"},{"$f":"Auswertung_Leistung!AE293","v":"qSK1)  - aus Primärdruck der gemessenen BG"},{"$f":"Auswertung_Leistung!AF293","v":"Kühlleistung \"mit Schieber\" im Vergleich zu \"ohne Schieber\""},"Primärvolumenstrom Minimal","Primärvolumenstrom Minimal","Primärdruck Minimal","Primärdruck Maximal",null,null,null,null,null,null,null,null,null,"Schieberstellung","QPK","QSK1)","QKges1)","QSensibel,K2)","QKges2)","QPH","QSH","Qhges","LWA","QKges2) ; QKges1)","Zeile","Zeile","Spalte",null,null,null,null,null,null,null,"Wassermenge Gesamt in der Luft","latente \nLeistung",null,null,null,"Kondensatmenge",null,null,null,null,"Zulufttemperatur",null,null,null,null,null,null,null,null,null,"Taupunkt im Kasten"]
[null,null,{"$f":"IF($AQ$7=1,$AO$2,$AN$2)","v":"[Pa]"},{"$f":"IF($AQ$7=2,$AO$2,$AN$2)","v":"[m³/h]"},"[m³/h]","[Pa]","[m³/h]","[dB(A)]","[dB(A)]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[°C]","[°C]","[°C]","[kg/h] bzw. [l / h]","[°C]",null,"[Anzahl / min]",{"$f":"CA44","v":"[°C]"},"[°C]","[W]","[W]","[W]","[W]",{"$f":"Auswertung_Leistung!AD294","v":"[Pa]"},{"$f":"Auswertung_Leistung!AE294","v":"[W/K]"},{"$f":"Auswertung_Leistung!AF294","v":0},"[m³/h]","[m³/h]","[m³/h]","[m³/h]","Grenzen der Auslegung",null,null,"Abhängig von Abfrage",null,null,null,"heizen",null,null,"[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[dB(A)]",null,null,null,null,null,null,null,null,null,null,null,"kg H20 / h","W bzw. J / s",null,null,null,"kg / h bzw.l / h",null,null,null,null,"[°C]",null,null,null,null,null,null,null,null,null,"[°C]"]
[null,5,{"$f":"$J$17","v":120},{"$f":"Auswertung_Leistung!C295","v":80.73043386129882},{"$f":"IF(C45=\"\",\"\",IF($AQ$7=1,C45,D45))","v":80.73043386129882},{"$f":"IF(C45=\"\",\"\",IF($AQ$7=1,D45,C45))","v":120},{"$f":"Auswertung_Leistung!K295","v":164.02443076580053},{"$f":"IFERROR(IF(OR(C45=\"\",C45=0,Auswertung_Leistung!T295<20),\"<20\",Auswertung_Leistung!T295),\"\")","v":28.283110685239627},{"$f":"IFERROR(IF(C45=\"\",\"\",H45-6.5),\"\")","v":21.783110685239627},{"$f":"ROUND(E45*1.2*1004.5*($J$16-$J$15)/3600,-1)","v":-220},{"$f":"IF(C45=\"\",\"\",IF(C45=0,,IFERROR((AB45*($J$7-$J$6)),\"\")))","v":-411.34218578828666},{"$f":"J45+K45","v":-631.34218578828666},{"$f":"IFERROR(AE45*($J$8-$J$6),\"\")","v":-1168.5069923850378},{"$f":"IFERROR(AD45*($J$8-$J$6),\"\")","v":-765.66570947044033},{"$f":"J45+N45","v":-985.66570947044033},{"$f":"ROUND(E45*1.2*1004.5*($Q$16-$Q$15)/3600,-1)","v":0},{"$f":"IF(G45=0,,IFERROR((AC45*($Q$7-$Q$6)),\"\"))","v":883.73923223201757},{"$f":"Q45+P45","v":883.73923223201757},{"$f":"IF(IFERROR(IF(K45=0,,$J$7-((K45/(4.2*$J$13/3.6)))),)=0,\"\",IFERROR(IF(K45=0,,$J$7-((K45/(4.2*$J$13/3.6)))),))","v":17.7628950819498},{"$f":"IF(IFERROR(IF(N45=0,,$J$8-((N45/(4.2*$J$13/3.6)))),)=0,\"\",IFERROR(IF(N45=0,,$J$8-((N45/(4.2*$J$13/3.6)))),))","v":9.2814244691590311},{"$f":"IF(C45=\"\",\"\",IFERROR(IF(Q45=0,,($Q$7-((Q45/(4.2*$Q$13/3.6))))),))","v":52.425092295154137},{"$f":"IFERROR(BV45,\"\")","v":0.58397336438075986},{"$f":"Z45","v":11.996006096853653},null,{"$f":"IFERROR(V45*1000/15/60,\"\")","v":0.64885929375639995},{"$f":"IFERROR(CA45,\"\")","v":11.996006096853653},{"$f":"IFERROR(CK45,\"\")","v":""},{"$f":"Auswertung_Leistung!Q295","v":41.134218578828666},{"$f":"IF($AN$11=1,AB45*Auswertung_Leistung!Y295,AB45*Auswertung_Leistung!AB295)","v":22.093480805800439},{"$f":"Auswertung_Leistung!R295","v":38.283285473522014},{"$f":"Auswertung_Leistung!S295","v":58.425349619251897},{"$f":"Auswertung_Leistung!AD295","v":120.00162820198784},{"$f":"Auswertung_Leistung!AE295","v":41.134526594315048},{"$f":"Auswertung_Leistung!AF295","v":7.4880597473736543E-6},{"$f":"Auswertung_Leistung!U295","v":49.797088153619242},{"$f":"Auswertung_Leistung!V295","v":127.82028754345181},{"$f":"Auswertung_Leistung!W295","v":45},{"$f":"Auswertung_Leistung!X295","v":305},{"$f":"$AM$96","v":"Primärdurck"},"Primärvolumenstrom",{"$f":"$AO$96","v":"Wassermassenstrom"},{"$f":"IF($AQ$7=1,AN45,AM45)","v":"Primärdurck"},"Einheit",{"$f":"IF($AQ$7=2,AN45,AM45)","v":"Primärvolumenstrom"},"Einheit",{"$f":"$AO$96","v":"Wassermassenstrom"},null,{"$f":"IF(OR(F45<$AM$46,F45>$AM$47),\"\",B45)","v":5},{"$f":"IF(AV45=\"\",\"\",ABS(J45))","v":220},{"$f":"IF(AV45=\"\",\"\",ABS(K45))","v":411.34218578828666},{"$f":"IF(AV45=\"\",\"\",ABS(L45))","v":631.34218578828666},{"$f":"IF(AV45=\"\",\"\",ABS(N45))","v":765.66570947044033},{"$f":"IF(AV45=\"\",\"\",(AW45+AZ45))","v":985.66570947044033},{"$f":"IF(AV45=\"\",\"\",(P45))","v":0},{"$f":"IF(AV45=\"\",\"\",ABS(Q45))","v":883.73923223201757},{"$f":"IF(AV45=\"\",\"\",(BB45+BC45))","v":883.73923223201757},{"$f":"IF(AV45=\"\",\"\",H45)","v":28.283110685239627},{"$f":"IF(AV45=\"\",\"\",CONCATENATE(ROUND(BA45,0),\"W ; \",ROUND(AY45,0), \"W\"))","v":"986W ; 631W"},{"$f":"IF(AV45=\"\",\"\",ROW(AV45))","v":45},{"$f":"MIN(BG45:BG53)","v":45},{"$f":"COLUMN(AV45)","v":48},null,null,null,null,null,null,null,{"$f":"$BM$37*(G45*$BM$28)","v":{"$error":"#NAME?"}},{"$f":"M45-N45","v":-402.84128291459751},{"$f":"50.09-0.9298*(273.15+$J$8)/1000-65.19*((273.15+$J$8)/1000)^2","v":44.750533670225003},{"$f":"BS45/$BM$31","v":2.4833814467383464},{"$f":"BT45*1000000","v":2483381.4467383465},{"$f":"ABS(BR45)/BU45*3600","v":0.58397336438075986},{"$f":"BQ45/$BM$53","v":{"$error":"#NAME?"}},{"$f":"G45-BW45","v":{"$error":"#NAME?"}},{"$f":"BX45*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BQ45-BV45","v":{"$error":"#NAME?"}},{"$f":"N45*3/G45+$BM$27","v":11.996006096853653},{"$f":"dichteLuft(0,Torr_in_Pa($BM$26),CA45)","v":{"$error":"#NAME?"}},{"$f":"999.972-7*10^(-3)*(CA45-4)^2","v":999.52444720549352},{"$f":"BY45/CB45*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BZ45/CC45*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BZ45+BY45","v":{"$error":"#NAME?"}},{"$f":"CD45+CE45","v":{"$error":"#NAME?"}},{"$f":"CF45/CG45","v":{"$error":"#NAME?"}},{"$f":"BZ45/CG45/CH45","v":{"$error":"#NAME?"}},{"$f":"rf_prozent_von_T_grad_x_hf_gH2O_kg_trLuft(CA45,CI45*1000)","v":{"$error":"#NAME?"}},{"$f":"td_T_grad_rf_prozent(CA45,CJ45)","v":{"$error":"#NAME?"}}]
[null,4.5,{"$f":"C45","v":120},{"$f":"Auswertung_Leistung!C296","v":96.944857405303324},{"$f":"IF(C46=\"\",\"\",IF($AQ$7=1,C46,D46))","v":96.944857405303324},{"$f":"IF(C46=\"\",\"\",IF($AQ$7=1,D46,C46))","v":120},{"$f":"Auswertung_Leistung!K296","v":154.89530616677845},{"$f":"IFERROR(IF(OR(C46=\"\",C46=0,Auswertung_Leistung!T296<20),\"<20\",Auswertung_Leistung!T296),\"\")","v":28.029613342122026},{"$f":"IFERROR(IF(C46=\"\",\"\",H46-6.5),\"\")","v":21.529613342122026},{"$f":"ROUND(E46*1.2*1004.5*($J$16-$J$15)/3600,-1)","v":-260},-377.57955145535453,{"$f":"J46+K46","v":-637.57955145535448},-1081.0419764385895,{"$f":"IFERROR(AD46*($J$8-$J$6),\"\")","v":-705.18453007107564},{"$f":"J46+N46","v":-965.18453007107564},0,821.76739730543716,{"$f":"Q46+P46","v":821.76739730543716},17.618198077665806,9.0222194145903245,52.956279451667683,{"$f":"IFERROR(BV46,\"\")","v":0.54485661423466913},{"$f":"Z46","v":12.342041972948014},null,{"$f":"IFERROR(V46*1000/15/60,\"\")","v":0.60539623803852127},{"$f":"IFERROR(CA46,\"\")","v":12.342041972948014},{"$f":"IFERROR(CK46,\"\")","v":""},{"$f":"Auswertung_Leistung!Q296","v":37.757955145535455},{"$f":"IF($AN$11=1,AB46*Auswertung_Leistung!Y296,AB46*Auswertung_Leistung!AB296)","v":20.544184932635929},{"$f":"Auswertung_Leistung!R296","v":35.259226503553784},{"$f":"Auswertung_Leistung!S296","v":54.052098821929476},{"$f":"Auswertung_Leistung!AD296","v":173.99655111742987},{"$f":"Auswertung_Leistung!AE296","v":49.000728741583814},{"$f":"Auswertung_Leistung!AF296","v":0.29775906965072285},{"$f":"Auswertung_Leistung!U296","v":58.896333262093655},{"$f":"Auswertung_Leistung!V296","v":155.72819534846124},{"$f":"Auswertung_Leistung!W296","v":45},{"$f":"Auswertung_Leistung!X296","v":305},{"$f":"AM97","v":45},{"$f":"MIN(AI45:AI53)","v":11.395074504856202},{"$f":"AO97","v":50},{"$f":"IF($AQ$7=1,AN46,AM46)","v":45},{"$f":"IF($AQ$7=1,\"m³/h\",\"Pa\")","v":"Pa"},{"$f":"IF($AQ$7=2,AN46,AM46)","v":11.395074504856202},{"$f":"IF($AQ$7=2,\"m³/h\",\"Pa\")","v":"m³/h"},{"$f":"AT97","v":50},null,{"$f":"IF(OR(F46<$AM$46,F46>$AM$47),\"\",B46)","v":4.5},{"$f":"IF(AV46=\"\",\"\",ABS(J46))","v":260},377.57955145535453,637.57955145535448,705.18453007107564,965.18453007107564,0,821.76739730543716,821.76739730543716,{"$f":"IF(AV46=\"\",\"\",H46)","v":28.029613342122026},{"$f":"IF(AV46=\"\",\"\",CONCATENATE(ROUND(BA46,0),\"W ; \",ROUND(AY46,0), \"W\"))","v":"965W ; 638W"},{"$f":"IF(AV46=\"\",\"\",ROW(AV46))","v":46},{"$f":"IF(COUNTIF($BG$45:$BG$53,BH45+1)=1,BH45+1,IF(COUNTIF($BG$45:$BG$53,BH45+2)=1,BH45+2,IF(COUNTIF($BG$45:$BG$53,BH45+3)=1,BH45+3,IF(COUNTIF($BG$45:$BG$53,BH45+4)=1,BH45+4,IF(COUNTIF($BG$45:$BG$53,BH45+5)=1,BH45+5,IF(COUNTIF($BG$45:$BG$53,BH45+6)=1,BH45+6,IF(COUNTIF($BG$45:$BG$53,BH45+7)=1,BH45+7,IF(COUNTIF($BG$45:$BG$53,BH45+8)=1,BH45+8,\"\"))))))))","v":46},48,null,null,null,null,null,null,null,{"$error":"#NAME?"},{"$f":"M46-N46","v":-375.85744636751383},44.750533670225003,2.4833814467383464,{"$f":"BT46*1000000","v":2483381.4467383465},{"$f":"ABS(BR46)/BU46*3600","v":0.54485661423466913},{"$f":"BQ46/$BM$53","v":{"$error":"#NAME?"}},{"$error":"#NAME?"},{"$f":"BX46*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BQ46-BV46","v":{"$error":"#NAME?"}},{"$f":"N46*3/G46+$BM$27","v":12.342041972948014},{"$error":"#NAME?"},{"$f":"999.972-7*10^(-3)*(CA46-4)^2","v":999.48487235005098},{"$f":"BY46/CB46*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BZ46/CC46*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BZ46+BY46","v":{"$error":"#NAME?"}},{"$f":"CD46+CE46","v":{"$error":"#NAME?"}},{"$f":"CF46/CG46","v":{"$error":"#NAME?"}},{"$f":"BZ46/CG46/CH46","v":{"$error":"#NAME?"}},{"$f":"rf_prozent_von_T_grad_x_hf_gH2O_kg_trLuft(CA46,CI46*1000)","v":{"$error":"#NAME?"}},{"$f":"td_T_grad_rf_prozent(CA46,CJ46)","v":{"$error":"#NAME?"}}]
[null,4,{"$f":"C46","v":120},{"$f":"Auswertung_Leistung!C297","v":60.780258355806176},60.780258355806176,{"$f":"IF(C47=\"\",\"\",IF($AQ$7=1,D47,C47))","v":120},{"$f":"Auswertung_Leistung!K297","v":98.926386288835431},{"$f":"IFERROR(IF(OR(C47=\"\",C47=0,Auswertung_Leistung!T297<20),\"<20\",Auswertung_Leistung!T297),\"\")","v":26.913996752316265},{"$f":"IFERROR(IF(C47=\"\",\"\",H47-6.5),\"\")","v":20.413996752316265},-160,-263.03715133112354,-423.03715133112354,-789.44731148114431,-501.99928693459094,-661.99928693459094,0,629.03263291018038,629.03263291018038,17.127302077133386,8.1514255154339619,54.608291717912742,{"$f":"IFERROR(BV47,\"\")","v":0.41669510325395531},{"$f":"Z47","v":10.77658067477862},null,{"$f":"IFERROR(V47*1000/15/60,\"\")","v":0.46299455917106147},{"$f":"IFERROR(CA47,\"\")","v":10.77658067477862},{"$f":"IFERROR(CK47,\"\")","v":""},{"$f":"Auswertung_Leistung!Q297","v":26.303715133112355},{"$f":"IF($AN$11=1,AB47*Auswertung_Leistung!Y297,AB47*Auswertung_Leistung!AB297)","v":15.725815822754509},{"$f":"Auswertung_Leistung!R297","v":25.099964346729546},{"$f":"Auswertung_Leistung!S297","v":39.472365574057214},{"$f":"Auswertung_Leistung!AD297","v":67.444862186503812},{"$f":"Auswertung_Leistung!AE297","v":28.164543973614087},{"$f":"Auswertung_Leistung!AF297","v":7.0743955030110328E-2},{"$f":"Auswertung_Leistung!U297","v":36.630806586501116},{"$f":"Auswertung_Leistung!V297","v":98.381681885788808},{"$f":"Auswertung_Leistung!W297","v":45},{"$f":"Auswertung_Leistung!X297","v":305},{"$f":"AM98","v":305},{"$f":"MAX(AJ45:AJ53)","v":155.72819534846124},{"$f":"AO98","v":300},{"$f":"IF($AQ$7=1,AN47,AM47)","v":305},{"$f":"IF($AQ$7=1,\"m³/h\",\"Pa\")","v":"Pa"},{"$f":"IF($AQ$7=2,AN47,AM47)","v":155.72819534846124},{"$f":"IF($AQ$7=2,\"m³/h\",\"Pa\")","v":"m³/h"},{"$f":"AT98","v":300},null,4,160,263.03715133112354,423.03715133112354,501.99928693459094,661.99928693459094,0,629.03263291018038,629.03263291018038,26.913996752316265,"662W ; 423W",{"$f":"IF(AV47=\"\",\"\",ROW(AV47))","v":47},{"$f":"IF(COUNTIF($BG$45:$BG$53,BH46+1)=1,BH46+1,IF(COUNTIF($BG$45:$BG$53,BH46+2)=1,BH46+2,IF(COUNTIF($BG$45:$BG$53,BH46+3)=1,BH46+3,IF(COUNTIF($BG$45:$BG$53,BH46+4)=1,BH46+4,IF(COUNTIF($BG$45:$BG$53,BH46+5)=1,BH46+5,IF(COUNTIF($BG$45:$BG$53,BH46+6)=1,BH46+6,IF(COUNTIF($BG$45:$BG$53,BH46+7)=1,BH46+7,IF(COUNTIF($BG$45:$BG$53,BH46+8)=1,BH46+8,\"\"))))))))","v":47},48,null,null,null,null,null,null,null,{"$error":"#NAME?"},{"$f":"M47-N47","v":-287.44802454655337},44.750533670225003,2.4833814467383464,{"$f":"BT47*1000000","v":2483381.4467383465},{"$f":"ABS(BR47)/BU47*3600","v":0.41669510325395531},{"$f":"BQ47/$BM$53","v":{"$error":"#NAME?"}},{"$error":"#NAME?"},{"$f":"BX47*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BQ47-BV47","v":{"$error":"#NAME?"}},10.77658067477862,{"$error":"#NAME?"},{"$f":"999.972-7*10^(-3)*(CA47-4)^2","v":999.65054568050755},{"$f":"BY47/CB47*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BZ47/CC47*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BZ47+BY47","v":{"$error":"#NAME?"}},{"$f":"CD47+CE47","v":{"$error":"#NAME?"}},{"$f":"CF47/CG47","v":{"$error":"#NAME?"}},{"$f":"BZ47/CG47/CH47","v":{"$error":"#NAME?"}},{"$f":"rf_prozent_von_T_grad_x_hf_gH2O_kg_trLuft(CA47,CI47*1000)","v":{"$error":"#NAME?"}},{"$f":"td_T_grad_rf_prozent(CA47,CJ47)","v":{"$error":"#NAME?"}}]
[null,3.5,120,{"$f":"Auswertung_Leistung!C298","v":60.65828271271986},60.65828271271986,120,{"$f":"Auswertung_Leistung!K298","v":81.627063125975369},{"$f":"IFERROR(IF(OR(C48=\"\",C48=0,Auswertung_Leistung!T298<20),\"<20\",Auswertung_Leistung!T298),\"\")","v":28.020321973295566},21.520321973295566,-160,-201.98804008772066,-361.98804008772066,-614.79121212453083,-388.15442345802501,-548.15442345802501,0,499.70841281982371,499.70841281982371,16.865663028947374,7.6635189576772502,55.716785032972936,0.32854092562824272,11.734348073053246,null,{"$f":"IFERROR(V48*1000/15/60,\"\")","v":0.36504547292026968},{"$f":"IFERROR(CA48,\"\")","v":11.734348073053246},{"$f":"IFERROR(CK48,\"\")","v":""},{"$f":"Auswertung_Leistung!Q298","v":20.198804008772065},{"$f":"IF($AN$11=1,AB48*Auswertung_Leistung!Y298,AB48*Auswertung_Leistung!AB298)","v":12.492710320495593},{"$f":"Auswertung_Leistung!R298","v":19.407721172901251},{"$f":"Auswertung_Leistung!S298","v":30.73956060622654},{"$f":"Auswertung_Leistung!AD298","v":67.170395260763343},{"$f":"Auswertung_Leistung!AE298","v":28.078827497634418},{"$f":"Auswertung_Leistung!AF298","v":0.39012327093426746},{"$f":"Auswertung_Leistung!U298","v":36.272124446051805},{"$f":"Auswertung_Leistung!V298","v":98.918243580174746},{"$f":"Auswertung_Leistung!W298","v":45},{"$f":"Auswertung_Leistung!X298","v":305},null,null,null,{"$f":"AVERAGE(AP46:AP47)","v":175},null,{"$f":"AVERAGE(AR46:AR47)","v":83.561634926658726},null,null,null,3.5,160,201.98804008772066,361.98804008772066,388.15442345802501,548.15442345802501,0,499.70841281982371,499.70841281982371,28.020321973295566,"548W ; 362W",48,48,48,null,null,null,null,null,null,null,{"$error":"#NAME?"},-226.63678866650582,44.750533670225003,2.4833814467383464,2483381.4467383465,0.32854092562824272,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},11.734348073053246,{"$error":"#NAME?"},999.553259019194,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"}]
[null,3,120,{"$f":"Auswertung_Leistung!C299","v":39.963087522579428},39.963087522579428,120,{"$f":"Auswertung_Leistung!K299","v":86.350933922726639},{"$f":"IFERROR(IF(OR(C49=\"\",C49=0,Auswertung_Leistung!T299<20),\"<20\",Auswertung_Leistung!T299),\"\")","v":28.350831416141009},21.850831416141009,-110,-216.2034877106791,-326.2034877106791,-655.56265283880509,-414.68911569683991,-524.68911569683996,0,529.8342994009106,529.8342994009106,16.926586375902911,7.7772390672721716,55.458563147992194,0.34917903363173453,11.592890654734488,null,0.38797670403526058,11.592890654734488,"",{"$f":"Auswertung_Leistung!Q299","v":21.62034877106791},{"$f":"IF($AN$11=1,AB49*Auswertung_Leistung!Y299,AB49*Auswertung_Leistung!AB299)","v":13.245857485022766},{"$f":"Auswertung_Leistung!R299","v":20.734455784841995},{"$f":"Auswertung_Leistung!S299","v":32.778132641940253},{"$f":"Auswertung_Leistung!AD299","v":28.793385541619394},{"$f":"Auswertung_Leistung!AE299","v":13.884957918723281},{"$f":"Auswertung_Leistung!AF299","v":-0.35778288936282276},{"$f":"Auswertung_Leistung!U299","v":23.723945867037322},{"$f":"Auswertung_Leistung!V299","v":65.621458991696059},{"$f":"Auswertung_Leistung!W299","v":45},{"$f":"Auswertung_Leistung!X299","v":305},null,null,null,null,null,null,null,null,null,3,110,216.2034877106791,326.2034877106791,414.68911569683991,524.68911569683996,0,529.8342994009106,529.8342994009106,28.350831416141009,"525W ; 326W",49,49,48,null,null,null,null,null,null,null,{"$error":"#NAME?"},-240.87353714196519,44.750533670225003,2.4833814467383464,2483381.4467383465,0.34917903363173453,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},11.592890654734488,{"$error":"#NAME?"},999.56843608053669,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"}]
[null,2.5,120,{"$f":"Auswertung_Leistung!C300","v":50.618740670748814},50.618740670748814,120,{"$f":"Auswertung_Leistung!K300","v":79.802348196225324},{"$f":"IFERROR(IF(OR(C50=\"\",C50=0,Auswertung_Leistung!T300<20),\"<20\",Auswertung_Leistung!T300),\"\")","v":26.26541587621108},19.76541587621108,-140,-198.13206921650635,-338.13206921650635,-603.93653638325168,-381.0221287721198,-521.0221287721198,0,491.98557456855582,491.98557456855582,16.849137439499312,7.6329519804519421,55.782980789412377,0.32314482676596512,11.676281310598991,null,0.35904980751773902,11.676281310598991,"",{"$f":"Auswertung_Leistung!Q300","v":19.813206921650636},{"$f":"IF($AN$11=1,AB50*Auswertung_Leistung!Y300,AB50*Auswertung_Leistung!AB300)","v":12.299639364213895},{"$f":"Auswertung_Leistung!R300","v":19.051106438605991},{"$f":"Auswertung_Leistung!S300","v":30.196826819162585},{"$f":"Auswertung_Leistung!AD300","v":46.523140578089006},{"$f":"Auswertung_Leistung!AE300","v":21.008337558006481},{"$f":"Auswertung_Leistung!AF300","v":6.0319898796891813E-2},{"$f":"Auswertung_Leistung!U300","v":30.020574634206334},{"$f":"Auswertung_Leistung!V300","v":83.195117726866584},{"$f":"Auswertung_Leistung!W300","v":45},{"$f":"Auswertung_Leistung!X300","v":305},null,null,null,null,null,null,null,null,null,2.5,140,198.13206921650635,338.13206921650635,381.0221287721198,521.0221287721198,0,491.98557456855582,491.98557456855582,26.26541587621108,"521W ; 338W",50,50,48,null,null,null,null,null,null,null,{"$error":"#NAME?"},-222.91440761113188,44.750533670225003,2.4833814467383464,2483381.4467383465,0.32314482676596512,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},11.676281310598991,{"$error":"#NAME?"},999.55952293668383,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"}]
[null,2,120,{"$f":"Auswertung_Leistung!C301","v":19.714783300680438},19.714783300680438,120,{"$f":"Auswertung_Leistung!K301","v":63.7559727987841},{"$f":"IFERROR(IF(OR(C51=\"\",C51=0,Auswertung_Leistung!T301<20),\"<20\",Auswertung_Leistung!T301),\"\")","v":20.854605102651437},14.354605102651437,-50,-124.80288994803732,-174.80288994803732,-385.26916081815932,-241.54867778231417,-291.54867778231414,0,320.44787291335092,320.44787291335092,16.534869528348732,7.0352086190670606,57.253303946456995,0.20834243551613199,{"$f":"Z51","v":14.634068283548135},null,0.23149159501792443,{"$f":"IFERROR(CA51,\"\")","v":14.634068283548135},"",{"$f":"Auswertung_Leistung!Q301","v":12.480288994803733},{"$f":"IF($AN$11=1,AB51*Auswertung_Leistung!Y301,AB51*Auswertung_Leistung!AB301)","v":8.0111968228337727},{"$f":"Auswertung_Leistung!R301","v":12.077433889115708},{"$f":"Auswertung_Leistung!S301","v":19.263458040907967},{"$f":"Auswertung_Leistung!AD301","v":6.8608232203697046},{"$f":"Auswertung_Leistung!AE301","v":3.5849719174690882},{"$f":"Auswertung_Leistung!AF301","v":-0.71274928657808168},{"$f":"Auswertung_Leistung!U301","v":11.395074504856202},{"$f":"Auswertung_Leistung!V301","v":33.205777924310411},{"$f":"Auswertung_Leistung!W301","v":45},{"$f":"Auswertung_Leistung!X301","v":305},null,null,null,null,null,null,null,null,null,2,50,124.80288994803732,174.80288994803732,241.54867778231417,291.54867778231414,0,320.44787291335092,320.44787291335092,20.854605102651437,"292W ; 175W",51,51,48,null,null,null,null,null,null,null,{"$error":"#NAME?"},-143.72048303584515,44.750533670225003,2.4833814467383464,2483381.4467383465,0.20834243551613199,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$f":"N51*3/G51+$BM$27","v":14.634068283548135},{"$error":"#NAME?"},999.18041614218578,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"}]
[null,2,{"$f":"C51","v":120},{"$f":"Auswertung_Leistung!C302","v":19.714783300680438},19.714783300680438,{"$f":"IF(C52=\"\",\"\",IF($AQ$7=1,D52,C52))","v":120},{"$f":"Auswertung_Leistung!K302","v":63.7559727987841},{"$f":"IFERROR(IF(OR(C52=\"\",C52=0,Auswertung_Leistung!T302<20),\"<20\",Auswertung_Leistung!T302),\"\")","v":23.502783332746802},{"$f":"IFERROR(IF(C52=\"\",\"\",H52-6.5),\"\")","v":17.002783332746802},-50,-124.80288994803732,-174.80288994803732,-385.26916081815932,-241.54867778231417,-291.54867778231414,0,320.44787291335092,320.44787291335092,16.534869528348732,7.0352086190670606,57.253303946456995,{"$f":"IFERROR(BV52,\"\")","v":0.20834243551613199},14.634068283548135,null,0.23149159501792443,14.634068283548135,"",{"$f":"Auswertung_Leistung!Q302","v":12.480288994803733},{"$f":"IF($AN$11=1,AB52*Auswertung_Leistung!Y302,AB52*Auswertung_Leistung!AB302)","v":8.0111968228337727},{"$f":"Auswertung_Leistung!R302","v":12.077433889115708},{"$f":"Auswertung_Leistung!S302","v":19.263458040907967},null,{"$f":"IF(C52=\"\",\"\",$BH$10*F52^$BI$10)","v":2.9070844090284653E+101},null,{"$f":"Auswertung_Leistung!U302","v":11.395074504856202},{"$f":"Auswertung_Leistung!V302","v":33.205777924310411},{"$f":"Auswertung_Leistung!W302","v":45},{"$f":"Auswertung_Leistung!X302","v":305},null,null,null,null,null,null,null,null,null,2,50,124.80288994803732,174.80288994803732,241.54867778231417,291.54867778231414,0,320.44787291335092,320.44787291335092,23.502783332746802,"292W ; 175W",52,52,48,null,null,"Dichte Luft_Trocken (T_Anszaug_Druck)",{"$f":"dichteLuft(0,Torr_in_Pa(BM26),BM27)","v":{"$error":"#NAME?"}},"kg/m³",null,null,{"$error":"#NAME?"},-143.72048303584515,44.750533670225003,2.4833814467383464,2483381.4467383465,0.20834243551613199,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},14.634068283548135,{"$error":"#NAME?"},999.18041614218578,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"}]
[null,2,120,{"$f":"Auswertung_Leistung!C303","v":19.714783300680438},19.714783300680438,{"$f":"IF(C53=\"\",\"\",IF($AQ$7=1,D53,C53))","v":120},{"$f":"Auswertung_Leistung!K303","v":63.7559727987841},{"$f":"IFERROR(IF(OR(C53=\"\",C53=0,Auswertung_Leistung!T303<20),\"<20\",Auswertung_Leistung!T303),\"\")","v":23.502783332746802},{"$f":"IFERROR(IF(C53=\"\",\"\",H53-6.5),\"\")","v":17.002783332746802},-50,-124.80288994803732,-174.80288994803732,-385.26916081815932,-241.54867778231417,-291.54867778231414,0,320.44787291335092,320.44787291335092,16.534869528348732,7.0352086190670606,57.253303946456995,{"$f":"IFERROR(BV53,\"\")","v":0.20834243551613199},14.634068283548135,null,{"$f":"IFERROR(V53*1000/15/60,\"\")","v":0.23149159501792443},{"$f":"IFERROR(CA53,\"\")","v":14.634068283548135},{"$f":"IFERROR(CK53,\"\")","v":""},{"$f":"Auswertung_Leistung!Q303","v":12.480288994803733},{"$f":"IF($AN$11=1,AB53*Auswertung_Leistung!Y303,AB53*Auswertung_Leistung!AB303)","v":8.0111968228337727},{"$f":"Auswertung_Leistung!R303","v":12.077433889115708},{"$f":"Auswertung_Leistung!S303","v":19.263458040907967},null,2.9070844090284653E+101,null,{"$f":"Auswertung_Leistung!U303","v":11.395074504856202},{"$f":"Auswertung_Leistung!V303","v":33.205777924310411},{"$f":"Auswertung_Leistung!W303","v":45},{"$f":"Auswertung_Leistung!X303","v":305},null,null,null,null,null,null,null,null,null,2,50,124.80288994803732,174.80288994803732,241.54867778231417,291.54867778231414,0,320.44787291335092,320.44787291335092,23.502783332746802,"292W ; 175W",53,53,48,null,null,"Dichte Wasser (T_Ansuag_Druck)",{"$f":"999.972-7*10^(-3)*(BM27-4)^2","v":996.58399999999995},"kg/m³",null,null,{"$error":"#NAME?"},-143.72048303584515,44.750533670225003,2.4833814467383464,2483381.4467383465,0.20834243551613199,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},14.634068283548135,{"$error":"#NAME?"},999.18041614218578,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"}]
[]
[null,{"$f":"IF(OR(C45<C56,C46<C56,C47<C56,C53<C56,C45>C57,C46>C57,C47>C57,C53>C57),\"Grenzwerte\",\"\")","v":""},0,null,null,null,null,null,null,null,"DpK =",{"$f":"Auswertung_Leistung!E290","v":28.201307810721179},"[kPa]"]
[null,"  Minimal",{"$f":"AP46","v":45},{"$f":"AQ46","v":"Pa"},null,null,null,null,null,null,"DpH =",{"$f":"Auswertung_Leistung!E291","v":1.6},"[kPa]"]
[null,"  Maximal",{"$f":"AP47","v":305},{"$f":"AQ47","v":"Pa"}]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"L_BG1000","v":"Baugröße 1000"}]
[null,"Baugröße 1000",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Schieberstellung","QPK Primärleistung","QSK1) Sekundärleistung","QKges1) Gesamtleistung","QSK2) Sekundärleistung","QKges2) Gesamtleistung","QPH Primärleistung","QSH Sekundärleistung","QGes Gesamtleistung","LWA - Schallleistung"]
[]
[{"$f":"A43","v":"Auswahl"},{"$f":"L_Auslegung","v":"Schieberstellung"},{"$f":"IF($AQ$7=1,$AO$1,$AN$1)","v":"Primärdruck"},{"$f":"IF($AQ$7=2,$AO$1,$AN$1)","v":"Primärvol."},{"$f":"E43","v":"Primärvol."},{"$f":"L_primaerdruck","v":"Primärdruck"},{"$f":"G43","v":"Sekundärvolumenstrom"},"LWA","LA18","QPK","QSK1","QKges1","QTotal2","QSensibel,K2","QKges2","QPH","QSH","Qhges","tKWRL","tKWRL2","tWWRL",{"$f":"V24","v":"Kondensat ²"},{"$f":"W24","v":"Zulufttemp.²"},null,"Tropfen","Zulufttemp.","Taupunkt nach WT","qSK1)","qSH","qSK2)","qtotal2)",{"$f":"Auswertung_Leistung!AD312","v":"Primärdruck Baugröße 800; S5"},null,{"$f":"Auswertung_Leistung!AF312","v":"Kühlleistung \"mit\" Schieber im Vergleich zu \"ohne Schieber\""},"Primärvolumenstrom Minimal","Primärvolumenstrom Minimal","Primärdruck Minimal","Primärdruck Maximal",null,null,null,null,null,null,null,null,null,"Schieberstellung","QPK","QSK1)","QKges1)","QSensibel,K2)","QKges2)","QPH","QSH","Qhges","LWA","QKges2) ; QKges1)","Zeile","Zeile","Spalte",null,null,null,null,null,null,null,"Wassermenge Gesamt in der Luft","latente \nLeistung",null,null,null,"Kondensatmenge",null,null,null,null,"Zulufttemperatur",null,null,null,null,null,null,null,null,null,"Taupunkt im Kasten"]
[null,null,{"$f":"IF($AQ$7=1,$AO$2,$AN$2)","v":"[Pa]"},{"$f":"IF($AQ$7=2,$AO$2,$AN$2)","v":"[m³/h]"},"[m³/h]","[Pa]","[m³/h]","[dB(A)]","[dB(A)]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[°C]","[°C]","[°C]","[kg/h] bzw. [l / h]","[°C]",null,"[Anzahl / min]",{"$f":"CA63","v":"[°C]"},"[°C]","[W]","[W]","[W]","[W]",{"$f":"Auswertung_Leistung!AD313","v":"[Pa]"},null,{"$f":"Auswertung_Leistung!AF313","v":0},"[m³/h]","[m³/h]","[m³/h]","[m³/h]","Grenzen der Auslegung",null,null,"Abhängig von Abfrage",null,null,null,"heizen",null,null,"[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[dB(A)]",null,null,null,null,null,null,null,null,null,null,null,"kg H20 / h","W bzw. J / s",null,null,null,"kg / h bzw.l / h",null,null,null,null,"[°C]",null,null,null,null,null,null,null,null,null,"[°C]"]
[null,5,{"$f":"$J$17","v":120},{"$f":"Auswertung_Leistung!C314","v":96.482713639113214},{"$f":"IF(C64=\"\",\"\",IF($AQ$7=1,C64,D64))","v":96.482713639113214},{"$f":"IF(C64=\"\",\"\",IF($AQ$7=1,D64,C64))","v":120},{"$f":"Auswertung_Leistung!K314","v":196.0291977444933},{"$f":"IFERROR(IF(OR(C64=\"\",C64=0,Auswertung_Leistung!T314<20),\"<20\",Auswertung_Leistung!T314),\"\")","v":29.057232918327411},{"$f":"IFERROR(IF(C64=\"\",\"\",H64-6.5),\"\")","v":22.557232918327411},{"$f":"ROUND(E64*1.2*1004.5*($J$16-$J$15)/3600,-1)","v":-260},{"$f":"IF(C64=\"\",\"\",IF(C64=0,,IFERROR((AB64*($J$7-$J$6)),\"\")))","v":-509.28507066104254},{"$f":"J64+K64","v":-769.28507066104248},{"$f":"IFERROR(AE64*($J$8-$J$6),\"\")","v":-1446.7350705697604},{"$f":"IFERROR(AD64*($J$8-$J$6),\"\")","v":-947.97501550470531},{"$f":"J64+N64","v":-1207.9750155047054},{"$f":"ROUND(E64*1.2*1004.5*($Q$16-$Q$15)/3600,-1)","v":0},{"$f":"IF(G64=0,,IFERROR((AC64*($Q$7-$Q$6)),\"\"))","v":1097.9374058768844},{"$f":"Q64+P64","v":1097.9374058768844},{"$f":"IF(IFERROR(IF(K64=0,,$J$7-((K64/(4.2*$J$13/3.6)))),)=0,\"\",IFERROR(IF(K64=0,,$J$7-((K64/(4.2*$J$13/3.6)))),))","v":18.182650302833039},{"$f":"IF(IFERROR(IF(N64=0,,$J$8-((N64/(4.2*$J$13/3.6)))),)=0,\"\",IFERROR(IF(N64=0,,$J$8-((N64/(4.2*$J$13/3.6)))),))","v":10.062750066448737},{"$f":"IF(C64=\"\",\"\",IFERROR(IF(Q64=0,,($Q$7-((Q64/(4.2*$Q$13/3.6))))),))","v":50.589107949626708},{"$f":"IFERROR(BV64,\"\")","v":0.72302070251529071},{"$f":"Z64","v":11.492339512499969},null,{"$f":"IFERROR(V64*1000/15/60,\"\")","v":0.80335633612810076},{"$f":"IFERROR(CA64,\"\")","v":11.492339512499969},{"$f":"IFERROR(CK64,\"\")","v":""},{"$f":"Auswertung_Leistung!Q314","v":50.928507066104252},{"$f":"IF($AN$11=1,AB64*Auswertung_Leistung!Y314,AB64*Auswertung_Leistung!AB314)","v":27.448435146922112},{"$f":"Auswertung_Leistung!R314","v":47.398750775235264},{"$f":"Auswertung_Leistung!S314","v":72.336753528488018},{"$f":"Auswertung_Leistung!AD314","v":120.00162820198784},null,{"$f":"Auswertung_Leistung!AF314","v":-7.488003676781041E-6},{"$f":"Auswertung_Leistung!U314","v":59.513593159203481},{"$f":"Auswertung_Leistung!V314","v":152.76083145436922},{"$f":"Auswertung_Leistung!W314","v":45},{"$f":"Auswertung_Leistung!X314","v":305},{"$f":"$AM$96","v":"Primärdurck"},"Primärvolumenstrom",{"$f":"$AO$96","v":"Wassermassenstrom"},{"$f":"IF($AQ$7=1,AN64,AM64)","v":"Primärdurck"},"Einheit",{"$f":"IF($AQ$7=2,AN64,AM64)","v":"Primärvolumenstrom"},"Einheit",{"$f":"AT96","v":"Wassermassenstrom"},null,{"$f":"IF(OR(F64<$AM$65,F64>$AM$66),\"\",B64)","v":5},{"$f":"IF(AV64=\"\",\"\",ABS(J64))","v":260},{"$f":"IF(AV64=\"\",\"\",ABS(K64))","v":509.28507066104254},{"$f":"IF(AV64=\"\",\"\",ABS(L64))","v":769.28507066104248},{"$f":"IF(AV64=\"\",\"\",ABS(N64))","v":947.97501550470531},{"$f":"IF(AV64=\"\",\"\",(AW64+AZ64))","v":1207.9750155047054},{"$f":"IF(AV64=\"\",\"\",(P64))","v":0},{"$f":"IF(AV64=\"\",\"\",ABS(Q64))","v":1097.9374058768844},{"$f":"IF(AV64=\"\",\"\",(BB64+BC64))","v":1097.9374058768844},{"$f":"IF(AV64=\"\",\"\",H64)","v":29.057232918327411},{"$f":"IF(AV64=\"\",\"\",CONCATENATE(ROUND(BA64,0),\" ; \",ROUND(AY64,0)))","v":"1208 ; 769"},{"$f":"IF(AV64=\"\",\"\",ROW(AV64))","v":64},{"$f":"MIN(BG64:BG72)","v":64},{"$f":"COLUMN(AV64)","v":48},null,null,null,null,null,null,null,{"$f":"$BM$37*(G64*$BM$28)","v":{"$error":"#NAME?"}},{"$f":"M64-N64","v":-498.7600550650551},{"$f":"50.09-0.9298*(273.15+$J$8)/1000-65.19*((273.15+$J$8)/1000)^2","v":44.750533670225003},{"$f":"BS64/$BM$31","v":2.4833814467383464},{"$f":"BT64*1000000","v":2483381.4467383465},{"$f":"ABS(BR64)/BU64*3600","v":0.72302070251529071},{"$f":"BQ64/$BM$53","v":{"$error":"#NAME?"}},{"$f":"G64-BW64","v":{"$error":"#NAME?"}},{"$f":"BX64*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BQ64-BV64","v":{"$error":"#NAME?"}},{"$f":"N64*3/G64+$BM$27","v":11.492339512499969},{"$f":"dichteLuft(0,Torr_in_Pa($BM$26),CA64)","v":{"$error":"#NAME?"}},{"$f":"999.972-7*10^(-3)*(CA64-4)^2","v":999.57905394040597},{"$f":"BY64/CB64*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BZ64/CC64*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BZ64+BY64","v":{"$error":"#NAME?"}},{"$f":"CD64+CE64","v":{"$error":"#NAME?"}},{"$f":"CF64/CG64","v":{"$error":"#NAME?"}},{"$f":"BZ64/CG64/CH64","v":{"$error":"#NAME?"}},{"$f":"rf_prozent_von_T_grad_x_hf_gH2O_kg_trLuft(CA64,CI64*1000)","v":{"$error":"#NAME?"}},{"$f":"td_T_grad_rf_prozent(CA64,CJ64)","v":{"$error":"#NAME?"}}]
[null,4.5,{"$f":"C64","v":120},{"$f":"Auswertung_Leistung!C315","v":115.86092714292349},115.86092714292349,{"$f":"IF(C65=\"\",\"\",IF($AQ$7=1,D65,C65))","v":120},{"$f":"Auswertung_Leistung!K315","v":185.118780540784},{"$f":"IFERROR(IF(OR(C65=\"\",C65=0,Auswertung_Leistung!T315<20),\"<20\",Auswertung_Leistung!T315),\"\")","v":28.803735575209807},{"$f":"IFERROR(IF(C65=\"\",\"\",H65-6.5),\"\")","v":22.303735575209807},{"$f":"ROUND(E65*1.2*1004.5*($J$16-$J$15)/3600,-1)","v":-310},-468.33529366015807,{"$f":"J65+K65","v":-778.33529366015807},-1340.8832908002139,-874.68403069621331,{"$f":"J65+N65","v":-1184.6840306962133},0,1022.9622811052338,{"$f":"Q65+P65","v":1022.9622811052338},18.007151258543534,9.7486458458409153,51.23175187624085,{"$f":"IFERROR(BV65,\"\")","v":0.67581939076604236},{"$f":"Z65","v":11.825035772042975},null,{"$f":"IFERROR(V65*1000/15/60,\"\")","v":0.75091043418449155},{"$f":"IFERROR(CA65,\"\")","v":11.825035772042975},{"$f":"IFERROR(CK65,\"\")","v":""},{"$f":"Auswertung_Leistung!Q315","v":46.83352936601581},{"$f":"IF($AN$11=1,AB65*Auswertung_Leistung!Y315,AB65*Auswertung_Leistung!AB315)","v":25.574057027630847},{"$f":"Auswertung_Leistung!R315","v":43.734201534810666},{"$f":"Auswertung_Leistung!S315","v":67.044164540010698},{"$f":"Auswertung_Leistung!AD315","v":173.99655111742987},null,{"$f":"Auswertung_Leistung!AF315","v":-0.22944094679366123},{"$f":"Auswertung_Leistung!U315","v":70.388300727868028},{"$f":"Auswertung_Leistung!V315","v":186.11418468474636},{"$f":"Auswertung_Leistung!W315","v":45},{"$f":"Auswertung_Leistung!X315","v":305},{"$f":"AM97","v":45},{"$f":"MIN(AI64:AI72)","v":13.618503676535461},{"$f":"AO97","v":50},{"$f":"IF($AQ$7=1,AN65,AM65)","v":45},{"$f":"IF($AQ$7=1,\"m³/h\",\"Pa\")","v":"Pa"},{"$f":"IF($AQ$7=2,AN65,AM65)","v":13.618503676535461},{"$f":"IF($AQ$7=2,\"m³/h\",\"Pa\")","v":"m³/h"},{"$f":"AT97","v":50},null,{"$f":"IF(OR(F65<$AM$65,F65>$AM$66),\"\",B65)","v":4.5},{"$f":"IF(AV65=\"\",\"\",ABS(J65))","v":310},468.33529366015807,778.33529366015807,874.68403069621331,1184.6840306962133,0,1022.9622811052338,1022.9622811052338,28.803735575209807,{"$f":"IF(AV65=\"\",\"\",CONCATENATE(ROUND(BA65,0),\" ; \",ROUND(AY65,0)))","v":"1185 ; 778"},{"$f":"IF(AV65=\"\",\"\",ROW(AV65))","v":65},{"$f":"IF(COUNTIF($BG$64:$BG$72,BH64+1)=1,BH64+1,IF(COUNTIF($BG$64:$BG$72,BH64+2)=1,BH64+2,IF(COUNTIF($BG$64:$BG$72,BH64+3)=1,BH64+3,IF(COUNTIF($BG$64:$BG$72,BH64+4)=1,BH64+4,IF(COUNTIF($BG$64:$BG$72,BH64+5)=1,BH64+5,IF(COUNTIF($BG$64:$BG$72,BH64+6)=1,BH64+6,IF(COUNTIF($BG$64:$BG$72,BH64+7)=1,BH64+7,IF(COUNTIF($BG$64:$BG$72,BH64+8)=1,BH64+8,\"\"))))))))","v":65},48,null,null,null,null,null,null,null,{"$error":"#NAME?"},{"$f":"M65-N65","v":-466.19926010400059},44.750533670225003,2.4833814467383464,{"$f":"BT65*1000000","v":2483381.4467383465},{"$f":"ABS(BR65)/BU65*3600","v":0.67581939076604236},{"$f":"BQ65/$BM$53","v":{"$error":"#NAME?"}},{"$error":"#NAME?"},{"$f":"BX65*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BQ65-BV65","v":{"$error":"#NAME?"}},11.825035772042975,{"$error":"#NAME?"},{"$f":"999.972-7*10^(-3)*(CA65-4)^2","v":999.5433817061637},{"$f":"BY65/CB65*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BZ65/CC65*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BZ65+BY65","v":{"$error":"#NAME?"}},{"$f":"CD65+CE65","v":{"$error":"#NAME?"}},{"$f":"CF65/CG65","v":{"$error":"#NAME?"}},{"$f":"BZ65/CG65/CH65","v":{"$error":"#NAME?"}},{"$f":"rf_prozent_von_T_grad_x_hf_gH2O_kg_trLuft(CA65,CI65*1000)","v":{"$error":"#NAME?"}},{"$f":"td_T_grad_rf_prozent(CA65,CJ65)","v":{"$error":"#NAME?"}}]
[null,4,{"$f":"C65","v":120},{"$f":"Auswertung_Leistung!C316","v":72.639820961817136},72.639820961817136,120,{"$f":"Auswertung_Leistung!K316","v":118.22909580860819},{"$f":"IFERROR(IF(OR(C66=\"\",C66=0,Auswertung_Leistung!T316<20),\"<20\",Auswertung_Leistung!T316),\"\")","v":27.688118985404049},21.188118985404049,-190,-327.7829183735912,-517.7829183735912,-983.76728287224512,-625.56483166038686,-815.56483166038686,0,794.31809850960622,794.31809850960622,17.404783935886819,8.6809921356873723,53.19155915563195,{"$f":"IFERROR(BV66,\"\")","v":0.5192632916124692},10.126627357286113,null,{"$f":"IFERROR(V66*1000/15/60,\"\")","v":0.57695921290274355},{"$f":"IFERROR(CA66,\"\")","v":10.126627357286113},{"$f":"IFERROR(CK66,\"\")","v":""},{"$f":"Auswertung_Leistung!Q316","v":32.77829183735912},{"$f":"IF($AN$11=1,AB66*Auswertung_Leistung!Y316,AB66*Auswertung_Leistung!AB316)","v":19.857952462740155},{"$f":"Auswertung_Leistung!R316","v":31.278241583019344},{"$f":"Auswertung_Leistung!S316","v":49.188364143612255},{"$f":"Auswertung_Leistung!AD316","v":67.444862186503812},null,{"$f":"Auswertung_Leistung!AF316","v":-6.606990840132354E-2},{"$f":"Auswertung_Leistung!U316","v":43.778281042403769},{"$f":"Auswertung_Leistung!V316","v":117.57810761960125},{"$f":"Auswertung_Leistung!W316","v":45},{"$f":"Auswertung_Leistung!X316","v":305},{"$f":"AM98","v":305},{"$f":"MAX(AJ64:AJ72)","v":186.11418468474636},{"$f":"AO98","v":300},{"$f":"IF($AQ$7=1,AN66,AM66)","v":305},{"$f":"IF($AQ$7=1,\"m³/h\",\"Pa\")","v":"Pa"},{"$f":"IF($AQ$7=2,AN66,AM66)","v":186.11418468474636},{"$f":"IF($AQ$7=2,\"m³/h\",\"Pa\")","v":"m³/h"},{"$f":"AT98","v":300},null,4,190,327.7829183735912,517.7829183735912,625.56483166038686,815.56483166038686,0,794.31809850960622,794.31809850960622,27.688118985404049,"816 ; 518",{"$f":"IF(AV66=\"\",\"\",ROW(AV66))","v":66},{"$f":"IF(COUNTIF($BG$64:$BG$72,BH65+1)=1,BH65+1,IF(COUNTIF($BG$64:$BG$72,BH65+2)=1,BH65+2,IF(COUNTIF($BG$64:$BG$72,BH65+3)=1,BH65+3,IF(COUNTIF($BG$64:$BG$72,BH65+4)=1,BH65+4,IF(COUNTIF($BG$64:$BG$72,BH65+5)=1,BH65+5,IF(COUNTIF($BG$64:$BG$72,BH65+6)=1,BH65+6,IF(COUNTIF($BG$64:$BG$72,BH65+7)=1,BH65+7,IF(COUNTIF($BG$64:$BG$72,BH65+8)=1,BH65+8,\"\"))))))))","v":66},48,null,null,null,null,null,null,null,{"$error":"#NAME?"},-358.20245121185826,44.750533670225003,2.4833814467383464,2483381.4467383465,0.5192632916124692,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},10.126627357286113,{"$error":"#NAME?"},999.70925106057462,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"}]
[null,3.5,120,{"$f":"Auswertung_Leistung!C317","v":72.494045193250557},72.494045193250557,120,{"$f":"Auswertung_Leistung!K317","v":97.55429495543396},{"$f":"IFERROR(IF(OR(C67=\"\",C67=0,Auswertung_Leistung!T317<20),\"<20\",Auswertung_Leistung!T317),\"\")","v":28.794444206383346},22.294444206383346,-190,-252.08976554421469,-442.08976554421469,-767.28588710405677,-484.43342270160423,-674.43342270160429,0,635.93538827732561,635.93538827732561,17.080384709475204,8.0761432401497331,54.549125243337208,0.41003321225026285,11.102652130603492,null,{"$f":"IFERROR(V67*1000/15/60,\"\")","v":0.45559245805584764},{"$f":"IFERROR(CA67,\"\")","v":11.102652130603492},{"$f":"IFERROR(CK67,\"\")","v":""},{"$f":"Auswertung_Leistung!Q317","v":25.208976554421469},{"$f":"IF($AN$11=1,AB67*Auswertung_Leistung!Y317,AB67*Auswertung_Leistung!AB317)","v":15.898384706933141},{"$f":"Auswertung_Leistung!R317","v":24.221671135080211},{"$f":"Auswertung_Leistung!S317","v":38.364294355202837},{"$f":"Auswertung_Leistung!AD317","v":67.170395260763343},null,{"$f":"Auswertung_Leistung!AF317","v":-0.28063933543970909},{"$f":"Auswertung_Leistung!U317","v":43.349612142842396},{"$f":"Auswertung_Leistung!V317","v":118.21936427874542},{"$f":"Auswertung_Leistung!W317","v":45},{"$f":"Auswertung_Leistung!X317","v":305},null,null,null,{"$f":"AVERAGE(AP65:AP66)","v":175},null,{"$f":"AVERAGE(AR65:AR66)","v":99.866344180640908},null,null,null,3.5,190,252.08976554421469,442.08976554421469,484.43342270160423,674.43342270160429,0,635.93538827732561,635.93538827732561,28.794444206383346,"674 ; 442",{"$f":"IF(AV67=\"\",\"\",ROW(AV67))","v":67},67,48,null,null,null,null,null,null,null,{"$error":"#NAME?"},-282.85246440245254,44.750533670225003,2.4833814467383464,2483381.4467383465,0.41003321225026285,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},11.102652130603492,{"$error":"#NAME?"},999.61886632898143,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"}]
[null,3,120,{"$f":"Auswertung_Leistung!C318","v":47.760763136741268},47.760763136741268,120,{"$f":"Auswertung_Leistung!K318","v":103.19989663935623},{"$f":"IFERROR(IF(OR(C68=\"\",C68=0,Auswertung_Leistung!T318<20),\"<20\",Auswertung_Leistung!T318),\"\")","v":29.124953649228789},22.624953649228789,-130,-269.75024663498857,-399.75024663498857,-817.92476689644241,-517.39448063743032,-647.39448063743032,0,672.81554459219763,672.81554459219763,17.156072485578523,8.2174049170175589,54.233009617781164,0.43565962528769564,10.959447708202919,null,0.48406625031966183,10.959447708202919,"",{"$f":"Auswertung_Leistung!Q318","v":26.975024663498857},{"$f":"IF($AN$11=1,AB68*Auswertung_Leistung!Y318,AB68*Auswertung_Leistung!AB318)","v":16.820388614804941},{"$f":"Auswertung_Leistung!R318","v":25.869724031871517},{"$f":"Auswertung_Leistung!S318","v":40.896238344822123},{"$f":"Auswertung_Leistung!AD318","v":28.793385541619394},null,{"$f":"Auswertung_Leistung!AF318","v":0.55710581894625544},{"$f":"Auswertung_Leistung!U318","v":28.353008475239726},{"$f":"Auswertung_Leistung!V318","v":78.425646112026996},{"$f":"Auswertung_Leistung!W318","v":45},{"$f":"Auswertung_Leistung!X318","v":305},null,null,null,null,null,null,null,null,null,3,130,269.75024663498857,399.75024663498857,517.39448063743032,647.39448063743032,0,672.81554459219763,672.81554459219763,29.124953649228789,"647 ; 400",68,68,48,null,null,null,null,null,null,null,{"$error":"#NAME?"},-300.53028625901209,44.750533670225003,2.4833814467383464,2483381.4467383465,0.43565962528769564,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},10.959447708202919,{"$error":"#NAME?"},999.63296261317748,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"}]
[null,2.5,120,{"$f":"Auswertung_Leistung!C319","v":60.495568118699801},60.495568118699801,120,{"$f":"Auswertung_Leistung!K319","v":95.373538088171728},{"$f":"IFERROR(IF(OR(C69=\"\",C69=0,Auswertung_Leistung!T319<20),\"<20\",Auswertung_Leistung!T319),\"\")","v":27.03953810929886},20.53953810929886,-160,-247.29622161434332,-407.29622161434332,-753.79631441303843,-475.56830738912561,-635.56830738912561,0,626.62621982994108,626.62621982994108,17.059840949775758,8.0381498888105387,54.62891811574336,0.4033294307653007,11.04087243939294,null,0.4481438119614452,11.04087243939294,"",{"$f":"Auswertung_Leistung!Q319","v":24.729622161434332},{"$f":"IF($AN$11=1,AB69*Auswertung_Leistung!Y319,AB69*Auswertung_Leistung!AB319)","v":15.665655495748528},{"$f":"Auswertung_Leistung!R319","v":23.77841536945628},{"$f":"Auswertung_Leistung!S319","v":37.689815720651922},{"$f":"Auswertung_Leistung!AD319","v":46.523140578089006},null,{"$f":"Auswertung_Leistung!AF319","v":-5.6888396478586234E-2},{"$f":"Auswertung_Leistung!U319","v":35.878247733563668},{"$f":"Auswertung_Leistung!V319","v":99.428311429669819},{"$f":"Auswertung_Leistung!W319","v":45},{"$f":"Auswertung_Leistung!X319","v":305},null,null,null,null,null,null,null,null,null,2.5,160,247.29622161434332,407.29622161434332,475.56830738912561,635.56830738912561,0,626.62621982994108,626.62621982994108,27.03953810929886,"636 ; 407",69,69,48,null,null,null,null,null,null,null,{"$error":"#NAME?"},-278.22800702391282,44.750533670225003,2.4833814467383464,2483381.4467383465,0.4033294307653007,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},11.04087243939294,{"$error":"#NAME?"},999.6249828070454,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"}]
[null,2,120,{"$f":"Auswertung_Leistung!C320","v":23.561570286179059},23.561570286179059,{"$f":"IF(C70=\"\",\"\",IF($AQ$7=1,D70,C70))","v":120},{"$f":"Auswertung_Leistung!K320","v":76.196162613180988},{"$f":"IFERROR(IF(OR(C70=\"\",C70=0,Auswertung_Leistung!T320<20),\"<20\",Auswertung_Leistung!T320),\"\")","v":21.628727335739217},{"$f":"IFERROR(IF(C70=\"\",\"\",H70-6.5),\"\")","v":15.128727335739217},-60,-155.94577699755089,-215.94577699755089,-481.40791180394535,-301.82391012882488,-361.82391012882488,0,411.62781137536683,411.62781137536683,16.668339044275218,7.2935310434092493,56.471761616782572,0.26033149554191315,14.116570450099815,null,0.28925721726879239,14.116570450099815,"",{"$f":"Auswertung_Leistung!Q320","v":15.59457769975509},{"$f":"IF($AN$11=1,AB70*Auswertung_Leistung!Y320,AB70*Auswertung_Leistung!AB320)","v":10.290695284384171},{"$f":"Auswertung_Leistung!R320","v":15.091195506441245},{"$f":"Auswertung_Leistung!S320","v":24.070395590197268},{"$f":"Auswertung_Leistung!AD320","v":6.8608232203697046},null,{"$f":"Auswertung_Leistung!AF320","v":2.4812794303879917},{"$f":"Auswertung_Leistung!U320","v":13.618503676535461},{"$f":"Auswertung_Leistung!V320","v":39.68495410466366},{"$f":"Auswertung_Leistung!W320","v":45},{"$f":"Auswertung_Leistung!X320","v":305},null,null,null,null,null,null,null,null,null,2,60,155.94577699755089,215.94577699755089,301.82391012882488,361.82391012882488,0,411.62781137536683,411.62781137536683,21.628727335739217,"362 ; 216",70,70,48,null,null,null,null,null,null,null,{"$error":"#NAME?"},-179.58400167512048,44.750533670225003,2.4833814467383464,2483381.4467383465,0.26033149554191315,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},14.116570450099815,{"$error":"#NAME?"},999.25558501629712,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"}]
[null,2,{"$f":"C70","v":120},{"$f":"Auswertung_Leistung!C321","v":23.561570286179059},23.561570286179059,{"$f":"IF(C71=\"\",\"\",IF($AQ$7=1,D71,C71))","v":120},{"$f":"Auswertung_Leistung!K321","v":76.196162613180988},{"$f":"IFERROR(IF(OR(C71=\"\",C71=0,Auswertung_Leistung!T321<20),\"<20\",Auswertung_Leistung!T321),\"\")","v":24.276905565834582},17.776905565834582,-60,-155.94577699755089,-215.94577699755089,-481.40791180394535,-301.82391012882488,-361.82391012882488,0,411.62781137536683,411.62781137536683,16.668339044275218,7.2935310434092493,56.471761616782572,{"$f":"IFERROR(BV71,\"\")","v":0.26033149554191315},14.116570450099815,null,0.28925721726879239,14.116570450099815,"",{"$f":"Auswertung_Leistung!Q321","v":15.59457769975509},{"$f":"IF($AN$11=1,AB71*Auswertung_Leistung!Y321,AB71*Auswertung_Leistung!AB321)","v":10.290695284384171},{"$f":"Auswertung_Leistung!R321","v":15.091195506441245},{"$f":"Auswertung_Leistung!S321","v":24.070395590197268},null,{"$f":"IF(C71=\"\",\"\",$BH$10*F71^$BI$10)","v":2.9070844090284653E+101},null,{"$f":"Auswertung_Leistung!U321","v":13.618503676535461},{"$f":"Auswertung_Leistung!V321","v":39.68495410466366},{"$f":"Auswertung_Leistung!W321","v":45},{"$f":"Auswertung_Leistung!X321","v":305},null,null,null,null,null,null,null,null,null,2,60,155.94577699755089,215.94577699755089,301.82391012882488,361.82391012882488,0,411.62781137536683,411.62781137536683,24.276905565834582,"362 ; 216",71,71,48,null,null,null,null,null,null,null,{"$error":"#NAME?"},-179.58400167512048,44.750533670225003,2.4833814467383464,2483381.4467383465,0.26033149554191315,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},14.116570450099815,{"$error":"#NAME?"},999.25558501629712,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"}]
[null,2,120,{"$f":"Auswertung_Leistung!C322","v":23.561570286179059},23.561570286179059,{"$f":"IF(C72=\"\",\"\",IF($AQ$7=1,D72,C72))","v":120},{"$f":"Auswertung_Leistung!K322","v":76.196162613180988},{"$f":"IFERROR(IF(OR(C72=\"\",C72=0,Auswertung_Leistung!T322<20),\"<20\",Auswertung_Leistung!T322),\"\")","v":24.276905565834582},17.776905565834582,-60,-155.94577699755089,-215.94577699755089,-481.40791180394535,-301.82391012882488,-361.82391012882488,0,411.62781137536683,411.62781137536683,16.668339044275218,7.2935310434092493,56.471761616782572,{"$f":"IFERROR(BV72,\"\")","v":0.26033149554191315},14.116570450099815,null,{"$f":"IFERROR(V72*1000/15/60,\"\")","v":0.28925721726879239},{"$f":"IFERROR(CA72,\"\")","v":14.116570450099815},{"$f":"IFERROR(CK72,\"\")","v":""},{"$f":"Auswertung_Leistung!Q322","v":15.59457769975509},{"$f":"IF($AN$11=1,AB72*Auswertung_Leistung!Y322,AB72*Auswertung_Leistung!AB322)","v":10.290695284384171},{"$f":"Auswertung_Leistung!R322","v":15.091195506441245},{"$f":"Auswertung_Leistung!S322","v":24.070395590197268},null,2.9070844090284653E+101,null,{"$f":"Auswertung_Leistung!U322","v":13.618503676535461},{"$f":"Auswertung_Leistung!V322","v":39.68495410466366},{"$f":"Auswertung_Leistung!W322","v":45},{"$f":"Auswertung_Leistung!X322","v":305},null,null,null,null,null,null,null,null,null,2,60,155.94577699755089,215.94577699755089,301.82391012882488,361.82391012882488,0,411.62781137536683,411.62781137536683,24.276905565834582,"362 ; 216",72,72,48,null,null,null,null,null,null,null,{"$error":"#NAME?"},-179.58400167512048,44.750533670225003,2.4833814467383464,2483381.4467383465,0.26033149554191315,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},14.116570450099815,{"$error":"#NAME?"},{"$f":"999.972-7*10^(-3)*(CA72-4)^2","v":999.25558501629712},{"$f":"BY72/CB72*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BZ72/CC72*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BZ72+BY72","v":{"$error":"#NAME?"}},{"$f":"CD72+CE72","v":{"$error":"#NAME?"}},{"$f":"CF72/CG72","v":{"$error":"#NAME?"}},{"$f":"BZ72/CG72/CH72","v":{"$error":"#NAME?"}},{"$f":"rf_prozent_von_T_grad_x_hf_gH2O_kg_trLuft(CA72,CI72*1000)","v":{"$error":"#NAME?"}},{"$f":"td_T_grad_rf_prozent(CA72,CJ72)","v":{"$error":"#NAME?"}}]
[]
[null,{"$f":"IF(OR(C64<C75,C65<C75,C66<C75,C72<C75,C64>C76,C65>C76,C66>C76,C72>C76),\"Grenzwerte\",\"\")","v":""},null,null,null,null,null,null,null,null,"DpK =",{"$f":"Auswertung_Leistung!E309","v":33.328818321761396},"[kPa]"]
[null,"  Minimal",{"$f":"AP65","v":45},{"$f":"AQ65","v":"Pa"},null,null,null,null,null,null,"DpH =",{"$f":"Auswertung_Leistung!E310","v":1.8},"[kPa]"]
[null,"  Maximal",{"$f":"AP66","v":305},{"$f":"AQ66","v":"Pa"}]
[]
[]
[null," Baugröße 1200"]
[]
[null,{"$f":"L_Auslegung","v":"Schieberstellung"},{"$f":"IF($AQ$7=1,$AO$1,$AN$1)","v":"Primärdruck"},{"$f":"IF($AQ$7=2,$AO$1,$AN$1)","v":"Primärvol."},{"$f":"E62","v":"Primärvol."},{"$f":"L_primaerdruck","v":"Primärdruck"},{"$f":"G62","v":"Sekundärvolumenstrom"},"LWA","LA18","QPK","QSK1)","QKges1)","QTotal2)","QSensibel,K2)","QKges2)","QPH","QSH","Qhges","tKWRL","tKWRL2)","tWWRL",{"$f":"V43","v":"Kondensat ²"},{"$f":"W43","v":"Zulufttemp.²"},null,"Tropfen","Zulufttemp.","Taupunkt nach WT","qSK1)","qSH","qSK2)","qtotal2)","Steuerspannung (mit Filter)","dp / rho",null,"Primärvolumenstrom Minimal","Primärvolumenstrom Minimal","Primärdruck Minimal","Primärdruck Maximal",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Wassermenge Gesamt in der Luft","latente \nLeistung",null,null,null,"Kondensatmenge",null,null,null,null,"Zulufttemperatur",null,null,null,null,null,null,null,null,null,"Taupunkt im Kasten"]
[null,null,{"$f":"IF($AQ$7=1,$AO$2,$AN$2)","v":"[Pa]"},{"$f":"IF($AQ$7=2,$AO$2,$AN$2)","v":"[m³/h]"},"[m³/h]","[Pa]","[m³/h]","[dB(A)]","[dB(A)]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[°C]","[°C]","[°C]","[kg/h] bzw. [l / h]","[°C]",null,"[Anzahl / min]",{"$f":"CA82","v":"[°C]"},"[°C]","[W]","[W]","[W]","[W]","[V]","[(Pa*m³)/kg]",null,"[m³/h]","[m³/h]","[m³/h]","[m³/h]","Grenzen der Auslegung",null,null,null,null,null,null,"heizen",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"kg H20 / h","W bzw. J / s",null,null,null,"kg / h bzw.l / h",null,null,null,null,"[°C]",null,null,null,null,null,null,null,null,null,"[°C]"]
[null,5,{"$f":"J17","v":120},{"$f":"Auswertung_Leistung!C333","v":118.14209833360803},{"$f":"IF(C83=\"\",\"\",IF($AQ$7=1,C83,D83))","v":118.14209833360803},{"$f":"IF(C83=\"\",\"\",IF($AQ$7=1,D83,C83))","v":120},{"$f":"Auswertung_Leistung!K333","v":240.0357523401959},{"$f":"IFERROR(IF(OR(C83=\"\",C83=0,Auswertung_Leistung!T333<20),\"<20\",Auswertung_Leistung!T333),\"\")","v":29.936784621878711},{"$f":"IFERROR(IF(C83=\"\",\"\",H83-6.5),\"\")","v":23.436784621878711},{"$f":"ROUND(E83*1.2*1004.5*($J$16-$J$15)/3600,-1)","v":-320},{"$f":"IF(C83=\"\",\"\",IF(C83=0,,IFERROR((AB83*($J$7-$J$6)),\"\")))","v":-596.53189158138866},{"$f":"J83+K83","v":-916.53189158138866},{"$f":"IFERROR(AE83*($J$8-$J$6),\"\")","v":-1694.5786514886927},{"$f":"IFERROR(AD83*($J$8-$J$6),\"\")","v":-1110.3748406308341},{"$f":"J83+N83","v":-1430.3748406308341},{"$f":"ROUND(E83*1.2*1004.5*($Q$16-$Q$15)/3600,-1)","v":0},{"$f":"IF(G83=0,,IFERROR((AC83*($Q$7-$Q$6)),\"\"))","v":1272.4119896464456},{"$f":"Q83+P83","v":1272.4119896464456},{"$f":"IF(IFERROR(IF(K83=0,,$J$7-((K83/(4.2*$J$13/3.6)))),)=0,\"\",IFERROR(IF(K83=0,,$J$7-((K83/(4.2*$J$13/3.6)))),))","v":18.556565249634524},{"$f":"IF(IFERROR(IF(N83=0,,$J$8-((N83/(4.2*$J$13/3.6)))),)=0,\"\",IFERROR(IF(N83=0,,$J$8-((N83/(4.2*$J$13/3.6)))),))","v":10.75874931698929},{"$f":"IF(C83=\"\",\"\",IFERROR(IF(Q83=0,,($Q$7-((Q83/(4.2*$Q$13/3.6))))),))","v":49.093611517316177},{"$f":"IFERROR(BV83,\"\")","v":0.84688307623886372},{"$f":"Z83","v":12.122381814308255},null,{"$f":"IFERROR(V83*1000/15/60,\"\")","v":0.94098119582095974},{"$f":"IFERROR(CA83,\"\")","v":12.122381814308255},{"$f":"IFERROR(CK83,\"\")","v":""},{"$f":"Auswertung_Leistung!Q333","v":59.653189158138872},{"$f":"IF($AN$11=1,AB83*Auswertung_Leistung!Y333,AB83*Auswertung_Leistung!AB333)","v":31.810299741161142},{"$f":"Auswertung_Leistung!R333","v":55.518742031541706},{"$f":"Auswertung_Leistung!S333","v":84.728932574434637},null,{"$f":"IF(C83=\"\",\"\",$BH$10*F83^$BI$10)","v":2.9070844090284653E+101},null,{"$f":"Auswertung_Leistung!U333","v":72.873787541881811},{"$f":"Auswertung_Leistung!V333","v":187.0540793318807},{"$f":"Auswertung_Leistung!W333","v":45},{"$f":"Auswertung_Leistung!X333","v":305},{"$f":"$AM$96","v":"Primärdurck"},null,{"$f":"$AO$96","v":"Wassermassenstrom"},null,null,null,null,{"$f":"AT64","v":"Wassermassenstrom"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"$BM$37*(G83*$BM$28)","v":{"$error":"#NAME?"}},{"$f":"M83-N83","v":-584.20381085785857},{"$f":"50.09-0.9298*(273.15+$J$8)/1000-65.19*((273.15+$J$8)/1000)^2","v":44.750533670225003},{"$f":"BS83/$BM$31","v":2.4833814467383464},{"$f":"BT83*1000000","v":2483381.4467383465},{"$f":"ABS(BR83)/BU83*3600","v":0.84688307623886372},{"$f":"BQ83/$BM$53","v":{"$error":"#NAME?"}},{"$f":"G83-BW83","v":{"$error":"#NAME?"}},{"$f":"BX83*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BQ83-BV83","v":{"$error":"#NAME?"}},{"$f":"N83*3/G83+$BM$27","v":12.122381814308255},{"$f":"dichteLuft(0,Torr_in_Pa($BM$26),CA83)","v":{"$error":"#NAME?"}},{"$f":"999.972-7*10^(-3)*(CA83-4)^2","v":999.51018839563812},{"$f":"BY83/CB83*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BZ83/CC83*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BZ83+BY83","v":{"$error":"#NAME?"}},{"$f":"CD83+CE83","v":{"$error":"#NAME?"}},{"$f":"CF83/CG83","v":{"$error":"#NAME?"}},{"$f":"BZ83/CG83/CH83","v":{"$error":"#NAME?"}},{"$f":"rf_prozent_von_T_grad_x_hf_gH2O_kg_trLuft(CA83,CI83*1000)","v":{"$error":"#NAME?"}},{"$f":"td_T_grad_rf_prozent(CA83,CJ83)","v":{"$error":"#NAME?"}}]
[null,4.5,{"$f":"C83","v":120},{"$f":"Auswertung_Leistung!C334","v":141.8705230321512},141.8705230321512,{"$f":"IF(C84=\"\",\"\",IF($AQ$7=1,D84,C84))","v":120},{"$f":"Auswertung_Leistung!K334","v":226.67605780504161},{"$f":"IFERROR(IF(OR(C84=\"\",C84=0,Auswertung_Leistung!T334<20),\"<20\",Auswertung_Leistung!T334),\"\")","v":29.683287278761107},{"$f":"IFERROR(IF(C84=\"\",\"\",H84-6.5),\"\")","v":23.183287278761107},{"$f":"ROUND(E84*1.2*1004.5*($J$16-$J$15)/3600,-1)","v":-380},-549.30450861216775,{"$f":"J84+K84","v":-929.30450861216775},-1572.7049554666901,-1025.9057734417504,{"$f":"J84+N84","v":-1405.9057734417504},0,1185.3985402921933,{"$f":"Q84+P84","v":1185.3985402921933},18.354162179766433,10.396739029036073,49.839441083209771,{"$f":"IFERROR(BV84,\"\")","v":0.79265996686701712},{"$f":"Z84","v":12.422397891830645},null,{"$f":"IFERROR(V84*1000/15/60,\"\")","v":0.88073329651890797},{"$f":"IFERROR(CA84,\"\")","v":12.422397891830645},{"$f":"IFERROR(CK84,\"\")","v":""},{"$f":"Auswertung_Leistung!Q334","v":54.930450861216777},{"$f":"IF($AN$11=1,AB84*Auswertung_Leistung!Y334,AB84*Auswertung_Leistung!AB334)","v":29.634963507304832},{"$f":"Auswertung_Leistung!R334","v":51.295288672087516},{"$f":"Auswertung_Leistung!S334","v":78.635247773334498},null,{"$f":"IF(C84=\"\",\"\",$BH$10*F84^$BI$10)","v":2.9070844090284653E+101},null,{"$f":"Auswertung_Leistung!U334","v":86.189755993307784},{"$f":"Auswertung_Leistung!V334","v":227.89492002213839},{"$f":"Auswertung_Leistung!W334","v":45},{"$f":"Auswertung_Leistung!X334","v":305},{"$f":"AM65","v":45},null,{"$f":"AO65","v":50},null,null,null,null,{"$f":"AT65","v":50},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#NAME?"},{"$f":"M84-N84","v":-546.79918202493968},44.750533670225003,2.4833814467383464,{"$f":"BT84*1000000","v":2483381.4467383465},{"$f":"ABS(BR84)/BU84*3600","v":0.79265996686701712},{"$f":"BQ84/$BM$53","v":{"$error":"#NAME?"}},{"$error":"#NAME?"},{"$f":"BX84*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BQ84-BV84","v":{"$error":"#NAME?"}},12.422397891830645,{"$error":"#NAME?"},{"$f":"999.972-7*10^(-3)*(CA84-4)^2","v":999.47544249626173},{"$f":"BY84/CB84*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BZ84/CC84*$BM$52","v":{"$error":"#NAME?"}},{"$f":"BZ84+BY84","v":{"$error":"#NAME?"}},{"$f":"CD84+CE84","v":{"$error":"#NAME?"}},{"$f":"CF84/CG84","v":{"$error":"#NAME?"}},{"$f":"BZ84/CG84/CH84","v":{"$error":"#NAME?"}},{"$f":"rf_prozent_von_T_grad_x_hf_gH2O_kg_trLuft(CA84,CI84*1000)","v":{"$error":"#NAME?"}},{"$f":"td_T_grad_rf_prozent(CA84,CJ84)","v":{"$error":"#NAME?"}}]
[null,4,{"$f":"C84","v":120},{"$f":"Auswertung_Leistung!C335","v":88.946719545082203},88.946719545082203,120,{"$f":"Auswertung_Leistung!K335","v":144.77032139829575},{"$f":"IFERROR(IF(OR(C85=\"\",C85=0,Auswertung_Leistung!T335<20),\"<20\",Auswertung_Leistung!T335),\"\")","v":28.567670688955349},{"$f":"IFERROR(IF(C85=\"\",\"\",H85-6.5),\"\")","v":22.067670688955349},-240,-385.16814049919441,-625.16814049919435,-1155.9962212429191,-735.08297554939168,-975.08297554939168,0,926.81699403087396,926.81699403087396,17.650720602139405,9.1503556094973924,52.05585433687822,{"$f":"IFERROR(BV85,\"\")","v":0.61017113842372683},10.76725819665041,null,{"$f":"IFERROR(V85*1000/15/60,\"\")","v":0.67796793158191859},{"$f":"IFERROR(CA85,\"\")","v":10.76725819665041},{"$f":"IFERROR(CK85,\"\")","v":""},{"$f":"Auswertung_Leistung!Q335","v":38.516814049919439},{"$f":"IF($AN$11=1,AB85*Auswertung_Leistung!Y335,AB85*Auswertung_Leistung!AB335)","v":23.170424850771848},{"$f":"Auswertung_Leistung!R335","v":36.754148777469581},{"$f":"Auswertung_Leistung!S335","v":57.799811062145949},null,2.9070844090284653E+101,null,{"$f":"Auswertung_Leistung!U335","v":53.606058419269921},{"$f":"Auswertung_Leistung!V335","v":143.97319300359337},{"$f":"Auswertung_Leistung!W335","v":45},{"$f":"Auswertung_Leistung!X335","v":305},{"$f":"AM66","v":305},null,{"$f":"AO66","v":300},null,null,null,null,{"$f":"AT66","v":300},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#NAME?"},-420.91324569352741,44.750533670225003,2.4833814467383464,2483381.4467383465,0.61017113842372683,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},10.76725819665041,{"$error":"#NAME?"},999.6514295154991,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"}]
[null,3.5,120,{"$f":"Auswertung_Leistung!C336","v":88.768218603980287},88.768218603980287,120,{"$f":"Auswertung_Leistung!K336","v":119.45423872093957},{"$f":"IFERROR(IF(OR(C86=\"\",C86=0,Auswertung_Leistung!T336<20),\"<20\",Auswertung_Leistung!T336),\"\")","v":29.673995909934646},23.173995909934646,-240,-295.95034157313302,-535.95034157313307,-900.78436894282447,-568.71899027109055,-808.71899027109055,0,746.76958443496255,746.76958443496255,17.268358606741998,8.4373671011618168,53.59911784770032,0.48137404134524625,11.717066308554584,null,{"$f":"IFERROR(V86*1000/15/60,\"\")","v":0.53486004593916248},{"$f":"IFERROR(CA86,\"\")","v":11.717066308554584},{"$f":"IFERROR(CK86,\"\")","v":""},{"$f":"Auswertung_Leistung!Q336","v":29.595034157313304},{"$f":"IF($AN$11=1,AB86*Auswertung_Leistung!Y336,AB86*Auswertung_Leistung!AB336)","v":18.669239610874065},{"$f":"Auswertung_Leistung!R336","v":28.435949513554526},{"$f":"Auswertung_Leistung!S336","v":45.039218447141224},null,2.9070844090284653E+101,null,{"$f":"Auswertung_Leistung!U336","v":53.081157725929472},{"$f":"Auswertung_Leistung!V336","v":144.75840523928011},{"$f":"Auswertung_Leistung!W336","v":45},{"$f":"Auswertung_Leistung!X336","v":305},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#NAME?"},-332.06537867173392,44.750533670225003,2.4833814467383464,2483381.4467383465,0.48137404134524625,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},11.717066308554584,{"$error":"#NAME?"},999.55512821312561,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"}]
[null,3,120,{"$f":"Auswertung_Leistung!C337","v":58.482567106213793},58.482567106213793,120,{"$f":"Auswertung_Leistung!K337","v":126.36722037472191},{"$f":"IFERROR(IF(OR(C87=\"\",C87=0,Auswertung_Leistung!T337<20),\"<20\",Auswertung_Leistung!T337),\"\")","v":30.00450535278009},23.50450535278009,-160,-316.79196192740881,-476.79196192740881,-960.56257536905548,-607.62284615566477,-767.62284615566477,0,788.53996663479415,788.53996663479415,17.357679836831753,8.6040979120957068,53.241086000273192,0.51163425853768063,11.574830774455849,null,0.56848250948631185,11.574830774455849,"",{"$f":"Auswertung_Leistung!Q337","v":31.679196192740879},{"$f":"IF($AN$11=1,AB87*Auswertung_Leistung!Y337,AB87*Auswertung_Leistung!AB337)","v":19.713499165869855},{"$f":"Auswertung_Leistung!R337","v":30.381142307783236},{"$f":"Auswertung_Leistung!S337","v":48.028128768452774},null,2.9070844090284653E+101,null,{"$f":"Auswertung_Leistung!U337","v":34.717969561518032},{"$f":"Auswertung_Leistung!V337","v":96.031403402482042},{"$f":"Auswertung_Leistung!W337","v":45},{"$f":"Auswertung_Leistung!X337","v":305},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#NAME?"},-352.93972921339071,44.750533670225003,2.4833814467383464,2483381.4467383465,0.51163425853768063,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},11.574830774455849,{"$error":"#NAME?"},999.57035357116843,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"}]
[null,2.5,120,{"$f":"Auswertung_Leistung!C338","v":74.07620585963241},74.07620585963241,120,{"$f":"Auswertung_Leistung!K338","v":116.78392418959804},{"$f":"IFERROR(IF(OR(C88=\"\",C88=0,Auswertung_Leistung!T338<20),\"<20\",Auswertung_Leistung!T338),\"\")","v":27.91908981285016},21.41908981285016,-200,-290.29183568195089,-490.29183568195089,-884.85345393792386,-558.25194595751304,-758.25194595751304,0,736.45485834247279,736.45485834247279,17.24410786720836,8.3925083398179137,53.687529785635945,0.47345341581484385,11.659363225767422,null,0.52605935090538203,11.659363225767422,"",{"$f":"Auswertung_Leistung!Q338","v":29.029183568195087},{"$f":"IF($AN$11=1,AB88*Auswertung_Leistung!Y338,AB88*Auswertung_Leistung!AB338)","v":18.41137145856182},{"$f":"Auswertung_Leistung!R338","v":27.912597297875649},{"$f":"Auswertung_Leistung!S338","v":44.242672696896193},null,2.9070844090284653E+101,null,{"$f":"Auswertung_Leistung!U338","v":43.932548245180001},{"$f":"Auswertung_Leistung!V338","v":121.74895277102426},{"$f":"Auswertung_Leistung!W338","v":45},{"$f":"Auswertung_Leistung!X338","v":305},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#NAME?"},-326.60150798041082,44.750533670225003,2.4833814467383464,2483381.4467383465,0.47345341581484385,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},11.659363225767422,{"$error":"#NAME?"},999.56133908483037,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"}]
[null,2,120,{"$f":"Auswertung_Leistung!C339","v":28.850902391239664},28.850902391239664,{"$f":"IF(C89=\"\",\"\",IF($AQ$7=1,D89,C89))","v":120},{"$f":"Auswertung_Leistung!K339","v":93.30142360797673},{"$f":"IFERROR(IF(OR(C89=\"\",C89=0,Auswertung_Leistung!T339<20),\"<20\",Auswertung_Leistung!T339),\"\")","v":22.508279039290517},16.008279039290517,-80,-182.47580868486278,-262.47580868486278,-563.30668072592709,-353.17123131875263,-433.17123131875263,0,486.96273289709961,486.96273289709961,16.782039180077984,7.5135909913660832,55.82603371802486,0.30461998452126354,14.644185126177694,null,0.33846664946807059,14.644185126177694,"",{"$f":"Auswertung_Leistung!Q339","v":18.247580868486278},{"$f":"IF($AN$11=1,AB89*Auswertung_Leistung!Y339,AB89*Auswertung_Leistung!AB339)","v":12.174068322427491},{"$f":"Auswertung_Leistung!R339","v":17.658561565937632},{"$f":"Auswertung_Leistung!S339","v":28.165334036296354},null,2.9070844090284653E+101,null,{"$f":"Auswertung_Leistung!U339","v":16.675718787594441},{"$f":"Auswertung_Leistung!V339","v":48.593821352649378},{"$f":"Auswertung_Leistung!W339","v":45},{"$f":"Auswertung_Leistung!X339","v":305},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#NAME?"},-210.13544940717446,44.750533670225003,2.4833814467383464,2483381.4467383465,0.30461998452126354,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},14.644185126177694,{"$error":"#NAME?"},999.17890926099756,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"}]
[null,2,120,{"$f":"Auswertung_Leistung!C340","v":28.850902391239664},28.850902391239664,{"$f":"IF(C90=\"\",\"\",IF($AQ$7=1,D90,C90))","v":120},{"$f":"Auswertung_Leistung!K340","v":93.30142360797673},{"$f":"IFERROR(IF(OR(C90=\"\",C90=0,Auswertung_Leistung!T340<20),\"<20\",Auswertung_Leistung!T340),\"\")","v":25.156457269385882},18.656457269385882,-80,-182.47580868486278,-262.47580868486278,-563.30668072592709,-353.17123131875263,-433.17123131875263,0,486.96273289709961,486.96273289709961,16.782039180077984,7.5135909913660832,55.82603371802486,{"$f":"IFERROR(BV90,\"\")","v":0.30461998452126354},14.644185126177694,null,0.33846664946807059,14.644185126177694,"",{"$f":"Auswertung_Leistung!Q340","v":18.247580868486278},{"$f":"IF($AN$11=1,AB90*Auswertung_Leistung!Y340,AB90*Auswertung_Leistung!AB340)","v":12.174068322427491},{"$f":"Auswertung_Leistung!R340","v":17.658561565937632},{"$f":"Auswertung_Leistung!S340","v":28.165334036296354},null,2.9070844090284653E+101,null,{"$f":"Auswertung_Leistung!U340","v":16.675718787594441},{"$f":"Auswertung_Leistung!V340","v":48.593821352649378},{"$f":"Auswertung_Leistung!W340","v":45},{"$f":"Auswertung_Leistung!X340","v":305},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#NAME?"},-210.13544940717446,44.750533670225003,2.4833814467383464,2483381.4467383465,0.30461998452126354,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},14.644185126177694,{"$error":"#NAME?"},999.17890926099756,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"}]
[null,2,120,{"$f":"Auswertung_Leistung!C341","v":28.850902391239664},28.850902391239664,{"$f":"IF(C91=\"\",\"\",IF($AQ$7=1,D91,C91))","v":120},{"$f":"Auswertung_Leistung!K341","v":93.30142360797673},{"$f":"IFERROR(IF(OR(C91=\"\",C91=0,Auswertung_Leistung!T341<20),\"<20\",Auswertung_Leistung!T341),\"\")","v":25.156457269385882},18.656457269385882,-80,-182.47580868486278,-262.47580868486278,-563.30668072592709,-353.17123131875263,-433.17123131875263,0,486.96273289709961,486.96273289709961,16.782039180077984,7.5135909913660832,55.82603371802486,{"$f":"IFERROR(BV91,\"\")","v":0.30461998452126354},14.644185126177694,null,{"$f":"IFERROR(V91*1000/15/60,\"\")","v":0.33846664946807059},{"$f":"IFERROR(CA91,\"\")","v":14.644185126177694},{"$f":"IFERROR(CK91,\"\")","v":""},{"$f":"Auswertung_Leistung!Q341","v":18.247580868486278},{"$f":"IF($AN$11=1,AB91*Auswertung_Leistung!Y341,AB91*Auswertung_Leistung!AB341)","v":12.174068322427491},{"$f":"Auswertung_Leistung!R341","v":17.658561565937632},{"$f":"Auswertung_Leistung!S341","v":28.165334036296354},null,2.9070844090284653E+101,null,{"$f":"Auswertung_Leistung!U341","v":16.675718787594441},{"$f":"Auswertung_Leistung!V341","v":48.593821352649378},{"$f":"Auswertung_Leistung!W341","v":45},{"$f":"Auswertung_Leistung!X341","v":305},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#NAME?"},-210.13544940717446,44.750533670225003,2.4833814467383464,2483381.4467383465,0.30461998452126354,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},14.644185126177694,{"$error":"#NAME?"},999.17890926099756,{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"},{"$error":"#NAME?"}]
[]
[null,{"$f":"IF(OR(C83<C94,C84<C94,C85<C94,C91<C94,C83>C95,C84>C95,C85>C95,C91>C95),\"Grenzwerte\",\"\")","v":""},null,null,null,null,null,null,null,null,"DpK =",{"$f":"Auswertung_Leistung!E328","v":37.174451205041549},"[kPa]"]
[null,"  Minimal",{"$f":"AP65","v":45},{"$f":"AQ65","v":"Pa"},null,null,null,null,null,null,"DpH =",{"$f":"Auswertung_Leistung!E329","v":2.1090909090909089},"[kPa]"]
[null,"  Maximal",{"$f":"AP66","v":305},{"$f":"AQ66","v":"Pa"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Grenzen der Auslegung",null,null,null,null,null,null,"heizen"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Primärdurck",null,"Wassermassenstrom",null,null,null,null,"Wassermassenstrom"]
[null,"© LTG Aktiengesellschaft - 09.01.2025, EI",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"Auswertung_Leistung!A238","v":45},null,{"$f":"Auswertung_Leistung!C238","v":50},null,null,null,null,{"$f":"AO97","v":50}]
[null,"Angaben zu Toleranzen sowie weitere Spezifikationen sind der aktuellen Bauteilmappe der LTG Aktiengesellschaft zu entnehmen.",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,false,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"Auswertung_Leistung!A239","v":305},null,{"$f":"Auswertung_Leistung!C239","v":300},null,null,null,null,{"$f":"AO98","v":300}]
[null,"Eine Fehlerfreiheit des Programms kann nicht zugesichert werden. Im Zweifel gelten die technischen Daten der aktuellen Bauteilmappe der LTG Aktiengesellschaft."]
[null,"Aus Programmierfehlern entstandener Schaden geht nicht zu Lasten der LTG Aktiengesellschaft. Technische Änderungen im Rahmen der Weiterentwicklung vorbehalten."]

{"sheet":"Legende","index":1,"n_rows":45,"n_cols":7,"rows_kept":45,"cut":false,"hidden":false,"merged":[]}
[]
["Zellenname","Deutsch","Englisch","Französisch","Italienisch","Portugues","Turkish"]
[]
["L_Kuehlfall","Kühlfall:","cooling mode:","Mode de refroidissement:","In raffescamento:"]
["L_Ansaugtemperatur_K","Ansaugtemperatur:","intake air temperature","Température de l'air d'admission","Temperatura aria in ingresso "]
["L_Kuehlwasservorlauf","Kühlwasservorlauf ¹:","water supply temperature ¹:","Température de l'eau ¹:","Temperatura acqua in ingresso ¹:"]
["L_Kuehlwasservorlauf_kon","Kühlwasservorlauf \nkondensierender Betrieb ²:","water supply temperature (condensation mode) ²:","Température de l'eau (Mode de condensation) ²","Temperatura acqua in ingresso ²:"]
["L_rF_kon","relative Feuchte ²:","relative humidity ²:","humidité relative"]
["L_projektierte_Leistung_k","projektierte Leistung:","required capacity for design situation:","Capacité requise pour la conception:","Potenzialità richiesta di progetto:"]
["L_Nennkühlwassermenge_K","Nennwassermenge:","nominal water flow rate:","quantité d'eau nominale","Portata acqua nominale:"]
["L_Istkühlwassermenge_K","Wassermenge Kühlen:","cold water flow rate:","quantité d'eau:","Portata acqua refrigerata:"]
["L_Heizfall","Heizfall:","heating mode:","Mode chauffage","In riscaldamento:"]
[]
["L_Ansaugtemperatur_H","Ansaugtemperatur:","intake air temperature","Température de l'air d'admission","Temperatura aria in ingresso "]
["L_Heizwasservorlauf","Heizwasservorlauf:","water supply temperature:","Température de l'eau:","Temperatura acqua in ingresso:"]
["L_projektierte_Leistung_h","projektierte Leistung:","required capacity for design situation:","Capacité requise pour la conception:","Potenzialità richiesta di progetto:"]
["L_Nennheizwassermenge_H","Nennwassermenge:","nominal water mass flow (heating):","quantité d'eau nominale","Portata acqua nominale:"]
["L_Istheizwassermenge_H","Wassermenge Heizen:","hot water flow rate:","quantité d'eau:","Portata acqua calda:"]
[]
["L_Volumenstrom","Volumenstrom","air flow rate","Debit d`air","Portata aria","Caudal de ar"]
["L_Drehzahl","Drehzahl","fan Speed","nombre de révolutions","Velocità del ventilatore "]
["L_Date","Datum:","Date:","data:","Data:","Data:","Tarih:"]
["L_Projekt","Projekt:","Project:","Projet:","Progetto:","Projecto:","Proje"]
["L_Bearbeiter","Bearbeiter:","Editor:","Responsable:","Responsabile:","Responsável:","Hazirlayan:"]
["L_Auslegung","Schieberstellung","slide position","position de coulissement","posizione slitta"]
["L_Kondensat","Kondensat ²","condensate ²","condensé ²","condensato ²"]
["L_Auslegetool","Auslegetool","Calculation Tool","programme de calcul","Risultato del dimensionamento"]
["L_mitFilter","mit Filter ","with filter ","avec filtre ","con filtro"]
["L_ohneFilter","ohne Filter","without filter","sans filtre","senza filtro"]
["L_mit3D","mit 3D-Strömung","with 3D-flow-application","avec 3D-courent","con 3D-corrente"]
["L_ohne3D","ohne 3D-Strömung","without 3D-flow-application"]
["L_mitSchalld","mit Schalldämmung","with sound insulation"]
["L_ohneSchalld","ohne Schalldämmung","without Schalldämmung"]
["L_BG630","Baugröße 630","Size 630","Taille 630","Grandezza 630"]
["L_BG800","Baugröße 800","Size 800","Taille 800","Grandezza 800"]
["L_BG1000","Baugröße 1000","Size 1000","Taille 1000","Grandezza 1000"]
["L_Angabe","Angaben zu Toleranzen sowie weitere Spezifikationen sind der aktuellen Bauteilmappe der LTG Aktiengesellschaft zu entnehmen.","Information on tolerances as well as further specifications can be found in the current component portfolio of LTG Aktiengesellschaft","Informations sur les tolérances et autres spécifications du portefeuille actuel de composants LTG se trouve dans","Informazioni sui tolleranze e altre specifiche della corrente portafoglio componente LTG può essere trovato in"]
["L_Fehlerfreiheit","Eine Fehlerfreiheit des Programms kann nicht zugesichert werden. Im Zweifel gelten die technischen Daten der aktuellen Bauteilmappe der LTG Aktiengesellschaft.","A fault-free program can not be guaranteed. In case of doubt, the technical data of the current component portfolio of LTG Aktiengesellschaft apply.","Une précision du programme ne peut pas être garantie. En cas de doute, les données techniques du portefeuille actuel de composants LTG s'appliquent.","Una precisione del programma non può essere garantita. In caso di dubbio, si applicano i dati tecnici del portafoglio componente corrente LTG"]
["L_Programmierfehler","Aus Programmierfehlern entstandener Schaden geht nicht zu Lasten der LTG Aktiengesellschaft. Technische Änderungen im Rahmen der Weiterentwicklung vorbehalten.","Damage resulting from programming errors shall not be charged to LTG Aktiengesellschaft. We reserve the right to make technical changes within the scope of further development","découlant du mal des erreurs de programmation ne sont pas au détriment de LTG. Sous réserve de modifications techniques dans le cadre du développement.","derivanti da errori di programmazione danno non va a scapito della LTG. Con riserva di modifiche tecniche come parte dello sviluppo."]
["L_Zulufttemp","Zulufttemp.²","supply air temp ²","temp de l'air d'alimentation ²","temp dell'aria di alimentazione ²"]
["L_primaervol","Primärvol.","primary air flow","flux primaire","flusso primario"]
["L_primaerdruck","Primärdruck","pimary pressure","pression primaire","pressione primaria"]
["L_sekundaervol","Sekundärvolumenstrom","secondary air flow","flux secondaire","flusso secondario"]
["L_heatexchanger","Wärmetauscher:","heat exchange:","échangeur de chaleur:","scambiatore di calore:"]
["L_Auswahl","Auswahl","selection","sélection","selezione"]

{"sheet":"Legende_Abkürzungen","index":2,"n_rows":38,"n_cols":8,"rows_kept":38,"cut":false,"hidden":false,"merged":[[0,13,0,17]]}
["Tel.  +49 (0)711 8201-180   Fax -720",null,"Email:","Raumluft@LTG-AG.de"]
["Legende für LTG-Induktionsgeräte",null,null,null,{"$f":"Auslegetool!BK1","v":1},"Abfrage"]
["LTG Aktiengesellschaft",null,null,null,1,2,3,4]
[null,{"$f":"IF($E$2=1,E4,IF($E$2=2,F4,IF($E$2=3,G4,IF($E$2=4,H4,I4))))","v":"Deutsch"},null,null,"Deutsch","Englisch","Französisch","Italienisch"]
["Dp [Pa]","statischer Luftdruck am Primärluftstutzen in Pa",null,null,"statischer Luftdruck am Primärluftstutzen in Pa","static pressure of primary air (spigot)","pression statique á la tubulure de l'air primaire","pressione statica sul canotto di entrata aria primaria"]
["VP [m³/h]","Primärluftvolmenstrom in m³/h pro Gerät (+/- 10%)",null,null,"Primärluftvolmenstrom in m³/h pro Gerät (+/- 10%)","Primary air flow rate(+/- 10%)","débit volume de l'air primaire (+/- 10%)","portata d'aria primaria (+/-10%)"]
["LWA [dB(A)]","Schallleistungspegel in dB(A) (+/- 3 dB)",null,null,"Schallleistungspegel in dB(A) (+/- 3 dB)","Sound power level (+/- 3 dB)","Niveau de puissance sonore (+/-3 dB)","Livello di potenza sonora (+/- 3 dB)"]
["LA18 [dB(A)]","Schalldruckpegel bei 18 m² Sabine in dB(A) (+/- 3 dB)",null,null,"Schalldruckpegel bei 18 m² Sabine in dB(A) (+/- 3 dB)","Sound pressure level at a room absorption of 18m² Sabine(+/-3 dB)","niveau de pression acoustique lors d'une absorption de la salle de 18m² Sabine","Livello di pressione sonora con 18m² Sabine di assorbimento"]
["QPK [W]","Kühlleistung Primärluft",null,null,"Kühlleistung Primärluft","cooling capacity primary air","puissance frigorifique de l'air primaire","potenza frigorifera aria primaria"]
["QSK1) [W]","Sekundärkühlleistung (sensibel) in W bei nicht kondensierendem Betrieb (+/- 5%)",null,null,"Sekundärkühlleistung (sensibel) in W bei nicht kondensierendem Betrieb (+/- 5%)","Secondary cooling capacity  - heat exchanger (not condensing)","Capacité de refroidissement secondaire - sur l'échangeur thermique (sans condensation)","capacità di raffreddamento secondario - scambiatore di calore (senza condensa)"]
["QKges1) [W]","Gesamtkühlleistung bei nichtkondensierendem Betrieb in W",null,null,"Gesamtkühlleistung bei nichtkondensierendem Betrieb in W","Total cooling capacity (not condensing)","Capacité totale de refroidissement (sans condensation)","Potenza frigorifera totale (senza condensa)"]
["QTotal2) [W]","Totalleistung (sensibel + latent) in W bei kondensierendem Betrieb (+/- 5%)",null,null,"Totalleistung (sensibel + latent) in W bei kondensierendem Betrieb (+/- 5%)","Total cooling capacity at condensation (sensetive + latent)","Capacité totale de refroidissement avec condensation (sensible + latent)","Potenza frigorifera totale con condensazione (sensitivo + latente)"]
["QSK2) [W]",{"$f":"IF($E$2=1,E13,IF($E$2=2,F13,IF($E$2=3,G13,IF($E$2=4,H13,I13))))","v":"Sekundärkühlleistung (sensibel) in W bei kondensierendem Betrieb (+/- 5%)"},null,null,"Sekundärkühlleistung (sensibel) in W bei kondensierendem Betrieb (+/- 5%)","Secondary cooling capacity at condensation (sensetive)","Capacité de refroidissement secondaire avec condensation (sensible)","capacità di raffreddamento secondario con condensazione (sensitivo)"]
["Qsensibel, K2) [W]",{"$f":"IF($E$2=1,E14,IF($E$2=2,F14,IF($E$2=3,G14,IF($E$2=4,H14,I14))))","v":"Sekundärkühlleistung (sensibel) in W bei kondensierendem Betrieb (+/- 5%)"},null,null,"Sekundärkühlleistung (sensibel) in W bei kondensierendem Betrieb (+/- 5%)","Secondary cooling capacity at condensation (sensetive)","Capacité de refroidissement secondaire avec condensation (sensible)","capacità di raffreddamento secondario con condensazione (sensitivo)"]
["QKges2) [W]","Gesamtkühlleistung (sensibel + primär) bei kondensierendem Betrieb in W",null,null,"Gesamtkühlleistung (sensibel + primär) bei kondensierendem Betrieb in W","cooling capacity at condensation (sensetive + primary)","Capacité de refroidissement (sensible + primaire)","capacità di raffreddamento (sensitivo + primario)"]
["QPH [W]","Primärheizleistung in W (negativ = kühlen)",null,null,"Primärheizleistung in W (negativ = kühlen)","Primary heating capacity","Primary heating capacity","riscaldamento primario"]
["QSH [W]","Sekundärheizleistung in W (+/- 5%)",null,null,"Sekundärheizleistung in W (+/- 5%)","Secondary heating capacity","chauffage secondaire","riscaldamento secondaria"]
["QHges [W]","Gesamtheizleistung in W",null,null,"Gesamtheizleistung in W","Total heating capacity","puissance de chauffage totale","potenza termica totale"]
["tRaum [°C]","Raumtemperatur in °C",null,null,"Raumtemperatur in °C","Room temperature:","Température ambiante:","Temperatura ambiente:"]
["tKWRL [°C]","Kaltwasser-Rücklauftemperatur in °C",null,null,"Kaltwasser-Rücklauftemperatur in °C","Cold water return temperature","température de retour d'eau froide","temperatura di ritorno dell'acqua fredda"]
["tKWRL2 [°C]",{"$f":"IF($E$2=1,E21,IF($E$2=2,F21,IF($E$2=3,G21,IF($E$2=4,H21,I21))))","v":"Kaltwasser-Rücklauftemperatur in °C (kondensierender Betrieb)"},null,null,"Kaltwasser-Rücklauftemperatur in °C (kondensierender Betrieb)","Cold water return temperature (at condensation)","température de retour d'eau froide (avec condensation)","temperatura di ritorno dell'acqua fredda (con condensazione)"]
["tWWRL [°C]","Warmwasser-Rücklauftemperatur in °C",null,null,"Warmwasser-Rücklauftemperatur in °C","Hot water return temperature","température de retour d'eau chaude","temperatura di ritorno dell'acqua calda"]
["wOK","Nennwassermenge Kühlen in kg/h",null,null,"Nennwassermenge Kühlen in kg/h","nominal water mass flow (cooling)","quantité d'eau nominale (refroidissement)","Portata acqua nominale (raffreddamento)"]
["wOH","Nennwassermenge Heizen in kg/h",null,null,"Nennwassermenge Heizen in kg/h","nominal water mass flow (heating)","quantité d'eau nominale (chauffage)","Portata acqua nominale (riscaldamento)"]
["wK=","gewählte Wassermenge Kühlen",null,null,"gewählte Wassermenge Kühlen","Cold Water Flow Rate","quantité d'eau (refroidissement)","Portata acqua refrigerata"]
["wH=","gewählte Wassermenge Heizen",null,null,"gewählte Wassermenge Heizen","Hot Water Flow Rate","quantité d'eau (chauffage)","Portata acqua calda"]
["DpK","wasserseitiger Druckverlust über Kühlregister in kPa",null,null,"wasserseitiger Druckverlust über Kühlregister in kPa","water-side pressure loss","perte de charge sur l'eau","perdita di carico lato acqua"]
["DpH","wasserseitiger Druckverlust Heizregister in kPa",null,null,"wasserseitiger Druckverlust Heizregister in kPa","water-side pressure loss","perte de charge sur l'eau","perdita di carico lato acqua"]
["QE","Eigenkonvektion bei Warmwasservorlaufttemperatur 55 °C, Raumlufttemperatur 20 °C, Nennwassermenge",null,null,"Eigenkonvektion bei Warmwasservorlaufttemperatur 55 °C, Raumlufttemperatur 20 °C, Nennwassermenge","heating capacity by natural convection (Water supply temperature = 55°C, Roomtemp. = 20°C, nominal water mass flow)","puissance calorifique de convection propre (Température de l'eau = 55°C; température ambiante = 20°C; quantité d'eau nominale)","potenza calorifera a convezione naturale (Temperatura acqua in ingresso = 55°C; temperatura ambiente = 20°C ; Portata acqua)"]
["1*)","nicht kondensierender Betrieb",null,null,"nicht kondensierender Betrieb","not condensing","sans condensation","senza condensa"]
["2*)","kondensierender Betrieb",null,null,"kondensierender Betrieb","at condensation","avec condensation","con condensazione"]
[]
[]
[]
["ã LTG Aktiengesellschaft: 12.04.2017, TT"]
[{"$f":"L_Angabe","v":"Angaben zu Toleranzen sowie weitere Spezifikationen sind der aktuellen Bauteilmappe der LTG Aktiengesellschaft zu entnehmen."}]
[{"$f":"L_Fehlerfreiheit","v":"Eine Fehlerfreiheit des Programms kann nicht zugesichert werden. Im Zweifel gelten die technischen Daten der aktuellen Bauteilmappe der LTG Aktiengesellschaft."}]
[{"$f":"L_Programmierfehler","v":"Aus Programmierfehlern entstandener Schaden geht nicht zu Lasten der LTG Aktiengesellschaft. Technische Änderungen im Rahmen der Weiterentwicklung vorbehalten."}]

{"sheet":"Rohdaten_Messwerte_Kühlen","index":3,"n_rows":166,"n_cols":53,"rows_kept":166,"cut":false,"hidden":true,"merged":[[160,6,160,8],[118,6,118,8],[132,6,132,8],[139,6,139,8],[146,6,146,8],[153,6,153,8],[3,49,4,49],[91,6,91,8],[97,6,97,8],[104,6,104,8],[111,6,111,8],[3,50,4,50],[125,6,125,8],[3,51,4,51],[3,52,4,52],[6,42,11,42],[7,44,11,51],[73,27,73,30],[73,35,73,38],[2,42,3,42],[2,43,4,43],[2,44,2,52],[3,44,4,44],[3,45,4,45],[3,46,4,46],[3,47,4,47],[3,48,4,48]]}
[null,"Messpunkt","Schieberstellung","Düsenanzahl","Primärdruck","Wassermenge [kg/h]","T Wasser Vorlauf [°C]","T Wasser Rücklauf [°C]","T Wasser Spreizung [K]","Q Sek [W]","q Sek [W/K]","V Sek [m³/h]","i [-]","T Ansaug mean [°C]","T Ausblas mean [°C]","T WT in [°C]","T WT out [°C]","Messstrecke","Wirkdruck","V Prim [m³/h]","T Ansaug 1","T Ansaug 2","T Ansaug 3","T Ausblas 1","T Ausblas 2","T Ausblas 3","T Primärluft",null,"ΔΘ\n(T_Ansaug_mean -\nT_W_Mittel) [K]","ΔΘ\n(T_Ansaugs_mean -\nT_W_Vorlauf) [K]","T_W_Mittel\n[°C]",null,"i_errechnet\n[-]",null,"q_Sek_Mittel [W/K]","q_Sek_Vorlauf [W/K]","Δp_Wasser\n[kPa]",null,"Datum","Start Messwert","Ende Messwert"]
[1,{"$f":"A2+1","v":2},{"$f":"B2+1","v":3},4,{"$f":"D2+1","v":5},6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,32,33,34,35,36,37]
["V1","(Schieberstellung 5 |\n150 Pa | 200 kg/h)",5,70,150,202.05018515151508,16.831181818181818,18.152333333333345,-1.3211515151515156,-309.94493493939387,45.704175121212131,238.80150281818183,1.916828272727273,23.612828318181812,18.645883757575753,23.612828318181812,19.73650593939394,"42,18/54,67",66.590909090909093,124.59541056060618,23.334242424242404,23.700606060606081,23.803787878787844,18.727727272727275,18.516666666666652,18.693030303030319,18.141515151515172,null,6.1210707424242461,6.781646499999999,17.491757575757578,null,1.5974299569654484,null,50.636943193643965,45.704174902356478,28.9,null,"2017-05-05","11:26:00","11:41:10",null,"Primärdruck","Wassermenge  [kg/h]","Schieberstellungen"]
["V2","Schieberstellung 5 | Edelstahlgitter | 4L-WT | 50 Pa | 200 kg/h",5,70,50,201.9774836212122,16.064787878787879,16.995348484848481,-0.93056060606060598,-218.23212375757569,23.032627500000011,103.62928477272723,1.4127545151515151,25.539707045454541,18.317944393939392,25.539707045454541,19.250127333333332,"42,18/54,67",22.5,73.352649999999912,25.867121212121209,25.646515151515167,25.105606060606057,18.456969696969711,18.140757575757576,18.354545454545466,18.701363636363645,null,9.0096388636363614,9.4749191666666679,16.530068181818184,null,1.1772826772216338,null,24.222343662110674,23.03262755884905,28.9,null,"2017-05-05","13:30:10","13:45:20",null,null,null,1,"1 - 2",2,"2 - 3",3,"3 - 4",4,"4 - 5",5]
["V3","Schieberstellung 5 | Edelstahlgitter | 4L-WT |\n100 Pa | 200 kg/h",5,70,100,202.02406874626863,16.075985074626868,17.470179104477609,-1.3941940298507463,-327.03808164179094,36.998066552238811,180.01060420895527,1.7441699253731342,24.915318447761194,18.389004955223875,24.915318447761194,19.489426402985075,"42,18/54,67",45.30000000000004,103.20703400000001,25.181044776119393,25.00776119402984,24.556865671641773,18.531343283582089,18.220597014925367,18.415820895522401,18.366119402985092,null,8.1422363582089599,8.8393333731343287,16.773082089552243,null,1.4535641399443229,null,40.165982109359881,36.998066389559611,28.9,null,"2017-05-05","14:08:10","14:23:40",null,"[Pa]"]
["V4","Schieberstellung 5 | Edelstahlgitter | 4L-WT |\n150 Pa | 200 kg/h",5,70,150,202.22353931343281,16.085626865671646,17.741776119402981,-1.6561492537313438,-388.86817553731345,45.27565994029851,233.17569323880599,1.8417050149253729,24.67474623880597,18.516532358208956,24.67474623880597,19.693910716417918,"42,18/54,67",68.800000000000082,126.6085979999999,24.814925373134308,24.718358208955255,24.49119402985076,18.637910447761207,18.35701492537315,18.555373134328335,18.238358208955223,null,7.7610447462686531,8.5891193731343272,16.91370149253731,null,1.5347638171095581,null,50.10706624661551,45.275660084576351,28.9,null,"2017-05-05","14:39:50","14:55:00",null,50,200,"x","x","x","x","x","x","x","x","x"]
["V5","Schieberstellung 5 | Edelstahlgitter | 4L-WT |\n250 Pa | 200 kg/h",5,70,250,200.38356357575756,16.000333333333334,17.786348484848489,-1.7860151515151521,-415.54792918181801,56.400179757575764,329.82211466666655,2.0395634090909085,23.368171757575762,18.509363636363638,23.368171757575762,19.605317348484846,"42,18/54,67",108.5,161.71211600000007,23.428030303030326,23.4598484848485,23.216060606060616,18.620000000000008,18.420303030303053,18.487575757575751,17.925303030303041,null,6.4748308484848494,7.3678384242424242,16.893340909090909,null,1.6997201404505884,null,64.179188880863308,56.40017949204293,28.9,null,"2017-05-08","09:12:00","09:27:10",null,150,200,"x","x","x","x","x","x","x","x","x"]
["V6","Schieberstellung 5 | Edelstahlgitter | 4L-WT |\n300 Pa | 200 kg/h",5,70,300,200.55822357575755,16.008181818181821,17.96916666666667,-1.9609848484848478,-456.654335,59.971489545454546,360.80656610606002,2.0311496363636361,23.622782803030304,18.682090893939403,23.622782803030304,19.842854090909096,"42,18/54,67",131.5,177.63662400000015,23.657878787878815,23.71378787878788,23.495757575757558,18.77484848484848,18.596969696969687,18.674696969696996,17.996818181818171,null,6.6341085606060588,7.6146009848484812,16.988674242424242,null,1.6926520662711375,null,68.835564799367688,59.971489701578271,28.9,null,"2017-05-08","09:46:40","10:01:50",null,null,50,"-",null,null,null,null,null,null,null,"x"]
[null,null,null,null,null,null,null,{"$f":"F8*4.18*I8/3600","v":-0.45665529040699609},{"$f":"ABS(H9)*3600/(N8-O8)/1.004/1.2","v":276.17747978797058},{"$f":"J8*3/(N8-O8)","v":-277.28160958169855},null,{"$f":"I9/T8","v":1.55473276607627},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,100,null,null,null,null,null,null,null,null,"x"]
["V7","Schieberstellung 5 | Edelstahlgitter | 4L-WT |\n150 Pa | 50 kg/h",5,70,150,45.684768878787864,16.075378787878783,19.906257575757582,-3.8308787878787869,-203.20930256060601,25.970992651515147,248.83247933333323,1.9829136515151513,23.899858590909087,19.826494939393935,23.899858590909087,21.460701409090905,"42,18/54,67",64.590909090909093,125.4900779090908,23.777727272727258,23.979848484848478,23.941666666666688,19.920909090909095,19.741212121212115,19.818030303030294,17.931666666666668,null,5.9090404090909052,7.8244798030303029,17.990818181818184,null,1.6525210388149338,null,34.389716420718685,25.970992625617018,1.9,null,"2017-05-08","10:28:40","10:44:00",null,null,150,null,null,null,null,null,null,null,null,"x"]
["V8","Schieberstellung 5 | Edelstahlgitter | 4L-WT |\n150 Pa | 100 kg/h",5,70,150,105.84956201515151,15.899045454545458,18.275560606060612,-2.376515151515151,-292.07844707575759,38.535232666666651,251.98003671212123,2.009348818181818,23.478661590909088,18.751974712121214,23.478661590909088,20.01683116666667,"42,18/54,67",64.5,125.40382899999992,23.301515151515151,23.518181818181823,23.616818181818157,18.865909090909085,18.633787878787864,18.756818181818186,17.793636363636367,null,6.3913585606060623,7.579616136363633,17.087303030303026,null,1.6744032945167,null,45.70015291409031,38.535232822371512,8.9,null,"2017-05-08","11:43:10","11:58:20",null,null,250,null,null,null,null,null,null,null,null,"x"]
["V9","Schieberstellung 5 | Edelstahlgitter | 4L-WT |\n150 Pa | 150 kg/h",5,70,150,157.62804990909092,15.852212121212119,17.656333333333336,-1.804121212121212,-330.19566203030308,43.626168696969707,249.86119009090902,1.9924525757575757,23.42094448484848,18.393000000000004,23.42094448484848,19.474144454545453,"42,18/54,67",64.5,125.40382899999992,23.242121212121209,23.48833333333334,23.533484848484836,18.5030303030303,18.275909090909074,18.399545454545457,17.908333333333324,null,6.6666717575757586,7.5687323636363635,16.754272727272721,null,1.6604133478759318,null,49.529536779205351,43.626168444111812,18.3,null,"2017-05-08","12:13:50","12:29:00",null,null,300,null,null,null,null,null,null,null,null,"x"]
["V10","Schieberstellung 5 | Edelstahlgitter | 4L-WT |\n150 Pa | 250 kg/h",5,70,150,251.43574669696974,15.999969696969702,17.1875909090909,-1.1876212121212122,-346.71585510606053,48.19325851515152,248.14767127272731,1.9787886060606059,23.194313181818185,18.116631272727268,23.194313181818185,19.021074393939397,"42,18/54,67",64.5,125.40382899999992,23.188787878787871,23.269242424242428,23.124090909090942,18.231969696969696,18.003333333333316,18.115000000000006,18.002272727272704,null,6.6005328787878774,7.1943434848484813,16.593780303030311,null,1.6489241956715013,null,52.529494032880784,48.193258150109664,43,null,"2017-05-08","13:03:30","13:18:40",null,250,200,"x","x","x","x","x","x","x","x","x"]
["V11","Schieberstellung 5 | Edelstahlgitter | 4L-WT |\n150 Pa | 300 kg/h",5,70,150,300.40299018181827,15.988969696969692,17.014136363636364,-1.025166666666667,-357.58012869696989,49.565262651515148,249.45501442424239,1.989213696969697,23.203378727272732,18.013752499999999,23.203378727272732,18.922203454545457,"42,18/54,67",64.5,125.40382899999992,23.255303030303022,23.272878787878778,23.082575757575757,18.134242424242434,17.899242424242424,18.008787878787874,17.927424242424252,null,6.7018256969696974,7.2144090303030284,16.501553030303025,null,1.6576346860352977,null,53.356734493776067,48.193258150109664,58.8,null,"2017-05-08","13:03:30","13:18:40",null,300,200,"x","x","x","x","x","x","x","x","x"]
[]
["V12","Schieberstellung 4-5 | Edelstahlgitter | 4L-WT |\n50 Pa | 200 kg/h",4.5,{"$f":"23+47-(47/2/2)","v":58.25},50,200.02352533333334,15.998666666666663,16.607878787878789,-0.60921212121212109,-141.49341943939388,22.916657030303032,117.56209709090908,1.8905222575757576,22.173085848484853,18.042469712121203,22.173085848484853,18.577203590909086,"42,18/54,67",15.299999999999983,62.184984999999955,22.515000000000008,21.950606060606074,22.05287878787879,18.151515151515152,17.962575757575781,18.012424242424231,18.331515151515159,null,5.8698131212121201,6.1744191818181822,16.303272727272727,null,1.5753122171642233,null,24.106283027433296,22.916657095657051,28.9,null,"2017-05-08","14:56:50","15:12:00"]
["V13","Schieberstellung 4-5 | Edelstahlgitter | 4L-WT |\n150 Pa | 200 kg/h",4.5,{"$f":"23+47-(47/2/2)","v":58.25},150,200.61807159090904,16.004863636363645,17.230348484848488,-1.2254848484848484,-285.46648056060599,39.95671624242425,208.51668313636355,1.9211085303030297,23.149217166666659,18.114797969696969,23.149217166666659,19.060391363636363,"42,18/54,67",48,108.53977300000018,23.320606060606085,23.254393939393932,22.872727272727296,18.140151515151523,18.046212121212108,18.157727272727278,17.909848484848471,null,6.5316111060606055,7.1443535303030314,16.617606060606054,null,1.6009211241131855,null,43.705862453757234,39.956716208734747,28.9,null,"2017-05-08","15:37:40","15:52:50"]
["V14","Schieberstellung 4-5 | Edelstahlgitter | 4L-WT |\n250 Pa | 200 kg/h",4.5,58.25,250,204.18283095454547,16.019333333333332,17.362469696969697,-1.3431363636363638,-318.4286596818182,50.317188848484854,278.48669992424243,1.9909664393939399,22.347883848484845,18.244095969696968,22.347883848484845,18.932916939393941,"42,18/54,67",81.5,139.87513399999992,22.290454545454551,22.371363636363654,22.381363636363659,18.212272727272737,18.167575757575772,18.352727272727261,18.234696969696977,null,5.6569823333333336,6.328550515151516,16.690901515151513,null,1.659053300341546,null,56.291053772221922,50.317188721015995,28.9,null,"2017-05-09","08:09:50","08:25:00"]
["V15","Schieberstellung 4-5 | Edelstahlgitter | 4L-WT |\n300 Pa | 200 kg/h",4.5,58.25,300,204.22658893939396,16.028181818181821,17.51706060606061,-1.4888787878787875,-353.05915251515142,53.97671965151514,309.65264450000012,1.99333140909091,22.569090924242413,18.295939439393937,22.569090924242413,19.163805348484843,"42,18/54,67",101,155.34428300000019,22.533333333333324,22.635606060606069,22.538636363636343,18.259999999999991,18.220909090909096,18.40757575757576,17.98530303030304,null,5.7964697121212128,6.5409091060606066,16.772621212121216,null,1.6611486231078021,null,60.909346442539288,53.976719522299419,28.9,null,"2017-05-09","08:34:20","08:49:30"]
[]
["V16","Schieberstellung 4 | Edelstahlgitter | 4L-WT |\n50 Pa | 200 kg/h",4,{"$f":"23+47-(47/2)","v":46.5},50,204.1375500454545,16.019666666666669,16.445772727272725,-0.42610606060606071,-100.99742904545454,14.649405803030303,68.035006590909077,1.4219965606060605,22.914055560606062,18.108595924242415,22.914055560606062,18.479970287878785,"42,18/54,67",9,47.844703000000067,22.587878787878811,23.061818181818158,23.092424242424279,18.336515151515144,18.014393939393948,17.974696969696993,18.71863636363635,null,6.6813358636363631,6.8943888939393929,16.232719696969699,null,1.1850283551646252,null,15.116880848935722,14.64940583848993,28.9,null,"2017-05-08","11:03:30","11:18:40"]
["V17","Schieberstellung 4 | Edelstahlgitter | 4L-WT |\n150 Pa | 200 kg/h",4,{"$f":"23+47-(47/2)","v":46.5},150,204.30769101515151,16.038227272727283,16.852878787878787,-0.81465151515151502,-193.25346269696971,29.214819500000011,139.5547394393939,1.6392058030303032,22.653313136363639,17.866656606060605,22.653313136363639,18.517252666666671,"42,18/54,67",29.5,85.135583000000139,23.039393939393911,22.894090909090917,22.025757575757556,18.023939393939386,17.744848484848493,17.831666666666671,18.107272727272733,null,6.2077601060606051,6.6150858636363621,16.445553030303032,null,1.36612710030854,null,31.132444981253052,29.214819465316808,28.9,null,"2017-05-09","10:38:50","10:54:00"]
["V18","Schieberstellung 4 | Edelstahlgitter | 4L-WT |\n250 Pa | 200 kg/h",4,46.5,250,204.3686087878788,16.072757575757581,17.213969696969698,-1.1412121212121213,-270.80558157575746,37.806210863636366,188.72389712121216,1.7166742878787871,23.235757545454543,18.038752515151511,23.235757545454543,18.950279969696965,"42,18/54,67",49.800000000000054,109.93576300000016,23.390757575757558,23.518636363636382,22.797424242424242,18.1219696969697,17.946818181818173,18.045909090909074,17.96136363636364,null,6.5923939090909114,7.1629999696969699,16.643363636363635,null,1.4304775349672758,null,41.079165978460665,37.806210983614591,28.9,null,"2017-05-09","11:16:10","11:31:20"]
["V19","Schieberstellung 4 | Edelstahlgitter | 4L-WT |\n300 Pa | 200 kg/h",4,46.5,300,204.41847927272727,16.092333333333329,17.379999999999995,-1.287666666666667,-305.6314508333333,41.451914060606093,213.54069143939392,1.7704201515151516,23.465424272727276,18.18109592424242,23.465424272727276,19.190801818181814,"42,18/54,67",60.199999999999932,120.6158240000002,23.550606060606039,23.700757575757599,23.14454545454543,18.226363636363633,18.106212121212099,18.211969696969696,17.952272727272721,null,6.7292576060606066,7.373090939393939,16.736166666666662,null,1.475424402991766,null,45.418288950101555,41.451913919096519,28.9,null,"2017-05-09","12:04:00","12:19:20",null,1248,1313]
[]
["V20","Schieberstellung 3-4 | Edelstahlgitter | 4L-WT |\n50 Pa | 200 kg/h",3.5,{"$f":"23+(47/4)","v":34.75},50,200.06402603076913,16.07464615384616,16.524261538461541,-0.44961538461538464,-104.44299286153846,10.818601784615382,56.919307615384589,1.4886871384615386,25.728599969230778,19.639789800000003,25.728599969230778,20.248280630769226,{"$error":"#DIV/0!"},5.6000000000000041,38.234565000000018,25.139230769230792,26.012153846153836,26.035230769230733,19.856461538461527,19.359846153846142,19.704923076923102,20.24476923076924,null,9.4291461230769222,9.6539538153846145,16.299453846153842,null,1.2405021223645469,null,11.076588269750724,10.818601821320598,28.9,null,"2017-06-12","13:08:50","13:23:40",null,{"$f":"AR26-64","v":621},685]
["V21","Schieberstellung 3-4 | Edelstahlgitter | 4L-WT |\n150 Pa | 200 kg/h",3.5,{"$f":"23+(47/4)","v":34.75},150,200.25050950769236,16.082984615384618,16.925446153846149,-0.84246153846153826,-195.88409076923085,22.813904215384614,114.81477490769231,1.6725571384615383,24.669087215384607,18.960553876923072,24.669087215384607,19.573588615384612,{"$error":"#DIV/0!"},18.799999999999979,68.64624599999992,24.758307692307678,24.6369230769231,24.611230769230758,19.245538461538466,18.719230769230787,18.91723076923077,19.526153846153829,null,8.1648718307692327,8.5861025999999967,16.504215384615389,null,1.3938357523419989,null,23.991196136195189,22.813904077283393,28.9,null,"2017-06-12","13:37:00","13:52:00",null,{"$f":"AR27-64","v":742},806]
["V22","Schieberstellung 3-4 | Edelstahlgitter | 4L-WT |\n250 Pa | 200 kg/h",3.5,34.75,250,201.2171045692308,16.103215384615378,17.206999999999997,-1.1037846153846151,-257.8698830923077,30.00132553846154,151.31169138461544,1.6986778153846156,24.698743692307687,18.871046169230777,24.698743692307687,19.608582215384619,{"$error":"#DIV/0!"},32.099999999999966,89.076154999999986,24.975538461538466,24.725384615384627,24.395230769230778,19.110461538461529,18.659846153846161,18.843076923076918,19.268307692307683,null,8.0436359999999993,8.595528307692307,16.655107692307695,null,1.4155143730806468,null,32.060387337653324,30.001325195566658,28.9,null,"2017-06-12","14:53:10","15:08:00",null,{"$f":"AR28-64","v":1068},1132]
["V23","Schieberstellung 3-4 | Edelstahlgitter | 4L-WT |\n300 Pa | 200 kg/h",3.5,34.75,300,203.78141501538454,16.002830769230769,17.269923076923067,-1.2670923076923075,-299.8064187846154,33.584705384615376,170.68730743076927,1.7468815692307693,24.929764061538457,18.855769246153852,24.929764061538457,19.683732076923082,{"$error":"#DIV/0!"},38.800000000000004,97.709718000000052,24.809692307692309,24.867384615384616,25.112153846153845,19.057230769230767,18.659076923076928,18.851230769230757,19.177846153846161,null,8.2933871384615401,8.9269332923076945,16.63637692307692,null,1.4557371019177556,null,36.152910864670254,33.584705603170953,28.9,null,"2017-06-12","16:01:00","16:16:00",null,{"$f":"AR29-64","v":1359},1423]
[]
["V24","Schieberstellung 3 | Edelstahlgitter | 4L-WT |\n50 Pa | 200 kg/h",3,32,50,198.80338695384617,15.951369230769236,16.321184615384613,-0.36981538461538466,-85.36618050769232,11.851510938461541,59.625354784615368,1.8600358615384611,23.15413332307692,18.726338476923075,23.15413332307692,18.877843969230764,{"$error":"#DIV/0!"},3.9000000000000039,32.056023000000039,23.176769230769253,23.223846153846164,23.060923076923061,18.77876923076921,18.587999999999994,18.811384615384593,19.816307692307685,null,7.0178564000000003,7.2027640923076932,16.136276923076927,null,1.5500309088083088,null,12.163936469683366,11.851510932997183,28.9,null,"2017-06-13","08:13:20","08:28:20",null,{"$f":"AR31-64","v":43},107]
["V25","Schieberstellung 3 | Edelstahlgitter | 4L-WT |\n150 Pa | 200 kg/h",3,32,150,199.29034539999998,15.962323076923083,16.624338461538464,-0.66201538461538467,-153.19002510769232,23.980817369230767,119.92103419999998,2.0726573076923076,22.350425661538456,18.313676969230766,22.350425661538456,18.535128707692305,{"$error":"#DIV/0!"},13.299999999999986,57.858592000000037,22.82292307692305,22.314307692307672,21.914153846153848,18.385999999999989,18.155846153846163,18.399230769230762,19.248923076923077,null,6.0570948923076928,6.3881025846153845,16.293330769230778,null,1.7272328908499257,null,25.291548551233163,23.980817370839485,28.9,null,"2017-06-13","08:41:10","08:56:00",null,{"$f":"AR32-64","v":162},226]
["V26","Schieberstellung 3 | Edelstahlgitter | 4L-WT |\n250 Pa | 200 kg/h",3,32,250,199.42056293846159,15.95887692307692,16.823030769230769,-0.86415384615384616,-200.09391704615388,32.250682076923077,166.18997919999993,2.1966719538461534,22.163133400000007,18.168374353846161,22.163133400000007,18.567231646153846,{"$error":"#DIV/0!"},23.099999999999984,75.655346999999921,22.080769230769228,22.072615384615371,22.336769230769214,18.22015384615387,18.008923076923075,18.274461538461527,18.754615384615388,null,5.7721795538461516,6.2042564769230752,16.390953846153842,null,1.8305716224840451,null,34.665121513348019,32.250681735698549,28.9,null,"2017-06-13","09:09:20","09:24:20",null,{"$f":"AR33-64","v":283},347]
["V27","Schieberstellung 3 | Edelstahlgitter | 4L-WT |\n300 Pa | 200 kg/h",3,32,300,199.2652703076923,15.964415384615387,16.899215384615388,-0.93479999999999985,-216.28440003076926,34.81429476923077,181.50127750769238,2.1882607076923075,22.176938461538455,18.122097446153845,22.176938461538455,18.617852292307695,{"$error":"#DIV/0!"},27.900000000000031,82.943169000000054,22.295538461538467,22.138000000000016,22.097692307692277,18.197846153846172,17.959846153846176,18.208307692307713,18.515692307692312,null,5.7451230769230754,6.2125230769230768,16.431815384615383,null,1.8236196663342126,null,37.646967749701837,34.814294788070669,28.9,null,"2017-06-13","10:30:50","10:45:50",null,{"$f":"AR34-64","v":632},696]
[]
["V28","Schieberstellung 2-3 | Edelstahlgitter | 4L-WT |\n50 Pa | 200 kg/h",2.5,{"$f":"23*0.75","v":17.25},50,199.14518212307689,15.978661538461539,16.333030769230763,-0.35436923076923088,-81.940590538461549,10.555556784615382,53.514793661538455,1.6902484461538463,23.741543599999993,18.667358984615383,23.741543599999993,19.168047600000008,{"$error":"#DIV/0!"},3.8000000000000043,31.660904000000027,23.803076923076915,23.71384615384618,23.707076923076947,18.74907692307692,18.512923076923066,18.740153846153849,19.2496923076923,null,7.5856974461538469,7.7628820615384626,16.155846153846149,null,1.4086129993313252,null,10.802273025324048,10.555556822118943,28.9,null,"2017-06-13","11:33:40","11:48:30",null,{"$f":"AR36-64","v":901},965]
["V29","Schieberstellung 2-3 | Edelstahlgitter | 4L-WT |\n150 Pa | 200 kg/h",2.5,{"$f":"23*0.75","v":17.25},150,199.20555646153838,15.982799999999997,16.630600000000001,-0.64780000000000015,-149.83442656923077,22.394639061538459,114.27535843076924,1.9896356923076925,22.673902584615384,18.222102553846156,22.673902584615384,18.757657907692305,{"$error":"#DIV/0!"},13.100000000000014,57.435316999999948,23.124769230769225,22.679076923076924,22.21738461538461,18.317538461538437,18.034153846153828,18.314923076923048,18.632615384615399,null,6.3672025846153844,6.6911025846153818,16.306699999999999,null,1.658083364914184,null,23.534246943970768,22.394638970880816,28.9,null,"2017-06-13","12:08:00","12:22:50",null,{"$f":"AR37-64","v":1048},1112]
["V30","Schieberstellung 2-3 | Edelstahlgitter | 4L-WT |\n250 Pa | 200 kg/h",2.5,17.25,250,199.12272516923073,15.98886153846154,16.843507692307693,-0.85464615384615361,-197.59614493846155,29.43040924615385,150.93841186153847,2.0164449230769228,22.702876892307685,18.176559046153852,22.702876892307685,18.792955199999994,{"$error":"#DIV/0!"},22.599999999999984,74.853723999999985,23.145384615384611,22.888307692307695,22.075846153846143,18.291384615384597,17.986615384615394,18.251846153846152,18.454461538461533,null,6.2866922769230769,6.7140153538461522,16.416184615384612,null,1.6804284004923256,null,31.431225211699132,29.43040936604201,28.9,null,"2017-06-13","12:53:00","13:07:50",null,{"$f":"AR38-64","v":1241},1305]
["V31","Schieberstellung 2-3 | Edelstahlgitter | 4L-WT |\n300 Pa | 200 kg/h",2.5,17.25,300,199.26832221538459,15.993384615384612,16.946738461538459,-0.95335384615384611,-220.57882190769229,33.207610430769236,173.02808973846157,2.1083258153846161,22.636287153846155,18.196656384615377,22.636287153846155,18.828221769230773,{"$error":"#DIV/0!"},27.299999999999972,82.068952999999979,22.841692307692313,22.631538461538458,22.434615384615377,18.291846153846141,18.005230769230767,18.292307692307674,18.424461538461525,null,6.1662256153846133,6.6429025384615361,16.470061538461536,null,1.757073347791404,null,35.77587100466171,33.207610506685505,28.9,null,"2017-06-13","13:26:50","13:41:40",null,{"$f":"AR39-64","v":1386},1450]
[]
["V32","Schieberstellung 2 | Edelstahlgitter | 4L-WT |\n50 Pa | 200 kg/h",2,23,50,199.03427481538461,15.988430769230774,16.214984615384612,-0.22655384615384622,-52.356569076923073,7.2829364000000023,51.637072861538456,2.3250523076923075,23.177282061538467,19.614261615384613,23.177282061538467,20.149052230769232,{"$error":"#DIV/0!"},1.799999999999998,22.208994000000008,22.776153846153825,23.206000000000017,23.549846153846126,19.376307692307709,19.322307692307696,20.144307692307699,19.751999999999995,null,7.0755743692307673,7.1888512923076915,16.101707692307695,null,1.9374050703630978,null,7.3995654194080727,7.2829364194708184,28.9,null,"2017-06-13","14:15:20","14:30:20",null,{"$f":"AR41-64","v":1594},1658]
["V33","Schieberstellung 2 | Edelstahlgitter | 4L-WT |\n150 Pa | 200 kg/h",2,23,150,199.20383052307699,16.008338461538461,16.47829230769231,-0.46995384615384622,-108.69983527692305,13.477221030769231,84.152460507692297,2.0400681999999994,24.073712800000003,19.315358969230768,24.073712800000003,20.215847353846151,{"$error":"#DIV/0!"},6.6000000000000068,41.249827000000053,23.739384615384616,24.184307692307684,24.297076923076915,18.79846153846152,18.797230769230751,20.349692307692294,19.096307692307686,null,7.8303974153846152,8.0653743384615346,16.243315384615382,null,1.700047689403996,null,13.881811616518222,13.477221108253712,28.9,null,"2017-06-13","14:54:30","15:09:30",null,{"$f":"AR42-64","v":1762},1826]
["V34","Schieberstellung 2 | Edelstahlgitter | 4L-WT |\n250 Pa | 200 kg/h",2,23,250,199.23695481538468,16.03773846153846,16.719538461538466,-0.68180000000000007,-157.72535070769229,18.991304753846158,128.40639906153842,2.3517479846153853,24.342882076923082,19.613369215384623,24.342882076923082,20.674360276923075,{"$error":"#DIV/0!"},11.79999999999999,54.600407999999916,23.753076923076915,24.337538461538443,24.938769230769243,18.749692307692303,18.78646153846152,21.304769230769224,18.972000000000019,null,7.9642436153846141,8.3051436153846137,16.378638461538461,null,1.9597669154141333,null,19.804315955189114,18.991304653893543,28.9,null,"2017-06-13","15:41:00","15:56:00",null,{"$f":"AR43-64","v":1961},2025]
["V35","Schieberstellung 2 | Edelstahlgitter | 4L-WT |\n300 Pa | 200 kg/h",2,23,300,198.77536586153849,15.937353846153844,16.52532307692308,-0.5879692307692308,-135.69925076923079,21.329262000000011,151.36298873846152,2.5032282615384625,22.298748707692308,19.19426666153846,22.298748707692308,19.620869169230765,{"$error":"#DIV/0!"},14.600000000000016,60.467113000000055,21.989538461538469,22.309230769230762,22.595846153846143,18.518923076923095,18.468923076923087,20.594461538461545,19.421230769230771,null,6.0674102461538482,6.3613948615384608,16.23133846153846,null,2.0861927115337995,null,22.364904562905409,21.32926202907711,28.9,null,"2017-06-14","08:24:30","08:39:30",null,{"$f":"AR44-64","v":91},155]
[]
["V36","Schieberstellung 1-2 | Edelstahlgitter | 4L-WT |\n50 Pa | 200 kg/h",1.5,{"$f":"0.5*23","v":11.5},50,198.84523673846158,15.944430769230769,16.04952307692308,-0.10509230769230773,-24.264413353846145,4.5136230923076939,71.550982292307694,6.4844906923076957,21.320471815384622,20.173041030769234,21.320471815384622,20.272805076923074,{"$error":"#DIV/0!"},0.39999999999999958,11.034172000000009,21.595999999999968,21.097538461538448,21.269384615384631,20.183230769230786,20.056307692307687,20.278923076923093,20.716769230769241,null,5.3234948923076928,5.3760410461538459,15.996976923076927,null,5.4043682907550155,null,4.5582999381389078,4.5136231070118562,28.9,null,"2017-06-14","08:14:20","08:29:10",null,{"$f":"AR46-64","v":244},308]
["V37","Schieberstellung 1-2 | Edelstahlgitter | 4L-WT |\n150 Pa | 200 kg/h",1.5,{"$f":"0.5*23","v":11.5},150,198.94390980000003,15.945076923076924,16.056338461538463,-0.11126153846153858,-25.700531523076926,4.721667292307691,109.29102653846154,4.6879946615384602,21.387856415384611,20.437307615384611,21.387856415384611,20.685557169230773,{"$error":"#DIV/0!"},2,23.312959000000021,21.924461538461539,21.201076923076947,21.03815384615384,20.537846153846139,20.328307692307689,20.44507692307695,20.016615384615402,null,5.3871487230769244,5.4427794923076922,16.000707692307685,null,3.9071050119395019,null,4.7705126852894724,4.7216672968881603,28.9,null,"2017-06-14","09:21:00","09:36:00",null,{"$f":"AR47-64","v":333},397]
["V38","Schieberstellung 1-2 | Edelstahlgitter | 4L-WT |\n250 Pa | 200 kg/h",1.5,11.5,250,198.76488416923075,15.951907692307689,16.066092307692312,-0.11418461538461541,-26.352491876923072,5.8311037384615387,504.46692689230787,16.156563415384618,20.470769292307693,20.249005107692309,20.470769292307693,20.313492923076922,{"$error":"#DIV/0!"},3.6999999999999957,31.223653000000009,20.897692307692292,20.217538461538485,20.296307692307671,20.501538461538455,20.16738461538462,20.076461538461537,19.80953846153843,null,4.461769292307693,4.518861600000001,16.008999999999993,null,13.459946017162652,null,5.9060714778416843,5.8311036079783696,28.9,null,"2017-06-14","10:15:10","10:30:10",null,{"$f":"AR48-64","v":565},629]
["V39","Schieberstellung 1-2 | Edelstahlgitter | 4L-WT |\n300 Pa | 200 kg/h",1.5,11.5,300,202.31644723076928,15.964876923076918,16.083723076923075,-0.11884615384615388,-27.918213276923073,6.1112054307692301,472.12504432307696,13.626225553846155,20.532646153846155,20.278307753846157,20.532646153846155,20.355510753846158,{"$error":"#DIV/0!"},4.5999999999999996,34.648263000000028,20.942153846153847,20.249076923076924,20.407076923076932,20.582615384615377,20.175538461538469,20.0756923076923,19.809230769230755,null,4.508346153846154,4.5677692307692306,16.0243,null,11.353720866780604,null,6.1921890409232958,6.1112054374447933,28.9,null,"2017-06-14","11:00:00","11:15:00",null,{"$f":"AR49-64","v":757},821]
[]
["V40","Schieberstellung 1 | Edelstahlgitter | 4L-WT |\n50 Pa | 200 kg/h",1,0,50,202.2512661230769,15.972923076923081,16.084830769230763,-0.11190769230769236,-26.279490738461529,4.6370206769230764,145.71543496923078,13.205833753846157,21.640174338461545,20.995712784615385,21.640174338461545,21.101225800000005,{"$error":"#DIV/0!"},0.39999999999999958,11.034172000000009,21.988000000000007,21.499538461538442,21.434153846153848,21.248153846153837,20.977384615384615,20.76092307692306,21.019846153846139,null,5.6112974153846151,5.6672512615384623,16.028876923076925,null,11.006630430424343,null,4.6835321245446222,4.6370207981377414,28.9,null,"2017-06-14","10:59:30","11:14:30",null,{"$f":"AR51-64","v":952},1016]
["V41","Schieberstellung 1 | Edelstahlgitter | 4L-WT |\n150 Pa | 200 kg/h",1,0,150,202.34788846153842,15.978384615384616,16.102476923076921,-0.12409230769230771,-29.154860861538456,5.0486205692307697,180.50619910769231,7.7427409076923057,21.753169246153846,21.058435923076917,21.753169246153846,21.269748876923067,{"$error":"#DIV/0!"},2,23.312959000000021,21.933538461538479,21.757692307692306,21.568923076923078,21.085846153846152,21.113384615384597,20.97584615384617,20.322000000000003,null,5.7127384769230742,5.7747846307692328,16.040430769230774,null,6.4523448303678261,null,5.1036184516502798,5.0486205771161199,28.9,null,"2017-06-14","12:11:40","12:26:40",null,{"$f":"AR52-64","v":1064},1128]
["V42","Schieberstellung 1 | Edelstahlgitter | 4L-WT |\n250 Pa | 200 kg/h",1,0,250,202.26438781538459,15.986876923076926,16.119969230769232,-0.1330923076923077,-31.256722353846154,6.2036659076923089,1320.0071240153845,42.832183523076928,21.025512861538463,20.905112769230772,21.025512861538463,20.946684800000007,{"$error":"#DIV/0!"},3.5999999999999961,30.818113999999973,21.075999999999986,20.926769230769242,21.07399999999997,20.870769230769255,21.063999999999986,20.780769230769206,20.076769230769226,null,4.9720897846153846,5.038635938461538,16.053423076923075,null,35.692387634906716,null,6.2868484096029942,6.2036658548139183,28.9,null,"2017-06-14","13:20:40","13:35:40",null,{"$f":"AR53-64","v":1360},1424]
["V43","Schieberstellung 1 | Edelstahlgitter | 4L-WT |\n300 Pa | 200 kg/h",1,0,300,202.28975841538463,15.996107692307694,16.134523076923074,-0.13841538461538466,-32.51096896923076,6.554585215384618,-16439.572466546873,-474.47032310937493,20.955887184615388,20.952553815384629,20.955887184615388,20.953881784615373,{"$error":"#DIV/0!"},4.5999999999999996,34.648263000000028,20.990000000000009,20.83830769230768,21.041076923076893,20.898461538461547,21.16753846153847,20.790923076923061,19.905076923076923,null,4.8905717999999991,4.9597794923076925,16.065315384615378,null,-395.56888890070456,null,6.6476600431193642,6.5545851778326956,28.9,null,"2017-06-14","13:47:30","14:02:30",null,{"$f":"AR54-64","v":1475},1539]
[]
["V44","Schieberstellung 5 |\n50 Pa | 200 kg/h | lenkendes Alu-Lineargitter | 4L-WT",5,null,50,201.1435704153846,16.020399999999999,16.785446153846152,-0.76504615384615382,-178.67651441538459,23.354396292307698,116.7231688769231,1.6310749999999998,23.671082076923081,18.594887138461541,23.671082076923081,19.099111384615384,{"$error":"#DIV/0!"},20.5,71.562111999999999,24.15476923076924,23.875846153846144,22.982000000000014,18.453692307692325,18.711538461538474,18.617846153846145,19.151846153846165,null,7.2681589999999998,7.6506820769230774,16.402923076923081,null,1.3592918373067198,null,24.583749002095448,23.354396267238776,28.9,null,"2017-06-14","14:23:30","14:38:30",null,{"$f":"AR56-64","v":1677},1741,null,{"$f":"(AJ56-AJ4)/AJ4","v":1.3970125968806528E-2}]
["V45","Schieberstellung 5 |\n100 Pa | 200 kg/h | lenkendes Alu-Lineargitter | 4L-WT",5,null,100,201.35295846153844,16.037676923076919,17.147476923076923,-1.1098000000000001,-259.46281943076934,35.855678815384621,191.13823247692306,1.8763239230769229,23.273912799999998,18.599712861538464,23.273912799999998,19.219717938461535,{"$error":"#DIV/0!"},42.300000000000018,101.86846299999986,23.860615384615386,23.141692307692306,22.819384615384603,18.50599999999999,18.712461538461547,18.580769230769231,18.898615384615397,null,6.681335876923078,7.2362358769230752,16.592576923076926,null,1.5634906412217073,null,38.834142601496886,35.855678929236745,28.9,null,"2017-06-14","15:31:10","15:46:10",null,{"$f":"AR57-64","v":1919},1983,null,{"$f":"(AJ57-AJ5)/AJ5","v":-3.0876950386932459E-2}]
["V46","Schieberstellung 5 |\n150 Pa | 200 kg/h | lenkendes Alu-Lineargitter | 4L-WT",5,null,150,201.5188392615384,16.045861538461534,17.475984615384618,-1.4301230769230775,-334.62799093846155,44.122572307692288,243.77683541538471,2.2906793230769238,23.630000030769235,18.75075378461538,23.630000030769235,19.53032253846154,{"$error":"#DIV/0!"},47.4,125.09879600000016,23.719846153846166,23.432307692307699,23.738153846153825,18.655538461538466,18.846461538461536,18.74938461538461,18.82738461538462,null,6.8690769538461529,7.5841384923076935,16.760923076923071,null,1.6216228334554195,null,48.716043421888074,44.12257213111689,28.9,null,"2017-06-14","15:50:20","",null,{"$f":"AR58-64","v":2001},2065,null,-2.5468164380275347E-2]
["V47","Schieberstellung 5 |\n250 Pa | 200 kg/h | lenkendes Alu-Lineargitter | 4L-WT",5,null,250,202.0117431538462,15.99452307692308,17.731723076923068,-1.7371999999999999,-407.47295304615386,54.139224523076926,315.240248723077,1.9560519999999997,23.520928153846146,19.238005092307688,23.520928153846146,19.660392138461546,{"$error":"#DIV/0!"},108.5,161.16148299999992,23.542615384615353,23.613384615384611,23.40584615384617,19.13323076923076,19.346615384615387,19.234769230769256,19.80846153846154,null,6.6578050769230748,7.5264050769230755,16.863123076923081,null,1.6299955055913045,null,61.202722589327344,54.139224931094127,28.9,null,"2017-06-16","07:44:20","07:59:10",null,{"$f":"AR59-64","v":105},169,null,-4.0087719246847162E-2]
["V48","Schieberstellung 5 |\n300 Pa | 200 kg/h | lenkendes Alu-Lineargitter | 4L-WT",5,null,300,201.95642340000001,16.006061538461545,17.87086153846154,-1.8647999999999996,-437.28384541538463,58.201755630769227,349.84120529230751,1.9724721999999999,23.519287138461536,19.192005107692303,23.519287138461536,19.78617293846154,{"$error":"#DIV/0!"},132,177.3617909999999,23.559999999999992,23.600615384615374,23.396923076923095,19.084923076923072,19.304307692307678,19.187076923076933,19.443384615384602,null,6.5808255999999972,7.5132256000000011,16.938461538461535,null,1.643498483362082,null,66.448303473662648,58.20175597832008,28.9,null,"2017-06-16","08:39:10","08:54:00",null,{"$f":"AR60-64","v":340},404,null,-2.9509584171820522E-2]
[]
["V49","Schieberstellung 5 |\n150 Pa | 200 kg/h | Edelstahlgitter | 2L-WT",5,null,150,198.93811509090904,15.978439393939391,18.041257575757577,-2.0628181818181819,-476.49134877272735,50.487755106060604,274.31738709090911,2.1422275454545452,25.416151484848484,19.640838348484834,25.416151484848484,20.228172378787882,{"$error":"#DIV/0!"},66.5,128.05240500000014,25.077121212121206,25.199393939393961,25.971515151515167,19.812424242424218,19.428030303030305,19.682575757575759,20.443636363636372,null,8.4063029999999994,9.4377120909090912,17.009848484848487,null,1.7853000781337431,null,56.684887944555783,50.487755243365072,28.9,null,"2017-06-23","11:25:30","11:40:40",null,{"$f":"AR62-65","v":733},798,null,{"$f":"(AJ62-AJ6)/AJ6","v":0.11511914236153296}]
[]
["V50","Schieberstellung 5 |\n150 Pa | 200 kg/h | Edelstahlgitter | 4L-WT | MQG 0 °",5,null,150,199.53666895454549,16.011469696969698,17.993272727272732,-1.9818030303030301,-459.14903136363642,50.323796606060618,243.07051369696967,1.9102757575757576,25.135540393939401,19.133984833333333,25.135540393939401,19.492639787878783,{"$error":"#DIV/0!"},65,127.24367499999988,24.772575757575762,25.1719696969697,25.462727272727278,19.184090909090926,19.015757575757565,19.201666666666686,20.359545454545433,null,8.1331691818181788,9.1240706969696994,17.002371212121211,null,1.5917831293904854,null,56.458776148204215,50.323796644274871,28.9,null,"2017-06-28","12:42:00","12:57:10",null,{"$f":"AR64-65","v":1161},1226,null,{"$f":"RIGHT(B64,3)","v":"0 °"},{"$f":"(AJ64-$AJ$64)/$AJ$64","v":0}]
["V51","Schieberstellung 5 |\n150 Pa | 200 kg/h | Edelstahlgitter | 4L-WT | MQG 15 °",5,null,150,199.5176144242424,15.996666666666673,17.98298484848484,-1.9863181818181819,-460.15327154545446,51.946123409090909,264.65788919696968,2.0644652878787877,24.855010121212128,19.298085833333328,24.855010121212128,19.662107954545451,{"$error":"#DIV/0!"},66,128.19682000000006,25.287727272727256,24.548636363636344,24.728333333333328,19.34878787878786,19.199696969696991,19.34636363636362,20.459090909090921,null,7.8651843636363656,8.8583434545454551,16.989825757575755,null,1.7202569404774692,null,58.506274042204147,51.946123252655646,28.9,null,"2017-06-28","09:12:30","09:27:40",null,{"$f":"AR65-65","v":264},329,null,{"$f":"RIGHT(B65,4)","v":"15 °"},{"$f":"(AJ65-$AJ$64)/$AJ$64","v":3.2237762580763857E-2}]
["V52","Schieberstellung 5 |\n150 Pa | 200 kg/h | Edelstahlgitter | 4L-WT | MQG 30 °",5,null,150,199.55892827272729,16.002909090909089,17.967621212121209,-1.964712121212121,-455.24619837878777,49.584509439393941,244.33469177272718,1.9059340454545457,25.183858560606062,19.32091412121212,25.183858560606062,19.619231772727272,{"$error":"#DIV/0!"},66,128.19682000000006,25.436363636363634,25.161363636363639,24.955606060606051,19.401515151515152,19.175909090909094,19.386060606060621,20.614242424242441,null,8.1985934090909094,9.1809494696969693,16.985265151515151,null,1.5883055165617082,null,55.526685567369483,49.584509653930056,28.9,null,"2017-06-28","10:15:10","10:30:20",null,{"$f":"AR66-65","v":532},597,null,{"$f":"RIGHT(B66,4)","v":"30 °"},-1.4690604438505166E-2]
["V53","Schieberstellung 5 |\n150 Pa | 200 kg/h | Edelstahlgitter | 4L-WT | MQG 45 °",5,null,150,199.68333286363634,16.003257575757573,17.918787878787874,-1.9155303030303037,-444.1228315606059,48.027357151515147,301.79572378787873,2.3649629848484848,25.250747484848489,20.137616106060602,25.250747484848489,20.852970621212119,{"$error":"#DIV/0!"},65.378787878787875,127.60471477272718,24.963484848484853,25.3980303030303,25.390606060606075,20.117727272727258,19.195909090909105,21.099090909090883,20.459090909090925,null,8.2897247575757582,9.2474899090909091,16.961022727272727,null,1.9708173855697637,null,53.57674999401376,48.027357071487749,28.9,null,"2017-06-28","11:01:10","11:16:20",null,729,794,null,"45 °",-4.5633273439602023E-2]
[]
["V54","Schieberstellung 5 |\n150 Pa | 200 kg/h | Edelstahlgitter | 4L-WT | MQG 0 °",5,null,150,197.6052378787879,15.955772727272725,17.887227272727273,-1.931454545454546,-443.15609703030299,51.134173000000004,250.72376118181819,1.9660961818181819,24.622419196969698,19.314954590909096,24.622419196969698,19.343377833333331,{"$error":"#DIV/0!"},65.433333333333323,127.52391675757562,24.367575757575757,24.756515151515149,24.742878787878791,19.470606060606087,19.165606060606073,19.308636363636342,20.997727272727289,null,7.7009191969696982,8.6666464696969712,16.921499999999998,null,1.6384650430985046,null,57.54713248508925,51.134172974260082,28.9,null,"2017-06-29","07:53:50","08:09:00",null,{"$f":"AR69-65","v":178},243,null,{"$f":"RIGHT(B69,3)","v":"0 °"},{"$f":"(AJ69-$AJ$69)/$AJ$69","v":0}]
["V55","Schieberstellung 5 |\n150 Pa | 200 kg/h | Edelstahlgitter | 4L-WT | MQG 15 °",5,null,150,194.92535866666671,15.965090909090915,17.857848484848482,-1.8927575757575761,-428.38421995454559,51.150355333333323,265.63955613636352,2.0820189242424254,24.340181742424239,19.34420706060606,24.340181742424239,19.523649636363633,{"$error":"#DIV/0!"},65.5,127.58748399999988,24.342575757575762,24.194696969696967,24.482424242424241,19.587121212121204,19.148939393939397,19.297878787878759,20.703484848484866,null,7.428712045454545,8.3750908333333314,16.911469696969704,null,1.7351087564393435,null,57.667331218020806,51.150355814808094,28.9,null,"2017-06-29","08:26:40","08:41:50",null,{"$f":"AR70-65","v":319},384,null,{"$f":"RIGHT(B70,4)","v":"15 °"},{"$f":"(AJ70-$AJ$69)/$AJ$69","v":3.1647799517865168E-4}]
["V56","Schieberstellung 5 |\n150 Pa | 200 kg/h | Edelstahlgitter | 4L-WT | MQG 30 °",5,null,150,193.69629478787874,15.967878787878789,17.871227272727275,-1.9033484848484858,-428.06881187878787,50.326482242424227,295.87211989393927,2.3189744848484843,24.473712151515159,19.694595939393945,24.473712151515159,20.152666030303024,{"$error":"#DIV/0!"},65.5,127.58748399999988,24.355151515151505,24.487272727272739,24.577575757575744,19.834090909090911,19.125303030303012,20.126060606060619,20.479242424242443,null,7.5541591212121233,8.5058333636363592,16.919553030303028,null,1.9324912459510328,null,56.666882614915608,50.326482060547477,28.9,null,"2017-06-29","09:16:40","09:31:50",null,{"$f":"AR71-65","v":533},598,null,{"$f":"RIGHT(B71,4)","v":"30 °"},-1.5795521208863211E-2]
["V57","Schieberstellung 5 |\n150 Pa | 200 kg/h | Edelstahlgitter | 4L-WT | MQG 45 °",5,null,150,198.30367331818184,15.966257575757574,17.672696969696979,-1.7064393939393934,-392.89530800000017,47.399540893939388,261.72499480303043,2.0559459393939399,24.255479803030301,19.452318181818178,24.255479803030301,19.772085090909087,{"$error":"#DIV/0!"},65.199999999999932,127.30149700000015,23.919696969696975,24.509545454545467,24.337121212121197,19.363787878787868,18.93151515151515,20.062121212121212,20.440606060606065,null,7.4360025303030293,8.2892222272727292,16.819477272727273,null,1.7132947837103019,null,52.838874406830854,47.399540853158683,28.9,null,"2017-06-29","09:45:00","10:00:20",null,655,720,null,"45 °",-7.3035934755048007E-2]
[null,null,null,null,null,null,null,{"$f":"F72*4.18*I72/3600","v":-0.39291210457568909},{"$f":"ABS(H73)*3600/(N72-O72)/1.004/1.2","v":244.43069913152931},{"$f":"J72*3/(N72-O72)","v":-245.3979309783351},null,{"$f":"I73/T72","v":1.9200928888646849}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"spezifische Kühlleistung (mit Vorlauftemperatur) [W/K]",null,null,null,null,null,null,null,"Induktionsverhältnis [-]"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Schieberstellung",50,150,250,300,"Pa",null,null,"Schieberstellung",50,150,250,300,null,null,null,null,"2L/lenk.Alu",{"$f":"AT62*AJ58","v":5.0793526625190522},"W/K"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,{"$f":"IFERROR(AJ51,\"\")","v":4.6370207981377414},{"$f":"IFERROR(AJ52,\"\")","v":5.0486205771161199},{"$f":"IFERROR(AJ53,\"\")","v":6.2036658548139183},{"$f":"IFERROR(AJ54,\"\")","v":6.5545851778326956},null,null,null,1,{"$f":"IFERROR(AG51,\"\")","v":11.006630430424343},{"$f":"IFERROR(AG52,\"\")","v":6.4523448303678261},{"$f":"IFERROR(AG53,\"\")","v":35.692387634906716},{"$f":"IFERROR(AG54,\"\")","v":-395.56888890070456},null,null,null,null,null,-0.89876275650702386]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.5,{"$f":"IFERROR(AJ46,\"\")","v":4.5136231070118562},{"$f":"IFERROR(AJ47,\"\")","v":4.7216672968881603},{"$f":"IFERROR(AJ48,\"\")","v":5.8311036079783696},{"$f":"IFERROR(AJ49,\"\")","v":6.1112054374447933},null,null,null,1.5,{"$f":"IFERROR(AG46,\"\")","v":5.4043682907550155},{"$f":"IFERROR(AG47,\"\")","v":3.9071050119395019},{"$f":"IFERROR(AG48,\"\")","v":13.459946017162652},{"$f":"IFERROR(AG49,\"\")","v":11.353720866780604}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,{"$f":"IFERROR(AJ41,\"\")","v":7.2829364194708184},{"$f":"IFERROR(AJ42,\"\")","v":13.477221108253712},{"$f":"IFERROR(AJ43,\"\")","v":18.991304653893543},{"$f":"IFERROR(AJ44,\"\")","v":21.32926202907711},null,null,null,2,{"$f":"IFERROR(AG41,\"\")","v":1.9374050703630978},{"$f":"IFERROR(AG42,\"\")","v":1.700047689403996},{"$f":"IFERROR(AG43,\"\")","v":1.9597669154141333},{"$f":"IFERROR(AG44,\"\")","v":2.0861927115337995}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.5,{"$f":"IFERROR(AJ36,\"\")","v":10.555556822118943},{"$f":"IFERROR(AJ37,\"\")","v":22.394638970880816},{"$f":"IFERROR(AJ38,\"\")","v":29.43040936604201},{"$f":"IFERROR(AJ39,\"\")","v":33.207610506685505},null,null,null,2.5,{"$f":"IFERROR(AG36,\"\")","v":1.4086129993313252},{"$f":"IFERROR(AG37,\"\")","v":1.658083364914184},{"$f":"IFERROR(AG38,\"\")","v":1.6804284004923256},{"$f":"IFERROR(AG39,\"\")","v":1.757073347791404}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,{"$f":"IFERROR(AJ31,\"\")","v":11.851510932997183},{"$f":"IFERROR(AJ32,\"\")","v":23.980817370839485},{"$f":"IFERROR(AJ33,\"\")","v":32.250681735698549},{"$f":"IFERROR(AJ34,\"\")","v":34.814294788070669},null,null,null,3,{"$f":"IFERROR(AG31,\"\")","v":1.5500309088083088},{"$f":"IFERROR(AG32,\"\")","v":1.7272328908499257},{"$f":"IFERROR(AG33,\"\")","v":1.8305716224840451},{"$f":"IFERROR(AG34,\"\")","v":1.8236196663342126}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.5,{"$f":"IFERROR(AJ26,\"\")","v":10.818601821320598},{"$f":"IFERROR(AJ27,\"\")","v":22.813904077283393},{"$f":"IFERROR(AJ28,\"\")","v":30.001325195566658},{"$f":"IFERROR(AJ29,\"\")","v":33.584705603170953},null,null,null,3.5,{"$f":"IFERROR(AG26,\"\")","v":1.2405021223645469},{"$f":"IFERROR(AG27,\"\")","v":1.3938357523419989},{"$f":"IFERROR(AG28,\"\")","v":1.4155143730806468},{"$f":"IFERROR(AG29,\"\")","v":1.4557371019177556}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,{"$f":"AJ21","v":14.64940583848993},{"$f":"AJ22","v":29.214819465316808},{"$f":"AJ23","v":37.806210983614591},{"$f":"AJ24","v":41.451913919096519},null,null,null,4,{"$f":"$AG$21","v":1.1850283551646252},{"$f":"$AG$22","v":1.36612710030854},{"$f":"$AG$23","v":1.4304775349672758},{"$f":"$AG$24","v":1.475424402991766}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.5,{"$f":"AJ16","v":22.916657095657051},{"$f":"AJ17","v":39.956716208734747},{"$f":"AJ18","v":50.317188721015995},{"$f":"AJ19","v":53.976719522299419},null,null,null,4.5,{"$f":"$AG$16","v":1.5753122171642233},{"$f":"$AG$17","v":1.6009211241131855},{"$f":"$AG$18","v":1.659053300341546},{"$f":"$AG$19","v":1.6611486231078021}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,{"$f":"AJ4","v":23.03262755884905},{"$f":"AJ6","v":45.275660084576351},{"$f":"AJ7","v":56.40017949204293},{"$f":"AJ8","v":59.971489701578271},null,null,null,5,{"$f":"$AG$4","v":1.1772826772216338},{"$f":"$AG$5","v":1.4535641399443229},{"$f":"$AG$6","v":1.5347638171095581},{"$f":"$AG$7","v":1.6997201404505884}]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,"Schieberstellung 5 | 200 kg/h | Edelstahlgitter"]
[null,null,null,null,null,null,"q_Sek_Mittel [W/K]","q_Sek_Vorlauf [W/K]","Induktionsverhältnis [-]"]
[null,null,null,null,null,"a =",{"$f":"TRANSPOSE(LINEST(AI4:AI8,T4:T8^{0,1,2},0,0))","v":-1.2516450260312778E-3},{"$f":"TRANSPOSE(LINEST(AJ4:AJ8,T4:T8^{0,1,2},0,0))","v":-1.3449692801279381E-3},{"$f":"TRANSPOSE(LINEST(AG4:AG8,$T$4:$T$8^{0,1,2,3},0,0))","v":1.2443680629820565E-7}]
[null,null,null,null,null,"b =",0.74248326886875993,0.69126332245931588,-8.9656021383573891E-5]
[null,null,null,null,null,"c =",-23.43815989006837,-20.347147683109299,2.1283361534709354E-2]
[null,null,null,null,null,"d =","-","-",5.381577023475391E-2]
[null,null,null,null,null,null,"Schieberstellung 5 | 150 Pa | Edelstahlgitter"]
[null,null,null,null,null,null,"q_Sek_Mittel [W/K]","q_Sek_Vorlauf [W/K]","Δp_W [kPa]"]
[null,null,null,null,null,"a =",{"$f":"TRANSPOSE(LINEST(AI10:AI14,F10:F14^{0,1,2},0,0))","v":-4.3918816591838274E-4},{"$f":"TRANSPOSE(LINEST(AJ10:AJ14,F10:F14^{0,1,2},0,0))","v":-5.12123588789378E-4},{"$f":"TRANSPOSE(LINEST(AK10:AK14,F10:F14^{0,1,2},0,0))","v":5.3310780995450386E-4}]
[null,null,null,null,null,"b =",0.22100962524885573,0.26093659443453493,4.0148386420608223E-2]
[null,null,null,null,null,"c =",25.872886088237269,15.59498951766313,-1.1622226709970782]
[null,null,null,null,null,"d =","-","-","-"]
[]
[null,null,null,null,null,null,"Schieberstellung 4 - 5 | 200 kg/h | Edelstahlgitter"]
[null,null,null,null,null,null,"q_Sek_Mittel [W/K]","q_Sek_Vorlauf [W/K]","Induktionsverhältnis [-]"]
[null,null,null,null,null,"a =",{"$f":"TRANSPOSE(LINEST(AI16:AI19,T16:T19^{0,1,2},0,0))","v":-6.6642673593035639E-4},{"$f":"TRANSPOSE(LINEST(AJ16:AJ19,T16:T19^{0,1,2},0,0))","v":-7.8879998939821588E-4},{"$f":"TRANSPOSE(LINEST(AG16:AG19,$T$16:$T$19^{0,1,2,3},0,0))","v":-5.7439677762013602E-7}]
[null,null,null,null,null,"b =",0.54346474413815105,0.50773133504557466,1.9517556861462542E-4]
[null,null,null,null,null,"c =",-7.1656888534648049,-5.6490087781522567,-1.9903853591772606E-2]
[null,null,null,null,null,"d =","-","-",2.1964183501356502]
[]
[null,null,null,null,null,null,"Schieberstellung 4 | 200 kg/h | Edelstahlgitter"]
[null,null,null,null,null,null,"q_Sek_Mittel [W/K]","q_Sek_Vorlauf [W/K]","Induktionsverhältnis [-]"]
[null,null,null,null,null,"a =",{"$f":"TRANSPOSE(LINEST(AI21:AI24,T21:T24^{0,1,2},0,0))","v":-3.5322553889501426E-4},{"$f":"TRANSPOSE(LINEST(AJ21:AJ24,T21:T24^{0,1,2},0,0))","v":-6.1325681274211478E-4},{"$f":"TRANSPOSE(LINEST(AG26:AG29,$T$21:$T$24^{0,1,2,3},0,0))","v":1.8366492125289686E-6}]
[null,null,null,null,null,"b =",0.47509223857288485,0.47086406898250244,-4.9829587153471468E-4]
[null,null,null,null,null,"c =",-6.7969469080555704,-6.4673730546526533,4.5377695440521677E-2]
[null,null,null,null,null,"d =","-","-",8.9230183171943901E-3]
[]
[null,null,null,null,null,null,"Schieberstellung 3 - 4 | 200 kg/h | Edelstahlgitter"]
[null,null,null,null,null,null,"q_Sek_Mittel [W/K]","q_Sek_Vorlauf [W/K]","Induktionsverhältnis [-]"]
[null,null,null,null,null,"a =",{"$f":"TRANSPOSE(LINEST(AI26:AI29,T26:T29^{0,1,2},0,0))","v":-2.1740415911186894E-5},{"$f":"TRANSPOSE(LINEST(AJ26:AJ29,T26:T29^{0,1,2},0,0))","v":-3.2539344487327975E-4},{"$f":"TRANSPOSE(LINEST(AG26:AG29,$T$26:$T$29^{0,1,2,3},0,0))","v":3.3978555186084787E-6}]
[null,null,null,null,null,"b =",0.42096493441812022,0.42371855754098448,-7.4413176352861813E-4]
[null,null,null,null,null,"c =",-4.9570009501397418,-4.8789998553843628,5.4678122843289545E-2]
[null,null,null,null,null,"d =","-","-",4.7819515605044931E-2]
[]
[null,null,null,null,null,null,"Schieberstellung 3 | 200 kg/h | Edelstahlgitter"]
[null,null,null,null,null,null,"q_Sek_Mittel [W/K]","q_Sek_Vorlauf [W/K]","Induktionsverhältnis [-]"]
[null,null,null,null,null,"a =",{"$f":"TRANSPOSE(LINEST(AI31:AI34,T31:T34^{0,1,2},0,0))","v":-4.4374496584180366E-4},{"$f":"TRANSPOSE(LINEST(AJ31:AJ34,T31:T34^{0,1,2},0,0))","v":-8.5808171469170264E-4},{"$f":"TRANSPOSE(LINEST(AG31:AG34,$T$31:$T$34^{0,1,2,3},0,0))","v":-4.8179879437619301E-6}]
[null,null,null,null,null,"b =",0.55666033480873489,0.55409717990974094,7.7337873189837775E-4]
[null,null,null,null,null,"c =",-5.2589254542273602,-5.0585436523727667,-3.2654753556642983E-2]
[null,null,null,null,null,"d =","-","-",1.9608037333044359]
[]
[null,null,null,null,null,null,"Schieberstellung 2 - 3 | 200 kg/h | Edelstahlgitter"]
[null,null,null,null,null,null,"q_Sek_Mittel [W/K]","q_Sek_Vorlauf [W/K]","Induktionsverhältnis [-]"]
[null,null,null,null,null,"a =",{"$f":"TRANSPOSE(LINEST(AI36:AI39,T36:T39^{0,1,2},0,0))","v":2.2604222233203584E-4},{"$f":"TRANSPOSE(LINEST(AJ36:AJ39,T36:T39^{0,1,2},0,0))","v":-2.5742600811024023E-4},{"$f":"TRANSPOSE(LINEST(AG36:AG39,$T$36:$T$39^{0,1,2,3},0,0))","v":1.1377882758390694E-5}]
[null,null,null,null,null,"b =",0.46324330287383159,0.47295525823126394,-2.0597909478137096E-3]
[null,null,null,null,null,"c =",-4.0460619303330949,-4.1210611055501998,0.12356955215589369]
[null,null,null,null,null,"d =","-","-",-0.80005307230172984]
[]
[null,null,null,null,null,null,"Schieberstellung 2 | 200 kg/h | Edelstahlgitter"]
[null,null,null,null,null,null,"q_Sek_Mittel [W/K]","q_Sek_Vorlauf [W/K]","Induktionsverhältnis [-]"]
[null,null,null,null,null,"a =",{"$f":"TRANSPOSE(LINEST(AI41:AI44,T41:T44^{0,1,2},0,0))","v":2.5285551243670805E-3},{"$f":"TRANSPOSE(LINEST(AJ41:AJ44,T41:T44^{0,1,2},0,0))","v":2.0684941700764561E-3},{"$f":"TRANSPOSE(LINEST(AG41:AG44,$T$41:$T$44^{0,1,2,3},0,0))","v":-2.290664813885283E-5}]
[null,null,null,null,null,"b =",0.18475286233817945,0.19869729047194054,3.6897715133420062E-3]
[null,null,null,null,null,"c =",2.0336196488382861,1.8346343218917063,-0.17535385192022312]
[null,null,null,null,null,"d =","-","-",4.2628244431455062]
[]
[null,null,null,null,null,null,"Schieberstellung 1 - 2 | 200 kg/h | Edelstahlgitter"]
[null,null,null,null,null,null,"q_Sek_Mittel [W/K]","q_Sek_Vorlauf [W/K]","Induktionsverhältnis [-]"]
[null,null,null,null,null,"a =",{"$f":"TRANSPOSE(LINEST(AI46:AI49,T46:T49^{0,1,2},0,0))","v":4.3034830213071031E-3},{"$f":"TRANSPOSE(LINEST(AJ46:AJ49,T46:T49^{0,1,2},0,0))","v":4.2045578432796608E-3},{"$f":"TRANSPOSE(LINEST(AG46:AG49,$T$46:$T$49^{0,1,2,3},0,0))","v":-9.5977903231936369E-3}]
[null,null,null,null,null,"b =",-0.12255207197617404,-0.11968934293681835,0.69518698416432467]
[null,null,null,null,null,"c =",5.3710921581475102,5.3072520795472871,-15.145788231458589]
[null,null,null,null,null,"d =","-","-",100.77861771830874]
[]
[null,null,null,null,null,null,"Schieberstellung 1 | 200 kg/h | Edelstahlgitter"]
[null,null,null,null,null,null,"q_Sek_Mittel [W/K]","q_Sek_Vorlauf [W/K]","Induktionsverhältnis [-]"]
[null,null,null,null,null,"a =",{"$f":"TRANSPOSE(LINEST(AI51:AI54,T51:T54^{0,1,2},0,0))","v":3.9343057050054116E-3},{"$f":"TRANSPOSE(LINEST(AJ51:AJ54,T51:T54^{0,1,2},0,0))","v":3.8297305496498928E-3},{"$f":"TRANSPOSE(LINEST(AG51:AG54,$T$51:$T$54^{0,1,2,3},0,0))","v":-0.44433788792732087}]
[null,null,null,null,null,"b =",-9.1661609787288253E-2,-8.8962954214271375E-2,29.171062311201627]
[null,null,null,null,null,"c =",5.198416832928288,5.1352425835046249,-592.41763188720461]
[null,null,null,null,null,"d =","-","-",3593.1243651376144]
[]
[null,null,null,null,null,null,"Schieberstellung 5 | 200 kg/h | lenkendes Alu-Lineargitter"]
[null,null,null,null,null,null,"q_Sek_Mittel [W/K]","q_Sek_Vorlauf [W/K]","Induktionsverhältnis [-]"]
[null,null,null,null,null,"a =",{"$f":"TRANSPOSE(LINEST(AI56:AI60,T56:T60^{0,1,2},0,0))","v":-1.0202405270923218E-3},{"$f":"TRANSPOSE(LINEST(AJ56:AJ60,U56:U60^{0,1,2},0,0))","v":35.389689730101246},{"$f":"TRANSPOSE(LINEST(AG56:AG60,$T$56:$T$60^{0,1,2,3},0,0))","v":5.4553272527921438E-7}]
[null,null,null,null,null,"b =",0.64845178895589473,-1742.5411209218121,-2.4586569363795123E-4]
[null,null,null,null,null,"c =",-16.588367742861905,21465.757934077898,3.7005667160096879E-2]
[null,null,null,null,null,"d =","-","-",-0.23003048344794774]

{"sheet":"Auswertung_Leistung","index":4,"n_rows":360,"n_cols":45,"rows_kept":360,"cut":false,"hidden":true,"merged":[]}
["Wassermengenvariation",null,null,null,"Abfrage",{"$f":"Auslegetool!AQ7","v":2},"Druck oder Volumenstrom",null,null,null,"Grenzewerte Primädruck"]
["HFBsf; HL; 4L; Schieberstellung 5; mit Edelstahlgitter",null,null,null,"Vorgabe   ==>",{"$f":"Q2","v":150},{"$f":"IF($F$1=1, \"m³/h\", \"Pa\")","v":"Pa"},{"$f":"IF($F$1=1, \"Primärvolumenstrom\", \"Primärdruck\")","v":"Primärdruck"},null,"min",45,null,null,null,null,null,150]
["Wassermenge kühlen",{"$f":"Auslegetool!J13","v":200},"kg/h",null,null,null,null,null,null,"max",305]
["Wassermenge heizen",{"$f":"Auslegetool!Q13","v":100},"kg/h"]
["Nennwassermenge",200,"kg/h"]
[null,null,null,null,null,null,"Wassermengenvariation 1",null,null,null,null,null,null,"Wassermengenvariation 2",null,null,null,null,null,null,"Wassermengenvariation 3"]
[null,null,null,null,null,null,null,1,5,20,6,11,37]
[null,null,null,null,null,null,{"$f":"CONCATENATE(\"Wassermassenstromvariation (bei Primädruck von \", ROUND(AVERAGE(I11:I14),0), \" Pa)\")","v":"Wassermassenstromvariation (bei Primädruck von 150 Pa)"},null,null,null,null,null,null,{"$f":"CONCATENATE(\"Wassermassenstromvariation (bei Primädruck von \", ROUND(AVERAGE(P11:P14),0), \" Pa)\")","v":"Wassermassenstromvariation (bei Primädruck von 150 Pa)"},null,null,null,null,null,null,{"$f":"CONCATENATE(\"Wassermassenstromvariation (bei Primädruck von \", ROUND(AVERAGE(W11:W14),0), \" Pa)\")","v":"Wassermassenstromvariation (bei Primädruck von 150 Pa)"}]
[null,null,null,null,null,null,"Messung","Messung","Primärdruck [Pa]","Primärvolumenstrom[m³/h]","Wasser-Massenstrom","spez. Kühlleistung","Druckverlust wassers.","Messung","Messung","Primärdruck [Pa]","Primärvolumenstrom[m³/h]","Wasser-Massenstrom","spez. Kühlleistung","Druckverlust wassers.","Messung","Messung","Primärdruck [Pa]","Primärvolumenstrom[m³/h]","Wasser-Massenstrom","spez. Kühlleistung","Druckverlust wassers."]
[null,null,null,null,null,null,null,null,"Pa","m³/h","kg/h","W/K","kPa",null,null,"Pa","m³/h","kg/h","W/K","kPa",null,null,"Pa","m³/h","kg/h","W/K","kPa"]
[null,null,null,null,null,null,"V7",{"$f":"VLOOKUP(G11,Matrix_Rohdaten,$H$7,0)","v":"V7"},{"$f":"VLOOKUP(G11,Matrix_Rohdaten,$I$7,0)","v":150},{"$f":"VLOOKUP(G11,Matrix_Rohdaten,$J$7,0)/$D$73*$D$77","v":89.635769935064857},{"$f":"VLOOKUP(G11,Matrix_Rohdaten,$K$7,0)","v":45.684768878787864},{"$f":"VLOOKUP(G11,Matrix_Rohdaten,$L$7,0)","v":25.970992651515147},{"$f":"VLOOKUP(G11,Matrix_Rohdaten,$M$7,0)","v":1.9},"V7",{"$f":"VLOOKUP(N11,Matrix_Rohdaten,$H$7,0)","v":"V7"},{"$f":"VLOOKUP(N11,Matrix_Rohdaten,$I$7,0)","v":150},{"$f":"VLOOKUP(N11,Matrix_Rohdaten,$J$7,0)/$D$73*$D$77","v":89.635769935064857},{"$f":"VLOOKUP(N11,Matrix_Rohdaten,$K$7,0)","v":45.684768878787864},{"$f":"VLOOKUP(N11,Matrix_Rohdaten,$L$7,0)","v":25.970992651515147},{"$f":"VLOOKUP(N11,Matrix_Rohdaten,$M$7,0)","v":1.9},"V7",{"$f":"VLOOKUP(U11,Matrix_Rohdaten,$H$7,0)","v":"V7"},{"$f":"VLOOKUP(U11,Matrix_Rohdaten,$I$7,0)","v":150},{"$f":"VLOOKUP(U11,Matrix_Rohdaten,$J$7,0)/$D$73*$D$77","v":89.635769935064857},{"$f":"VLOOKUP(U11,Matrix_Rohdaten,$K$7,0)","v":45.684768878787864},{"$f":"VLOOKUP(U11,Matrix_Rohdaten,$L$7,0)","v":25.970992651515147},{"$f":"VLOOKUP(U11,Matrix_Rohdaten,$M$7,0)","v":1.9}]
[null,null,null,null,null,null,"V8",{"$f":"VLOOKUP(G12,Matrix_Rohdaten,$H$7,0)","v":"V8"},{"$f":"VLOOKUP(G12,Matrix_Rohdaten,$I$7,0)","v":150},{"$f":"VLOOKUP(G12,Matrix_Rohdaten,$J$7,0)/$D$73*$D$77","v":89.574163571428514},{"$f":"VLOOKUP(G12,Matrix_Rohdaten,$K$7,0)","v":105.84956201515151},{"$f":"VLOOKUP(G12,Matrix_Rohdaten,$L$7,0)","v":38.535232666666651},{"$f":"VLOOKUP(G12,Matrix_Rohdaten,$M$7,0)","v":8.9},"V8",{"$f":"VLOOKUP(N12,Matrix_Rohdaten,$H$7,0)","v":"V8"},{"$f":"VLOOKUP(N12,Matrix_Rohdaten,$I$7,0)","v":150},{"$f":"VLOOKUP(N12,Matrix_Rohdaten,$J$7,0)/$D$73*$D$77","v":89.574163571428514},{"$f":"VLOOKUP(N12,Matrix_Rohdaten,$K$7,0)","v":105.84956201515151},{"$f":"VLOOKUP(N12,Matrix_Rohdaten,$L$7,0)","v":38.535232666666651},{"$f":"VLOOKUP(N12,Matrix_Rohdaten,$M$7,0)","v":8.9},"V8",{"$f":"VLOOKUP(U12,Matrix_Rohdaten,$H$7,0)","v":"V8"},{"$f":"VLOOKUP(U12,Matrix_Rohdaten,$I$7,0)","v":150},{"$f":"VLOOKUP(U12,Matrix_Rohdaten,$J$7,0)/$D$73*$D$77","v":89.574163571428514},{"$f":"VLOOKUP(U12,Matrix_Rohdaten,$K$7,0)","v":105.84956201515151},{"$f":"VLOOKUP(U12,Matrix_Rohdaten,$L$7,0)","v":38.535232666666651},{"$f":"VLOOKUP(U12,Matrix_Rohdaten,$M$7,0)","v":8.9}]
[null,null,null,null,null,null,"V10",{"$f":"VLOOKUP(G13,Matrix_Rohdaten,$H$7,0)","v":"V10"},{"$f":"VLOOKUP(G13,Matrix_Rohdaten,$I$7,0)","v":150},{"$f":"VLOOKUP(G13,Matrix_Rohdaten,$J$7,0)/$D$73*$D$77","v":89.574163571428514},{"$f":"VLOOKUP(G13,Matrix_Rohdaten,$K$7,0)","v":251.43574669696974},{"$f":"VLOOKUP(G13,Matrix_Rohdaten,$L$7,0)","v":48.19325851515152},{"$f":"VLOOKUP(G13,Matrix_Rohdaten,$M$7,0)","v":43},"V10",{"$f":"VLOOKUP(N13,Matrix_Rohdaten,$H$7,0)","v":"V10"},{"$f":"VLOOKUP(N13,Matrix_Rohdaten,$I$7,0)","v":150},{"$f":"VLOOKUP(N13,Matrix_Rohdaten,$J$7,0)/$D$73*$D$77","v":89.574163571428514},{"$f":"VLOOKUP(N13,Matrix_Rohdaten,$K$7,0)","v":251.43574669696974},{"$f":"VLOOKUP(N13,Matrix_Rohdaten,$L$7,0)","v":48.19325851515152},{"$f":"VLOOKUP(N13,Matrix_Rohdaten,$M$7,0)","v":43},"V10",{"$f":"VLOOKUP(U13,Matrix_Rohdaten,$H$7,0)","v":"V10"},{"$f":"VLOOKUP(U13,Matrix_Rohdaten,$I$7,0)","v":150},{"$f":"VLOOKUP(U13,Matrix_Rohdaten,$J$7,0)/$D$73*$D$77","v":89.574163571428514},{"$f":"VLOOKUP(U13,Matrix_Rohdaten,$K$7,0)","v":251.43574669696974},{"$f":"VLOOKUP(U13,Matrix_Rohdaten,$L$7,0)","v":48.19325851515152},{"$f":"VLOOKUP(U13,Matrix_Rohdaten,$M$7,0)","v":43}]
[null,null,null,null,null,null,"V11",{"$f":"VLOOKUP(G14,Matrix_Rohdaten,$H$7,0)","v":"V11"},{"$f":"VLOOKUP(G14,Matrix_Rohdaten,$I$7,0)","v":150},{"$f":"VLOOKUP(G14,Matrix_Rohdaten,$J$7,0)/$D$73*$D$77","v":89.574163571428514},{"$f":"VLOOKUP(G14,Matrix_Rohdaten,$K$7,0)","v":300.40299018181827},{"$f":"VLOOKUP(G14,Matrix_Rohdaten,$L$7,0)","v":49.565262651515148},{"$f":"VLOOKUP(G14,Matrix_Rohdaten,$M$7,0)","v":58.8},"V11",{"$f":"VLOOKUP(N14,Matrix_Rohdaten,$H$7,0)","v":"V11"},{"$f":"VLOOKUP(N14,Matrix_Rohdaten,$I$7,0)","v":150},{"$f":"VLOOKUP(N14,Matrix_Rohdaten,$J$7,0)/$D$73*$D$77","v":89.574163571428514},{"$f":"VLOOKUP(N14,Matrix_Rohdaten,$K$7,0)","v":300.40299018181827},{"$f":"VLOOKUP(N14,Matrix_Rohdaten,$L$7,0)","v":49.565262651515148},{"$f":"VLOOKUP(N14,Matrix_Rohdaten,$M$7,0)","v":58.8},"V11",{"$f":"VLOOKUP(U14,Matrix_Rohdaten,$H$7,0)","v":"V11"},{"$f":"VLOOKUP(U14,Matrix_Rohdaten,$I$7,0)","v":150},{"$f":"VLOOKUP(U14,Matrix_Rohdaten,$J$7,0)/$D$73*$D$77","v":89.574163571428514},{"$f":"VLOOKUP(U14,Matrix_Rohdaten,$K$7,0)","v":300.40299018181827},{"$f":"VLOOKUP(U14,Matrix_Rohdaten,$L$7,0)","v":49.565262651515148},{"$f":"VLOOKUP(U14,Matrix_Rohdaten,$M$7,0)","v":58.8}]
[]
[]
[null,null,null,null,null,null,"Wassermengenvariation",null,null,null,null,null,null,"Wassermengenvariation",null,null,null,null,null,null,"Wassermengenvariation"]
[null,null,null,null,null,null,{"$f":"CONCATENATE($A$2,\"; \", \"Primärdruck\", \" = \",L27, \" \", L26,\"; m_w=\", ROUND(G24,0), \" kg/h\")","v":"HFBsf; HL; 4L; Schieberstellung 5; mit Edelstahlgitter; Primärdruck = 150 Pa; m_w=200 kg/h"},null,null,null,null,null,null,{"$f":"CONCATENATE($A$2,\"; \", \"Primärdruck\", \" = \",S27, \" \", S26,\"; m_w=\", ROUND(N24,0), \" kg/h\")","v":"HFBsf; HL; 4L; Schieberstellung 5; mit Edelstahlgitter; Primärdruck = 150 Pa; m_w=200 kg/h"},null,null,null,null,null,null,{"$f":"CONCATENATE($A$2,\"; \", \"Primärdruck\", \" = \",Z27, \" \", Z26,\"; m_w=\", ROUND(U24,0), \" kg/h\")","v":"HFBsf; HL; 4L; Schieberstellung 5; mit Edelstahlgitter; Primärdruck = 150 Pa; m_w=200 kg/h"}]
[]
[null,null,null,null,null,null,"wok","spez. Leistung bei wok",null,null,"Druckverlust bei wok",null,null,"wok","spez. Leistung bei wok",null,null,"Druckverlust bei wok",null,null,"wok","spez. Leistung bei wok",null,null,"Druckverlust bei wok"]
[null,null,null,null,null,null,{"$f":"B5","v":200},{"$f":"G39*G21^G38+H39*G21^H38+I39*G21^I38+J39*G21^J38+K39","v":46.680898364205419},null,null,{"$f":"H$44*G21^I$44","v":28.201307810721179},null,null,{"$f":"G21","v":200},{"$f":"N39*N21^N38+O39*N21^O38+P39*N21^P38+Q39*N21^Q38+R39","v":46.680898364205419},null,null,{"$f":"O$44*N21^P$44","v":28.201307810721179},null,null,{"$f":"G21","v":200},{"$f":"U39*U21^U38+V39*U21^V38+W39*U21^W38+X39*U21^X38+Y39","v":46.680898364205419},null,null,{"$f":"V$44*U21^W$44","v":28.201307810721179}]
[]
[null,null,null,null,null,null,"w_soll",null,null,null,null,null,null,"w_soll",null,null,null,null,null,null,"w_soll"]
[null,null,null,null,null,null,{"$f":"B3","v":200},null,{"$f":"G24/G21","v":1},{"$f":"G$51*I24^G$50+H$51*I24^H$50+I$51*I24^I$50+J$51*I24^J$50+K$51","v":1.0000000000000004},{"$f":"H$44*G24^I$44","v":28.201307810721179},null,null,{"$f":"B3","v":200},null,{"$f":"N24/N21","v":1},{"$f":"N$51*P24^N$50+O$51*P24^O$50+P$51*P24^P$50+Q$51*P24^Q$50+R$51","v":1.0000000000000004},{"$f":"O$44*N24^P$44","v":28.201307810721179},null,null,{"$f":"B3","v":200},null,{"$f":"U24/U21","v":1},{"$f":"U$51*W24^U$50+V$51*W24^V$50+W$51*W24^W$50+X$51*W24^X$50+Y$51","v":1.0000000000000004},{"$f":"V$44*U24^W$44","v":28.201307810721179}]
[null,null,null,null,null,null,"Wassermenge","spez. Leistung","Faktor: Wassermenge zu Nennwassermenge ","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok","wasserseit. Druckverlust - kühlen","Primärdruck [Pa]","Primärvolumenstrom[m³/h]","Wassermenge","spez. Leistung","Faktor: Wassermenge zu Nennwassermenge ","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok","wasserseit. Druckverlust - kühlen","Primärdruck [Pa]","Primärvolumenstrom[m³/h]","Wassermenge","spez. Leistung","Faktor: Wassermenge zu Nennwassermenge ","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok","wasserseit. Druckverlust - kühlen","Primärdruck [Pa]","Primärvolumenstrom[m³/h]"]
[null,null,null,null,null,null,"[kg/h]","[W/K]","[-]","[-]","[kPa]","Pa","m³/h","[kg/h]","[W/K]","[-]","[-]","[kPa]","Pa","m³/h","[kg/h]","[W/K]","[-]","[-]","[kPa]","Pa","m³/h"]
[null,null,null,null,null,null,{"$f":"K11","v":45.684768878787864},{"$f":"L11","v":25.970992651515147},{"$f":"G27/G$21","v":0.22842384439393931},0.5563516033665179,{"$f":"M11","v":1.9},{"$f":"I11","v":150},{"$f":"J11","v":89.635769935064857},{"$f":"R11","v":45.684768878787864},25.970992651515147,{"$f":"N27/N$21","v":0.22842384439393931},0.5563516033665179,{"$f":"T11","v":1.9},{"$f":"P11","v":150},{"$f":"Q11","v":89.635769935064857},{"$f":"Y11","v":45.684768878787864},25.970992651515147,{"$f":"U27/U$21","v":0.22842384439393931},0.5563516033665179,{"$f":"AA11","v":1.9},{"$f":"W11","v":150},{"$f":"X11","v":89.635769935064857}]
[null,null,null,null,null,null,105.84956201515151,38.535232666666651,0.5292478100757575,0.82550323616340671,{"$f":"M12","v":8.9},{"$f":"I12","v":150},{"$f":"J12","v":89.574163571428514},105.84956201515151,38.535232666666651,0.5292478100757575,0.82550323616340671,{"$f":"T12","v":8.9},{"$f":"P12","v":150},{"$f":"Q12","v":89.574163571428514},105.84956201515151,38.535232666666651,0.5292478100757575,0.82550323616340671,{"$f":"AA12","v":8.9},{"$f":"W12","v":150},89.574163571428514]
[null,null,null,null,null,null,251.43574669696974,48.19325851515152,1.2571787334848488,1.0323978373155254,{"$f":"M13","v":43},{"$f":"I13","v":150},{"$f":"J13","v":89.574163571428514},251.43574669696974,48.19325851515152,{"$f":"N29/N$21","v":1.2571787334848488},{"$f":"O29/O$21","v":1.0323978373155254},{"$f":"T13","v":43},{"$f":"P13","v":150},89.574163571428514,251.43574669696974,48.19325851515152,1.2571787334848488,1.0323978373155254,{"$f":"AA13","v":43},{"$f":"W13","v":150},89.574163571428514]
[null,null,null,null,null,null,300.40299018181827,49.565262651515148,1.5020149509090914,1.0617889626888894,{"$f":"M14","v":58.8},{"$f":"I14","v":150},89.574163571428514,300.40299018181827,49.565262651515148,1.5020149509090914,1.0617889626888894,{"$f":"T14","v":58.8},{"$f":"P14","v":150},89.574163571428514,300.40299018181827,49.565262651515148,1.5020149509090914,1.0617889626888894,{"$f":"AA14","v":58.8},{"$f":"W14","v":150},89.574163571428514]
[]
[]
[null,null,null,null,null,null,"y = qk\nx = wk",null,null,null,null,null,null,"y = qk\nx = wk",null,null,null,null,null,null,"y = qk\nx = wk"]
[]
[null,null,null,null,null,null,"y =","axn+bx(n-1)+...+nx+m",null,null,null,null,null,"y =","axn+bx(n-1)+...+nx+m",null,null,null,null,null,"y =","axn+bx(n-1)+...+nx+m"]
[null,null,null,null,null,null,"Polynom",{"$f":"G38","v":3},"Ordnung",null,null,null,null,"Polynom",750,"Ordnung",null,null,null,null,"Polynom",{"$f":"U38","v":3},"Ordnung"]
[null,null,null,null,null,null,"a =","b =","c =","m =",null,null,null,"a =",750,"c =","m =",null,null,null,"a =","b =","c =","m ="]
[null,null,null,null,null,null,3,2,1,0,null,null,null,3,2,1,0,null,null,null,3,2,1,0]
[null,null,null,null,null,null,{"$f":"LINEST(H27:H30,G27:G30^{0,1,2,3},0,0)","v":1.945598709151086E-6},-1.476561779207728E-3,0.39731248542365366,10.716082774575124,null,null,null,{"$f":"LINEST(O27:O30,N27:N30^{0,1,2,3},0,0)","v":1.945598709151086E-6},-1.476561779207728E-3,0.39731248542365366,10.716082774575124,null,null,null,{"$f":"LINEST(V27:V30,U27:U30^{0,1,2,3},0,0)","v":1.945598709151086E-6},-1.476561779207728E-3,0.39731248542365366,10.716082774575124]
[null,null,null,null,null,null,"y = Druck dp [kPa] \nx = Wasserm. wk",null,null,null,null,null,null,"y = Druck dp [kPa] \nx = Wasserm. wk",null,null,null,null,null,null,"y = Druck dp [kPa] \nx = Wasserm. wk"]
[]
[null,null,null,null,null,null,"y =","mxb",null,null,null,null,null,"y =","mxb",null,null,null,null,null,"y =","mxb"]
[null,null,null,null,null,null,null,"m","b","R2",null,null,null,null,"m","b","R2",null,null,null,null,"m","b","R2"]
[null,null,null,null,null,null,null,{"$f":"INDEX(LOGEST(K27:K30,LN(G27:G30),,TRUE),1,2)","v":1.7922773591199607E-3},{"$f":"LN(INDEX(LOGEST(K27:K30,LN(G27:G30),,TRUE),1,1))","v":1.8239067018257689},{"$f":"INDEX(LOGEST(K27:K30,LN(G27:G30),,TRUE),3,1)","v":0.99998094898325074},null,null,null,null,{"$f":"INDEX(LOGEST(R27:R30,LN(N27:N30),,TRUE),1,2)","v":1.7922773591199607E-3},{"$f":"LN(INDEX(LOGEST(R27:R30,LN(N27:N30),,TRUE),1,1))","v":1.8239067018257689},{"$f":"INDEX(LOGEST(R27:R30,LN(N27:N30),,TRUE),3,1)","v":0.99998094898325074},null,null,null,null,{"$f":"INDEX(LOGEST(Y27:Y30,LN(U27:U30),,TRUE),1,2)","v":1.7922773591199607E-3},{"$f":"LN(INDEX(LOGEST(Y27:Y30,LN(U27:U30),,TRUE),1,1))","v":1.8239067018257689},{"$f":"INDEX(LOGEST(Y27:Y30,LN(U27:U30),,TRUE),3,1)","v":0.99998094898325074}]
[null,null,null,null,null,null,"y = qk in %\nx = wk in %",null,null,null,null,null,null,"y = qk in %\nx = wk in %",null,null,null,null,null,null,"y = qk in %\nx = wk in %"]
[]
[null,null,null,null,null,null,"y =","axn+bx(n-1)+...+nx+m",null,null,null,null,null,"y =","axn+bx(n-1)+...+nx+m",null,null,null,null,null,"y =","axn+bx(n-1)+...+nx+m"]
[null,null,null,null,null,null,"Polynom",{"$f":"G50","v":3},"Ordnung",null,null,null,null,"Polynom",{"$f":"N50","v":3},"Ordnung",null,null,null,null,"Polynom",{"$f":"U50","v":3},"Ordnung"]
[null,null,null,null,null,null,"a =","b =","c =","m =",null,null,null,"a =","b =","c =","m =",null,null,null,"a =","b =","c =","m ="]
[null,null,null,null,null,null,3,2,1,0,null,null,null,3,2,1,0,null,null,null,3,2,1,0]
[null,null,null,null,null,null,{"$f":"LINEST(J27:J30,I27:I30^{0,1,2,3},0,0)","v":0.33342952296615669},-1.2652385287768517,1.7022486684973894,0.22956033731330613,null,null,null,{"$f":"LINEST(Q27:Q30,P27:P30^{0,1,2,3},0,0)","v":0.33342952296615669},-1.2652385287768517,1.7022486684973894,0.22956033731330613,null,null,null,{"$f":"LINEST(X27:X30,W27:W30^{0,1,2,3},0,0)","v":0.33342952296615669},-1.2652385287768517,1.7022486684973894,0.22956033731330613]
[]
[]
[]
[]
["Basisdaten - Leistung",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Wird nicht verwendet"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,"Einheiten"]
["Primärvolumenstrom",{"$f":"F2","v":150},"m³/h",null,null,null,null,null,null,null,null,null,null,null,null,1.5,null,1,"Primärvolumenstrom","[m³/h]"]
["Primärdruck",{"$f":"F2","v":150},"Pa",null,null,null,null,null,null,null,null,null,null,null,null,2,null,2,"Primärdruck","[Pa]"]
[null,null,null,null,null,null,null,null,null,"CER/Ei; 23.03.2023",null,null,null,null,null,2.5,null,{"$f":"F1","v":2},{"$f":"IF($F$1=1,S58,S59)","v":"Primärdruck"},{"$f":"IF($F$1=1,T58,T59)","v":"[Pa]"},null,"Polynom    y =","axn+bx(n-1)+...+nx+m","Ordnung"]
["Datenübergabe AUS WASSERMENGENVARIATION",null,null,null,null,null,null,null,null,"Anpassungen von HFBsf-HL (Adidas) zu HFBsf:",null,null,null,null,null,3,null,{"$f":"IF(F1=1,2,1)","v":1},{"$f":"IF($F$1=2,S58,S59)","v":"Primärvolumenstrom"},{"$f":"IF($F$1=2,T58,T59)","v":"[m³/h]"},null,"a =","b =","m ="]
["Wassermenge kühlen",{"$f":"B3","v":200},"kg/h",null,null,null,null,null,null,"statt 3x25 Düsen sind 2x25 Düsen vorhanden",null,null,null,null,null,3.5,null,null,null,null,null,2,1,0]
["Wassermenge heizen",{"$f":"B4","v":100},"kg/h",null,null,null,null,null,null,"Primärluftvolumenstrom wurde dasher um den Faktor (z.B. 50/70) angepasst",null,null,null,null,null,4,null,null,null,null,null,{"$f":"LINEST(N73:N76,H73:H76^{0,1,2},0,0)","v":0},0,0]
["Nennwassermenge",{"$f":"B5","v":200},"kg/h",null,null,null,null,null,null,"Geringe Abweichungen der latentan Leistung sind durch deutlich geringere Sekundärluftsolumenströme zu erklären",null,null,null,null,null,4.5,null,null,null,null,null,"Abweichung Auslegung 1",{"$f":"V63*R74^V62+W63*R74^W62+X63*R74^X62","v":0},{"$f":"IF(W64>=0, CONCATENATE(\"+\", ROUND(AVERAGE(W64)*100,0), \" % Kühlleistung bei \", ROUND($B$62,0), \" kg/h\"),CONCATENATE(ROUND(AVERAGE(W64)*100,0), \" % Kühlleistung bei \", ROUND($B$62,0), \" kg/h\"))","v":"+0 % Kühlleistung bei 200 kg/h"}]
["Polynom Wassermenge",{"$f":"G50","v":3},2,1,0,0,"Primärdruck","Primärvolumenstrom",null,"WÜT sind identisch (VKB) und haben dieselbe Breite, daher sind Kühlleistungen ebenfalls identisch; durch Messungen verifiziert.",null,null,null,null,null,5,null,null,null,null,null,"Abweichung Auslegung 2",{"$f":"V63*T76^V62+W63*T76^W62+X63*T76^X62","v":0},{"$f":"IF(W65>=0, CONCATENATE(\"+\", ROUND(AVERAGE(W65)*100,0), \" % Kühlleistung bei \", ROUND($B$62,0), \" kg/h\"),CONCATENATE(ROUND(AVERAGE(W65)*100,0), \" % Kühlleistung bei \", ROUND($B$62,0), \" kg/h\"))","v":"+0 % Kühlleistung bei 200 kg/h"}]
["Wassermengenvar. 1",0.33342952296615669,-1.2652385287768517,1.7022486684973894,0.22956033731330613,0,{"$f":"$L$27","v":150},{"$f":"AVERAGE($M$27:$M$30)","v":89.589565162337607}]
["Wassermengenvar. 2",{"$f":"N51","v":0.33342952296615669},{"$f":"O51","v":-1.2652385287768517},{"$f":"P51","v":1.7022486684973894},{"$f":"Q51","v":0.22956033731330613},{"$f":"R51","v":0},{"$f":"IFERROR(IF($S$27=0,G66,$S$27),G66)","v":150},{"$f":"IFERROR(IF($T$27=0,H66,$T$27),H66)","v":89.635769935064857}]
["Wassermengenvar. 3",{"$f":"U51","v":0.33342952296615669},{"$f":"V51","v":-1.2652385287768517},{"$f":"W51","v":1.7022486684973894},{"$f":"X51","v":0.22956033731330613},{"$f":"Y51","v":0},{"$f":"IFERROR(IF($Z$27=0,G66,$Z$27),G66)","v":150},{"$f":"IFERROR(IF($AA$27=0,H66,$AA$27),H66)","v":89.635769935064857}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Heizen"]
["HFBsf; HL; 4L; mit Edelstahlgitter",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,20]
[null,1,3,4,6,5,11,20,33,null,null,null,null,null,null,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29]
["Messreihe 1","Messung (Kontrolle)","Schieberstellung","Anzahl Düsen","Wasser-\nmenge [kg/h]","Primärdruck [Pa]","spez. Kühlleistung q Sek [W/K]","Primärvolumenstrom [m³/h]","Induktionsverhältnis i [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok",{"$f":"CONCATENATE(\"q Sek [W/K] bei wok \", $B$64, \" kg/h\")","v":"q Sek [W/K] bei wok 200 kg/h"},{"$f":"CONCATENATE(\"Korrektur bei \", ROUND(AVERAGE($B$62),0), \" kg/h (Mittelwert)\")","v":"Korrektur bei 200 kg/h (Mittelwert)"},{"$f":"CONCATENATE(\"q Sek [W/K] bei w_soll \", ROUND($B$62,0), \" kg/h\")","v":"q Sek [W/K] bei w_soll 200 kg/h"},{"$f":"CONCATENATE(\"q Sek Abweichung von Nennwassermenge bei \", $B$62, \" kg/h\")","v":"q Sek Abweichung von Nennwassermenge bei 200 kg/h"},"Sekundärvolumenstrom [m³/h]",null,null,"x - Achse","y - Achse","y - Achse","y - Achse",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Primärvolumenstrom [m³/h]",{"$f":"K72","v":"q Sek [W/K] bei wok 200 kg/h"},{"$f":"CONCATENATE(\"Korrektur bei \", ROUND(AVERAGE($B$63),0), \" kg/h (Mittelwert)\")","v":"Korrektur bei 100 kg/h (Mittelwert)"},{"$f":"CONCATENATE(\"q Sek [W/K] bei w_soll \", ROUND($B$63,0), \" kg/h\")","v":"q Sek [W/K] bei w_soll 100 kg/h"},"Korrektur kühlen heizen bei \ngleichem Wärmetauscher"]
["V2",{"$f":"VLOOKUP(A73,Matrix_Rohdaten,$B$71,0)","v":"V2"},{"$f":"VLOOKUP(A73,Matrix_Rohdaten,$C$71,0)","v":5},{"$f":"VLOOKUP(A73,Matrix_Rohdaten,$D$71,0)","v":70},{"$f":"VLOOKUP(A73,Matrix_Rohdaten,$E$71,0)","v":201.9774836212122},{"$f":"VLOOKUP(A73,Matrix_Rohdaten,$F$71,0)","v":50},{"$f":"VLOOKUP(A73,Matrix_Rohdaten,$G$71,0)","v":23.032627500000011},{"$f":"VLOOKUP(A73,Matrix_Rohdaten,$H$71,0)/D73*D$77","v":52.394749999999931},{"$f":"VLOOKUP(A73,Matrix_Rohdaten,$I$71,0)/$D$77*D73","v":1.6481957481102874},{"$f":"IF(G78=G79,G78,E83*H73^E82+F83*H73^F82+G83*H73^G82)","v":1.0010952303531182},{"$f":"G73/J73","v":23.007429065340435},{"$f":"IF(L78=L79,L78,J83*H73^J82+K83*H73^K82+L83*H73^L82)","v":1.0000000000000004},{"$f":"K73*L73","v":23.007429065340446},{"$f":"1/K73*M73-1","v":0},{"$f":"I73*H73","v":86.35680417330137},{"$f":"CONCATENATE(A72,\": Auslegung1\")","v":"Messreihe 1: Auslegung1"},1,"V_Prim soll [m³/h]","q sek [W/K] Auslegung 1","Primärdruck [Pa]","Induktionsverhältnis","Titel für Diagramme:",null,null,null,null,null,null,null,null,null,"Akustikmessung:",null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A73,Matrix_Rohdaten,$AO$70,0)/$D$76*$D$77","v":52.394749999999931},{"$f":"K73","v":23.007429065340435},{"$f":"IF(AQ78=AQ79,AQ78,AO83*AO73^AO82+AP83*AO73^AP82+AQ83*AO73^AQ82)","v":0.80605372973855749},{"$f":"AP73*AQ73","v":18.545224009812951},{"$f":"1/M73*AR73","v":0.80605372973855716}]
["V4",{"$f":"VLOOKUP(A74,Matrix_Rohdaten,$B$71,0)","v":"V4"},{"$f":"VLOOKUP(A74,Matrix_Rohdaten,$C$71,0)","v":5},{"$f":"VLOOKUP(A74,Matrix_Rohdaten,$D$71,0)","v":70},{"$f":"VLOOKUP(A74,Matrix_Rohdaten,$E$71,0)","v":202.22353931343281},{"$f":"VLOOKUP(A74,Matrix_Rohdaten,$F$71,0)","v":150},{"$f":"VLOOKUP(A74,Matrix_Rohdaten,$G$71,0)","v":45.27565994029851},{"$f":"VLOOKUP(A74,Matrix_Rohdaten,$H$71,0)/D74*D$77","v":90.434712857142785},{"$f":"VLOOKUP(A74,Matrix_Rohdaten,$I$71,0)/$D$77*D74","v":2.1486693439533813},{"$f":"IF(G78=G79,G78,E83*H74^E82+F83*H74^F82+G83*H74^G82)","v":1.0010952303531182},{"$f":"G74/J74","v":45.226126913349034},{"$f":"IF(L78=L79,L78,J83*H74^J82+K83*H74^K82+L83*H74^L82)","v":1.0000000000000004},{"$f":"K74*L74","v":45.226126913349056},{"$f":"1/K74*M74-1","v":0},{"$f":"I74*H74","v":194.31429514536941},null,1,91,{"$f":"R80*R74^R79+S80*R74^S79+T80*R74^T79+U80*R74^U79","v":45.432001797413804},{"$f":"V80*R74^W80","v":153.02115681133563},{"$f":"X80*R74^X79+Y80*R74^Y79+Z80*R74^Z79","v":2.1707391992880449},{"$f":"CONCATENATE($A$70, \" ; \",K72)","v":"HFBsf; HL; 4L; mit Edelstahlgitter ; q Sek [W/K] bei wok 200 kg/h"},null,null,null,null,null,null,null,null,null,"\\\\file\\Daten\\M\\r\\PM\\Luft-Wasser-Systeme\\Induktion\\HFBsf\\Messungen\\Akustik\\HFBsf_Akustik_1mm_Schieber_HFI.xlsx",null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A74,Matrix_Rohdaten,$AO$70,0)/$D$76*$D$77","v":90.434712857142785},{"$f":"K74","v":45.226126913349034},{"$f":"IF(AQ78=AQ79,AQ78,AO83*AO74^AO82+AP83*AO74^AP82+AQ83*AO74^AQ82)","v":0.80605372973855749},{"$f":"AP74*AQ74","v":36.454688280134341},{"$f":"1/M74*AR74","v":0.80605372973855705}]
["V5",{"$f":"VLOOKUP(A75,Matrix_Rohdaten,$B$71,0)","v":"V5"},{"$f":"VLOOKUP(A75,Matrix_Rohdaten,$C$71,0)","v":5},{"$f":"VLOOKUP(A75,Matrix_Rohdaten,$D$71,0)","v":70},{"$f":"VLOOKUP(A75,Matrix_Rohdaten,$E$71,0)","v":200.38356357575756},{"$f":"VLOOKUP(A75,Matrix_Rohdaten,$F$71,0)","v":250},{"$f":"VLOOKUP(A75,Matrix_Rohdaten,$G$71,0)","v":56.400179757575764},{"$f":"VLOOKUP(A75,Matrix_Rohdaten,$H$71,0)/D75*D$77","v":115.50865428571433},{"$f":"VLOOKUP(A75,Matrix_Rohdaten,$I$71,0)/$D$77*D75","v":2.3796081966308238},{"$f":"IF(G78=G79,G78,E83*H75^E82+F83*H75^F82+G83*H75^G82)","v":1.0010952303531182},{"$f":"G75/J75","v":56.338476148449558},{"$f":"IF(L78=L79,L78,J83*H75^J82+K83*H75^K82+L83*H75^L82)","v":1.0000000000000004},{"$f":"K75*L75","v":56.338476148449587},{"$f":"1/K75*M75-1","v":0},{"$f":"I75*H75","v":274.86534052008193},{"$f":"CONCATENATE(A72,\": Auslegung2\")","v":"Messreihe 1: Auslegung2"},2,"Primärdruck Soll [Pa]","q sek [W/K] Auslegung 2","V_Prim soll [m³/h] Auslegung 2","Induktionsverhältnis",{"$f":"CONCATENATE($A$70, \" ; \",M72)","v":"HFBsf; HL; 4L; mit Edelstahlgitter ; q Sek [W/K] bei w_soll 200 kg/h"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A75,Matrix_Rohdaten,$AO$70,0)/$D$76*$D$77","v":115.50865428571433},{"$f":"K75","v":56.338476148449558},{"$f":"IF(AQ78=AQ79,AQ78,AO83*AO75^AO82+AP83*AO75^AP82+AQ83*AO75^AQ82)","v":0.80605372973855749},{"$f":"AP75*AQ75","v":45.41183882724453},{"$f":"1/M75*AR75","v":0.80605372973855705}]
["V6",{"$f":"VLOOKUP(A76,Matrix_Rohdaten,$B$71,0)","v":"V6"},{"$f":"VLOOKUP(A76,Matrix_Rohdaten,$C$71,0)","v":5},{"$f":"VLOOKUP(A76,Matrix_Rohdaten,$D$71,0)","v":70},{"$f":"VLOOKUP(A76,Matrix_Rohdaten,$E$71,0)","v":200.55822357575755},{"$f":"VLOOKUP(A76,Matrix_Rohdaten,$F$71,0)","v":300},{"$f":"VLOOKUP(A76,Matrix_Rohdaten,$G$71,0)","v":59.971489545454546},{"$f":"VLOOKUP(A76,Matrix_Rohdaten,$H$71,0)/D76*D$77","v":126.88330285714298},{"$f":"VLOOKUP(A76,Matrix_Rohdaten,$I$71,0)/$D$77*D76","v":2.3697128927795927},{"$f":"IF(G78=G79,G78,E83*H76^E82+F83*H76^F82+G83*H76^G82)","v":1.0010952303531182},{"$f":"G76/J76","v":59.905878808653085},{"$f":"IF(L78=L79,L78,J83*H76^J82+K83*H76^K82+L83*H76^L82)","v":1.0000000000000004},{"$f":"K76*L76","v":59.905878808653114},{"$f":"1/K76*M76-1","v":0},300.67699865902944,null,2,77.3,{"$f":"R83*R76^R82+S83*R76^S82+T83*R76^T82+U83*R76^U82","v":31.106884466873126},{"$f":"V83*R76^W83","v":65.005381588255773},{"$f":"X83*R76^X82+Y83*R76^Y82+Z83*R76^Z82","v":1.8136815625545948},{"$f":"CONCATENATE(\"im Mittel \", ROUND(AVERAGE(N73:N76)*100,0), \" % Kühlleistung bei \", ROUND($B$62,0), \" kg/h\")","v":"im Mittel 0 % Kühlleistung bei 200 kg/h"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A76,Matrix_Rohdaten,$AO$70,0)/$D$76*$D$77","v":126.88330285714298},{"$f":"K76","v":59.905878808653085},{"$f":"IF(AQ78=AQ79,AQ78,AO83*AO76^AO82+AP83*AO76^AP82+AQ83*AO76^AQ82)","v":0.80605372973855749},{"$f":"AP76*AQ76","v":48.28735704698083},{"$f":"1/M76*AR76","v":0.80605372973855705}]
[null,null,"Düsenanzahl HFBsf-Standard (2x25 Düsen je 6,8mm)",{"$f":"25+25","v":50},{"$f":"CONCATENATE(\"w_mess = \", ROUND(E78,0),\" kg/h\")","v":"w_mess = 201 kg/h"},"Faktor: Wassermenge zu Nennwassermenge [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa] bei Wassermengenvariation (muss identisch sein)","Primärvolumenstrom Wassermengenvariation [m³/h]",{"$f":"CONCATENATE(\"w_soll = \", ROUND($B$62,0),\" kg/h\")","v":"w_soll = 200 kg/h"},"Faktor: Wassermenge zu Nennwassermenge  [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa]","Primärvolumenstrom[m³/h]",null,null,null,"Polynom  y =","axn+bx(n-1)+...+nx+m",null,null,"Umrechnung: Druck D Volumenstrom",null,"y =","axn+bx(n-1)+...+nx+m",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"CONCATENATE(\"w_soll = \", ROUND($B$63,0),\" kg/h\")","v":"w_soll = 100 kg/h"},"Faktor: Wassermenge zu Nennwassermenge  [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa]","Primärvolumenstrom[m³/h]"]
[null,null,null,null,{"$f":"AVERAGE(E73:E76)","v":201.28570252154003},{"$f":"E78/$B$64","v":1.0064285126077002},{"$f":"$B$66*F78^$B$65+$C$66*F78^$C$65+$D$66*F78^$D$65+$E$66*F78^$E$65+$F$66","v":1.0010952303531182},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607},{"$f":"$B$62","v":200},{"$f":"J78/$B$64","v":1},{"$f":"$B$66*K78^$B$65+$C$66*K78^$C$65+$D$66*K78^$D$65+$E$66*K78^$E$65+$F$66","v":1.0000000000000004},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607},null,null,null,"a =","b =","c =","m =","y =","mxb","a =","b =","m =",null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO78/$B$64","v":0.5},{"$f":"$B$66*AP78^$B$65+$C$66*AP78^$C$65+$D$66*AP78^$D$65+$E$66*AP78^$E$65+$F$66","v":0.80605372973855749},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607}]
[null,null,null,null,{"$f":"AVERAGE(E73:E76)","v":201.28570252154003},{"$f":"E79/$B$64","v":1.0064285126077002},{"$f":"IFERROR($B$67*F79^$B$65+$C$67*F79^$C$65+$D$67*F79^$D$65+$E$67*F79^$E$65+$F$67,G78)","v":1.0010952303531182},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857},{"$f":"$B$62","v":200},{"$f":"J79/$B$64","v":1},{"$f":"IFERROR($B$67*K79^$B$65+$C$67*K79^$C$65+$D$67*K79^$D$65+$E$67*K79^$E$65+$F$67,L78)","v":1.0000000000000004},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857},null,null,1,3,2,1,0,null,null,2,1,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO79/$B$64","v":0.5},{"$f":"IFERROR($B$67*AP79^$B$65+$C$67*AP79^$C$65+$D$67*AP79^$D$65+$E$67*AP79^$E$65+$F$67,AQ78)","v":0.80605372973855749},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857}]
[null,null,null,null,{"$f":"AVERAGE(E73:E76)","v":201.28570252154003},{"$f":"E80/$B$64","v":1.0064285126077002},{"$f":"IFERROR($B$68*F80^$B$65+$C$68*F80^$C$65+$D$68*F80^$D$65+$E$68*F80^$E$65+$F$68,G78)","v":1.0010952303531182},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857},{"$f":"$B$62","v":200},{"$f":"J80/$B$64","v":1},{"$f":"IFERROR($B$68*K80^$B$65+$C$68*K80^$C$65+$D$68*K80^$D$65+$E$68*K80^$E$65+$F$68,L78)","v":1.0000000000000004},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857},null,null,1,{"$f":"LINEST(M73:M76,H73:H76^{1,2,3},0,0)","v":-3.107116330477844E-5},5.9974316586378909E-3,0.21078678939536949,0,{"$f":"INDEX(LOGEST(Auswertung_Leistung!F73:F76,LN(Auswertung_Leistung!H73:H76),,TRUE),1,2)","v":1.6145364844895434E-2},{"$f":"LN(INDEX(LOGEST(F73:F76,LN(H73:H76),,TRUE),1,1))","v":2.0299232231534488},{"$f":"LINEST(I73:I76,$H$73:$H$76^{0,1,2},0,0)","v":-1.0141969342352791E-4},2.8161953993566118E-2,0.44785786711376258,null,null,"Für Vergleich mit \"ohne Schieber\"",null,null,"Akustik",null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO80/$B$64","v":0.5},{"$f":"IFERROR($B$68*AP80^$B$65+$C$68*AP80^$C$65+$D$68*AP80^$D$65+$E$68*AP80^$E$65+$F$68,AQ78)","v":0.80605372973855749},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857}]
[null,null,null,null,"a =","b =","m =",null,null,"a =","b =","m =",null,"Korrektur\nWassermenge",null,null,null,"a =","b =","c =","m =","y =","mxb","a =","b =","m =",null,null,null,null,null,"Druckverlust [Pa] → \nSchallleistung [dBA]",null,null,null,null,null,null,null,null,"a =","b =","m ="]
[null,null,null,null,2,1,0,null,null,2,1,0,"Auslegung 1",{"$f":"J83*R74^2+K83*R74+L83","v":0.99976039169835085},null,null,2,3,2,1,0,null,null,2,1,0,null,null,"Umrechnung: Druck _Volumenstrom",null,null,null,null,null,null,null,null,null,null,null,2,1,0]
[null,null,null,null,{"$f":"LINEST(G78:G80,I78:I80^{0,1,2},0,0)","v":-1.2466272339124268E-4},2.2342718373934724E-2,0,null,null,{"$f":"LINEST(L78:L80,N78:N80^{0,1,2},0,0)","v":-1.245263383656661E-4},2.2318274722026722E-2,0,"Auslegung 2",{"$f":"J83*T76^2+K83*T76+L83","v":0.92459706206305148},null,null,2,{"$f":"LINEST(M73:M76,F73:F76^{1,2,3},0,0)","v":2.7277708636672305E-6},-1.9347347828079372E-3,0.53567342832371656,0,{"$f":"INDEX(LOGEST(Auswertung_Leistung!H73:H76,LN(Auswertung_Leistung!F73:F76),,TRUE),1,2)","v":7.6353163888134548},{"$f":"LN(INDEX(LOGEST(H73:H76,LN(F73:F76),,TRUE),1,1))","v":0.49260267740287489},{"$f":"LINEST(I73:I76,$F$73:$F$76^{0,1,2},0,0)","v":-1.440436495437062E-5},7.9490782195637162E-3,1.2852880740505208,null,null,"y =","mxb",null,"m","b",null,null,null,null,null,null,null,{"$f":"LINEST(AQ78:AQ80,AS78:AS80^{0,1,2},0,0)","v":-1.0037491949032032E-4},1.7989728581018466E-2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"CONCATENATE(\"H\",P85)","v":"H5"},{"$f":"$F$1","v":2},{"$f":"R82","v":3},2,1,0,null,null,{"$f":"X82","v":2},{"$f":"Y82","v":1},0,"V_Prim Min [m³/h]","V_Prim Max [m³/h]",null,null,null,"y = m∙LN(x) + b",null,null,null,null,null,null,null,null,"Korrekturfaktor Mittel"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"C73","v":5},{"$f":"$F$1","v":2},{"$f":"R83","v":2.7277708636672305E-6},{"$f":"S83","v":-1.9347347828079372E-3},0.53567342832371656,0,{"$f":"IF(Q85=1,V80,V83)","v":7.6353163888134548},{"$f":"IF(Q85=1,W80,W83)","v":0.49260267740287489},{"$f":"X83","v":-1.440436495437062E-5},{"$f":"Y83","v":7.9490782195637162E-3},1.2852880740505208,{"$f":"V83*$K$2^W83","v":49.797088153619242},{"$f":"V83*$K$3^W83","v":127.82028754345181},{"$f":"V80","v":1.6145364844895434E-2},{"$f":"W80","v":2.0299232231534488},"Schieberstellung 5",15.4620222900769,-44.279912998433083,null,null,null,null,null,null,null,{"$f":"AVERAGE(AS73:AS76)","v":0.80605372973855705}]
[]
["Messreihe 2","Messung (Kontrolle)","Schieberstellung","Anzahl Düsen","Wasser-\nmenge [kg/h]","Primärdruck [Pa]","spez. Kühlleistung q Sek [W/K]","Primärvolumenstrom [m³/h]","Induktionsverhältnis i [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok",{"$f":"CONCATENATE(\"q Sek [W/K] bei wok \", G$21, \" kg/h\")","v":"q Sek [W/K] bei wok 200 kg/h"},{"$f":"CONCATENATE(\"Korrektur bei \", ROUND(AVERAGE($B$62),0), \" kg/h (Mittelwert)\")","v":"Korrektur bei 200 kg/h (Mittelwert)"},{"$f":"CONCATENATE(\"q Sek [W/K] bei w_soll \", ROUND($B$62,0), \" kg/h\")","v":"q Sek [W/K] bei w_soll 200 kg/h"},{"$f":"CONCATENATE(\"q Sek Abweichung von Nennwassermenge bei \", $B$62, \" kg/h\")","v":"q Sek Abweichung von Nennwassermenge bei 200 kg/h"},"Sekundärvolumenstrom [m³/h]",null,null,"x - Achse","y - Achse","y - Achse","y - Achse",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Primärvolumenstrom [m³/h]",{"$f":"K87","v":"q Sek [W/K] bei wok 200 kg/h"},{"$f":"CONCATENATE(\"Korrektur bei \", ROUND(AVERAGE($B$63),0), \" kg/h (Mittelwert)\")","v":"Korrektur bei 100 kg/h (Mittelwert)"},{"$f":"CONCATENATE(\"q Sek [W/K] bei w_soll \", ROUND($B$63,0), \" kg/h\")","v":"q Sek [W/K] bei w_soll 100 kg/h"},"Korrektur kühlen heizen bei \ngleichem Wärmetauscher"]
["V12",{"$f":"VLOOKUP(A88,Matrix_Rohdaten,$B$71,0)","v":"V12"},{"$f":"VLOOKUP(A88,Matrix_Rohdaten,$C$71,0)","v":4.5},{"$f":"VLOOKUP(A88,Matrix_Rohdaten,$D$71,0)","v":58.25},{"$f":"VLOOKUP(A88,Matrix_Rohdaten,$E$71,0)","v":200.02352533333334},{"$f":"VLOOKUP(A88,Matrix_Rohdaten,$F$71,0)","v":50},{"$f":"VLOOKUP(A88,Matrix_Rohdaten,$G$71,0)","v":22.916657030303032},{"$f":"VLOOKUP(A88,Matrix_Rohdaten,$H$71,0)","v":62.184984999999955},{"$f":"VLOOKUP(A88,Matrix_Rohdaten,$I$71,0)","v":1.5753122171642233},{"$f":"IF(G93=G94,G93,E98*H88^E97+F98*H88^F97+G98*H88^G97)","v":1.0019132183726924},{"$f":"G88/J88","v":22.87289618508504},{"$f":"IF(L93=L94,L93,J98*H88^J97+K98*H88^K97+L98*H88^L97)","v":1.0000000000000004},{"$f":"K88*L88","v":22.87289618508505},{"$f":"1/K88*M88-1","v":0},{"$f":"I88*H88","v":97.960766594673899},{"$f":"CONCATENATE(A87,\": Auslegung1\")","v":"Messreihe 2: Auslegung1"},1,"V_Prim soll [m³/h]","q sek [W/K] Auslegung 1","Primärdruck [Pa]","Induktionsverhältnis","Titel für Diagramme:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A88,Matrix_Rohdaten,$AO$70,0)","v":62.184984999999955},{"$f":"K88","v":22.87289618508504},{"$f":"IF(AQ93=AQ94,AQ93,AO98*AO88^AO97+AP98*AO88^AP97+AQ98*AO88^AQ97)","v":0.80605372973855749},{"$f":"AP88*AQ88","v":18.436783279910617},{"$f":"1/M88*AR88","v":0.80605372973855705}]
["V13",{"$f":"VLOOKUP(A89,Matrix_Rohdaten,$B$71,0)","v":"V13"},{"$f":"VLOOKUP(A89,Matrix_Rohdaten,$C$71,0)","v":4.5},{"$f":"VLOOKUP(A89,Matrix_Rohdaten,$D$71,0)","v":58.25},{"$f":"VLOOKUP(A89,Matrix_Rohdaten,$E$71,0)","v":200.61807159090904},{"$f":"VLOOKUP(A89,Matrix_Rohdaten,$F$71,0)","v":150},{"$f":"VLOOKUP(A89,Matrix_Rohdaten,$G$71,0)","v":39.95671624242425},{"$f":"VLOOKUP(A89,Matrix_Rohdaten,$H$71,0)","v":108.53977300000018},{"$f":"VLOOKUP(A89,Matrix_Rohdaten,$I$71,0)","v":1.6009211241131855},{"$f":"IF(G93=G94,G93,E98*H89^E97+F98*H89^F97+G98*H89^G97)","v":1.0019132183726924},{"$f":"G89/J89","v":39.880416297253724},{"$f":"IF(L93=L94,L93,J98*H89^J97+K98*H89^K97+L98*H89^L97)","v":1.0000000000000004},{"$f":"K89*L89","v":39.880416297253738},{"$f":"1/K89*M89-1","v":0},{"$f":"I89*H89","v":173.76361540215026},null,1,{"$f":"$B$58","v":150},{"$f":"R95*R89^R94+S95*R89^S94+T95*R89^T94+U95*R89^U94","v":52.685779589785199},{"$f":"V95*R89^W95","v":283.28724322269511},{"$f":"X95*R89^X94+Y95*R89^Y94+Z95*R89^Z94","v":1.7219549732893928},{"$f":"CONCATENATE($A$70, \" ; \",K87)","v":"HFBsf; HL; 4L; mit Edelstahlgitter ; q Sek [W/K] bei wok 200 kg/h"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A89,Matrix_Rohdaten,$AO$70,0)","v":108.53977300000018},{"$f":"K89","v":39.880416297253724},{"$f":"IF(AQ93=AQ94,AQ93,AO98*AO89^AO97+AP98*AO89^AP97+AQ98*AO89^AQ97)","v":0.80605372973855749},{"$f":"AP89*AQ89","v":32.145758299927714},{"$f":"1/M89*AR89","v":0.80605372973855716}]
["V14",{"$f":"VLOOKUP(A90,Matrix_Rohdaten,$B$71,0)","v":"V14"},{"$f":"VLOOKUP(A90,Matrix_Rohdaten,$C$71,0)","v":4.5},{"$f":"VLOOKUP(A90,Matrix_Rohdaten,$D$71,0)","v":58.25},{"$f":"VLOOKUP(A90,Matrix_Rohdaten,$E$71,0)","v":204.18283095454547},{"$f":"VLOOKUP(A90,Matrix_Rohdaten,$F$71,0)","v":250},{"$f":"VLOOKUP(A90,Matrix_Rohdaten,$G$71,0)","v":50.317188848484854},{"$f":"VLOOKUP(A90,Matrix_Rohdaten,$H$71,0)","v":139.87513399999992},{"$f":"VLOOKUP(A90,Matrix_Rohdaten,$I$71,0)","v":1.659053300341546},{"$f":"IF(G93=G94,G93,E98*H90^E97+F98*H90^F97+G98*H90^G97)","v":1.0019132183726924},{"$f":"G90/J90","v":50.221104907878185},{"$f":"IF(L93=L94,L93,J98*H90^J97+K98*H90^K97+L98*H90^L97)","v":1.0000000000000004},{"$f":"K90*L90","v":50.221104907878207},{"$f":"1/K90*M90-1","v":0},232.06030269841585,{"$f":"CONCATENATE(A87,\": Auslegung2\")","v":"Messreihe 2: Auslegung2"},2,"Primärdruck Soll [Pa]","q sek [W/K] Auslegung 2","V_Prim soll [m³/h] Auslegung 2","Induktionsverhältnis",{"$f":"CONCATENATE($A$70, \" ; \",M87)","v":"HFBsf; HL; 4L; mit Edelstahlgitter ; q Sek [W/K] bei w_soll 200 kg/h"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A90,Matrix_Rohdaten,$AO$70,0)","v":139.87513399999992},{"$f":"K90","v":50.221104907878185},{"$f":"IF(AQ93=AQ94,AQ93,AO98*AO90^AO97+AP98*AO90^AP97+AQ98*AO90^AQ97)","v":0.80605372973855749},{"$f":"AP90*AQ90","v":40.480908922586586},{"$f":"1/M90*AR90","v":0.80605372973855705}]
["V15",{"$f":"VLOOKUP(A91,Matrix_Rohdaten,$B$71,0)","v":"V15"},{"$f":"VLOOKUP(A91,Matrix_Rohdaten,$C$71,0)","v":4.5},{"$f":"VLOOKUP(A91,Matrix_Rohdaten,$D$71,0)","v":58.25},{"$f":"VLOOKUP(A91,Matrix_Rohdaten,$E$71,0)","v":204.22658893939396},{"$f":"VLOOKUP(A91,Matrix_Rohdaten,$F$71,0)","v":300},{"$f":"VLOOKUP(A91,Matrix_Rohdaten,$G$71,0)","v":53.97671965151514},{"$f":"VLOOKUP(A91,Matrix_Rohdaten,$H$71,0)","v":155.34428300000019},{"$f":"VLOOKUP(A91,Matrix_Rohdaten,$I$71,0)","v":1.6611486231078021},{"$f":"IF(G93=G94,G93,E98*H91^E97+F98*H91^F97+G98*H91^G97)","v":1.0019132183726924},{"$f":"G91/J91","v":53.873647599124538},{"$f":"IF(L93=L94,L93,J98*H91^J97+K98*H91^K97+L98*H91^L97)","v":1.0000000000000004},{"$f":"K91*L91","v":53.87364759912456},{"$f":"1/K91*M91-1","v":0},258.04994181311906,null,2,{"$f":"$B$59","v":150},{"$f":"R98*R91^R97+S98*R91^S97+T98*R91^T97+U98*R91^U97","v":41.446864371629033},{"$f":"V98*R91^W98","v":108.58383211606997},{"$f":"X98*R91^X97+Y98*R91^Y97+Z98*R91^Z97","v":1.6087938861891049},{"$f":"CONCATENATE(\"im Mittel \", ROUND(AVERAGE(N88:N91)*100,0), \" % Kühlleistung bei \", ROUND($B$62,0), \" kg/h\")","v":"im Mittel 0 % Kühlleistung bei 200 kg/h"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A91,Matrix_Rohdaten,$AO$70,0)","v":155.34428300000019},{"$f":"K91","v":53.873647599124538},{"$f":"IF(AQ93=AQ94,AQ93,AO98*AO91^AO97+AP98*AO91^AP97+AQ98*AO91^AQ97)","v":0.80605372973855749},{"$f":"AP91*AQ91","v":43.425054581895019},{"$f":"1/M91*AR91","v":0.80605372973855716}]
[null,null,null,null,{"$f":"CONCATENATE(\"w_mess = \", ROUND(E93,0),\" kg/h\")","v":"w_mess = 202 kg/h"},"Faktor: Wassermenge zu Nennwassermenge [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa]","Primärvolumenstrom[m³/h]",{"$f":"CONCATENATE(\"w_soll = \", ROUND($B$62,0),\" kg/h\")","v":"w_soll = 200 kg/h"},"Faktor: Wassermenge zu Nennwassermenge  [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa]","Primärvolumenstrom[m³/h]",null,null,null,"Polynom  y =","axn+bx(n-1)+...+nx+m",null,null,"Umrechnung: Druck D Volumenstrom",null,"y =","axn+bx(n-1)+...+nx+m",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"CONCATENATE(\"w_soll = \", ROUND($B$63,0),\" kg/h\")","v":"w_soll = 100 kg/h"},"Faktor: Wassermenge zu Nennwassermenge  [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa]","Primärvolumenstrom[m³/h]"]
[null,null,null,null,{"$f":"AVERAGE(E88:E91)","v":202.26275420454547},{"$f":"E93/$B$64","v":1.0113137710227273},{"$f":"$B$66*F93^$B$65+$C$66*F93^$C$65+$D$66*F93^$D$65+$E$66*F93^$E$65+$F$66","v":1.0019132183726924},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607},{"$f":"$B$62","v":200},{"$f":"J93/$B$64","v":1},{"$f":"$B$66*K93^$B$65+$C$66*K93^$C$65+$D$66*K93^$D$65+$E$66*K93^$E$65+$F$66","v":1.0000000000000004},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607},null,null,null,"a =","b =","c =","m =","y =","mxb","a =","b =","m =",null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO93/$B$64","v":0.5},{"$f":"$B$66*AP93^$B$65+$C$66*AP93^$C$65+$D$66*AP93^$D$65+$E$66*AP93^$E$65+$F$66","v":0.80605372973855749},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607}]
[null,null,null,null,{"$f":"AVERAGE(E88:E91)","v":202.26275420454547},{"$f":"E94/$B$64","v":1.0113137710227273},{"$f":"IFERROR($B$67*F94^$B$65+$C$67*F94^$C$65+$D$67*F94^$D$65+$E$67*F94^$E$65+$F$67,G93)","v":1.0019132183726924},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857},{"$f":"$B$62","v":200},{"$f":"J94/$B$64","v":1},{"$f":"IFERROR($B$67*K94^$B$65+$C$67*K94^$C$65+$D$67*K94^$D$65+$E$67*K94^$E$65+$F$67,L93)","v":1.0000000000000004},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857},null,null,1,3,2,1,0,null,null,2,1,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO94/$B$64","v":0.5},{"$f":"IFERROR($B$67*AP94^$B$65+$C$67*AP94^$C$65+$D$67*AP94^$D$65+$E$67*AP94^$E$65+$F$67,AQ93)","v":0.80605372973855749},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857}]
[null,null,null,null,{"$f":"AVERAGE(E88:E91)","v":202.26275420454547},{"$f":"E95/$B$64","v":1.0113137710227273},{"$f":"IFERROR($B$68*F95^$B$65+$C$68*F95^$C$65+$D$68*F95^$D$65+$E$68*F95^$E$65+$F$68,G93)","v":1.0019132183726924},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857},{"$f":"$B$62","v":200},{"$f":"J95/$B$64","v":1},{"$f":"IFERROR($B$68*K95^$B$65+$C$68*K95^$C$65+$D$68*K95^$D$65+$E$68*K95^$E$65+$F$68,L93)","v":1.0000000000000004},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857},null,null,1,{"$f":"LINEST(M88:M91,H88:H91^{1,2,3},0,0)","v":-5.4245904536263721E-6},9.7343722163114362E-4,0.32727623256048988,0,{"$f":"INDEX(LOGEST(Auswertung_Leistung!F88:F91,LN(Auswertung_Leistung!H88:H91),,TRUE),1,2)","v":1.4794808962291069E-2},{"$f":"LN(INDEX(LOGEST(F88:F91,LN(H88:H91),,TRUE),1,1))","v":1.967802424924336},{"$f":"LINEST(I88:I91,$H$73:$H$76^{0,1,2},0,0)","v":1.0690031876136949E-5},-6.4816626243064366E-4,1.5786541954409081,null,null,"Für Vergleich mit \"ohne Schieber\"",null,null,"Akustik",null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO95/$B$64","v":0.5},{"$f":"IFERROR($B$68*AP95^$B$65+$C$68*AP95^$C$65+$D$68*AP95^$D$65+$E$68*AP95^$E$65+$F$68,AQ93)","v":0.80605372973855749},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857}]
[null,null,null,null,"a =","b =","m =",null,null,"a =","b =","m =",null,"Korrektur\nWassermenge",null,null,null,"a =","b =","c =","m =","y =","mxb","a =","b =","m =",null,null,null,null,null,"Druckverlust [Pa] → \nSchallleistung [dBA]",null,null,null,null,null,null,null,null,"a =","b =","m ="]
[null,null,null,null,2,1,0,null,null,2,1,0,"Auslegung 1",{"$f":"J98*P89^2+K98*P89+L98","v":0},null,null,2,3,2,1,0,null,null,2,1,0,null,null,"Umrechnung: Druck _Volumenstrom",null,null,null,null,null,null,null,null,null,null,null,2,1,0]
[null,null,null,null,{"$f":"LINEST(G93:G95,I93:I95^{0,1,2},0,0)","v":-1.2476458444410157E-4},2.2360974455270816E-2,0,null,null,{"$f":"LINEST(L93:L95,N93:N95^{0,1,2},0,0)","v":-1.245263383656661E-4},2.2318274722026722E-2,0,"Auslegung 2",{"$f":"J98*R91^2+K98*R91+L98","v":0.54589859507652116},null,null,2,{"$f":"LINEST(M88:M91,F88:F91^{1,2,3},0,0)","v":3.5941103319159843E-6},-2.2483163585707128E-3,0.53269240046169086,0,{"$f":"INDEX(LOGEST(Auswertung_Leistung!H88:H91,LN(Auswertung_Leistung!F88:F91),,TRUE),1,2)","v":8.5130262193714756},{"$f":"LN(INDEX(LOGEST(H88:H91,LN(F88:F91),,TRUE),1,1))","v":0.50810423920799186},{"$f":"LINEST(I88:I91,$F$73:$F$76^{0,1,2},0,0)","v":1.303386695452488E-7},3.3236724256752067E-4,1.5560061797392086,null,null,"y =","mxb",null,"m","b",null,null,null,null,null,null,null,{"$f":"LINEST(AQ93:AQ95,AS93:AS95^{0,1,2},0,0)","v":-1.0037491949032032E-4},1.7989728581018466E-2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"CONCATENATE(\"H\",P100)","v":"H4,5"},{"$f":"$F$1","v":2},{"$f":"R97","v":3},2,1,0,null,null,{"$f":"X97","v":2},{"$f":"Y97","v":1},0,"V_Prim Min [m³/h]","V_Prim Max [m³/h]",null,null,null,"y = m∙LN(x) + b",null,null,null,null,null,null,null,null,"Korrekturfaktor Mittel"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"C88","v":4.5},{"$f":"$F$1","v":2},{"$f":"R98","v":3.5941103319159843E-6},-2.2483163585707128E-3,0.53269240046169086,0,{"$f":"IF(Q100=1,V95,V98)","v":8.5130262193714756},{"$f":"IF(Q100=1,W95,W98)","v":0.50810423920799186},{"$f":"X98","v":1.303386695452488E-7},{"$f":"Y98","v":3.3236724256752067E-4},1.5560061797392086,{"$f":"V98*$K$2^W98","v":58.896333262093655},{"$f":"V98*$K$3^W98","v":155.72819534846124},{"$f":"V95","v":1.4794808962291069E-2},{"$f":"W95","v":1.967802424924336},"Schieberstellung 4.2",15.984627550164161,-48.496659065735294,null,null,null,null,null,null,null,{"$f":"AVERAGE(AS88:AS91)","v":0.80605372973855705}]
[]
["Messreihe 3","Messung (Kontrolle)","Schieberstellung","Anzahl Düsen","Wasser-\nmenge [kg/h]","Primärdruck [Pa]","spez. Kühlleistung q Sek [W/K]","Primärvolumenstrom [m³/h]","Induktionsverhältnis i [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok",{"$f":"CONCATENATE(\"q Sek [W/K] bei wok \", G$21, \" kg/h\")","v":"q Sek [W/K] bei wok 200 kg/h"},{"$f":"CONCATENATE(\"Korrektur bei \", ROUND(AVERAGE($B$62),0), \" kg/h (Mittelwert)\")","v":"Korrektur bei 200 kg/h (Mittelwert)"},{"$f":"CONCATENATE(\"q Sek [W/K] bei w_soll \", ROUND($B$62,0), \" kg/h\")","v":"q Sek [W/K] bei w_soll 200 kg/h"},{"$f":"CONCATENATE(\"q Sek Abweichung von Nennwassermenge bei \", $B$62, \" kg/h\")","v":"q Sek Abweichung von Nennwassermenge bei 200 kg/h"},"Sekundärvolumenstrom [m³/h]",null,null,"x - Achse","y - Achse","y - Achse","y - Achse",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Primärvolumenstrom [m³/h]",{"$f":"K102","v":"q Sek [W/K] bei wok 200 kg/h"},{"$f":"CONCATENATE(\"Korrektur bei \", ROUND(AVERAGE($B$63),0), \" kg/h (Mittelwert)\")","v":"Korrektur bei 100 kg/h (Mittelwert)"},{"$f":"CONCATENATE(\"q Sek [W/K] bei w_soll \", ROUND($B$63,0), \" kg/h\")","v":"q Sek [W/K] bei w_soll 100 kg/h"},"Korrektur kühlen heizen bei \ngleichem Wärmetauscher"]
["V16",{"$f":"VLOOKUP(A103,Matrix_Rohdaten,$B$71,0)","v":"V16"},{"$f":"VLOOKUP(A103,Matrix_Rohdaten,$C$71,0)","v":4},{"$f":"VLOOKUP(A103,Matrix_Rohdaten,$D$71,0)","v":46.5},{"$f":"VLOOKUP(A103,Matrix_Rohdaten,$E$71,0)","v":204.1375500454545},{"$f":"VLOOKUP(A103,Matrix_Rohdaten,$F$71,0)","v":50},{"$f":"VLOOKUP(A103,Matrix_Rohdaten,$G$71,0)","v":14.649405803030303},{"$f":"VLOOKUP(A103,Matrix_Rohdaten,$H$71,0)/D103*D$107","v":38.584437903225862},{"$f":"VLOOKUP(A103,Matrix_Rohdaten,$I$71,0)/$D$107*D103","v":1.4694351604041354},{"$f":"IF(G108=G109,G108,E113*H103^E112+F113*H103^F112+G113*H103^G112)","v":1.0035866455753542},{"$f":"G103/J103","v":14.597051353380484},{"$f":"IF(L108=L109,L108,J113*H103^J112+K113*H103^K112+L113*H103^L112)","v":1.0000000000000004},{"$f":"K103*L103","v":14.597051353380492},{"$f":"1/K103*M103-1","v":0},{"$f":"I103*H103","v":56.697329699430092},{"$f":"CONCATENATE(A102,\": Auslegung1\")","v":"Messreihe 3: Auslegung1"},1,"V_Prim soll [m³/h]","q sek [W/K] Auslegung 1","Primärdruck [Pa]","Induktionsverhältnis","Titel für Diagramme:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A103,Matrix_Rohdaten,$AO$70,0)/$D$106*$D$107","v":38.584437903225862},{"$f":"K103","v":14.597051353380484},{"$f":"IF(AQ108=AQ109,AQ108,AO113*AO103^AO112+AP113*AO103^AP112+AQ113*AO103^AQ112)","v":0.80605372973855749},{"$f":"AP103*AQ103","v":11.766007686577598},{"$f":"1/M103*AR103","v":0.80605372973855716}]
["V17",{"$f":"VLOOKUP(A104,Matrix_Rohdaten,$B$71,0)","v":"V17"},{"$f":"VLOOKUP(A104,Matrix_Rohdaten,$C$71,0)","v":4},{"$f":"VLOOKUP(A104,Matrix_Rohdaten,$D$71,0)","v":46.5},{"$f":"VLOOKUP(A104,Matrix_Rohdaten,$E$71,0)","v":204.30769101515151},{"$f":"VLOOKUP(A104,Matrix_Rohdaten,$F$71,0)","v":150},{"$f":"VLOOKUP(A104,Matrix_Rohdaten,$G$71,0)","v":29.214819500000011},{"$f":"VLOOKUP(A104,Matrix_Rohdaten,$H$71,0)/D104*D$107","v":68.657728225806565},{"$f":"VLOOKUP(A104,Matrix_Rohdaten,$I$71,0)/$D$107*D104","v":1.6939976043825895},{"$f":"IF(G108=G109,G108,E113*H104^E112+F113*H104^F112+G113*H104^G112)","v":1.0035866455753542},{"$f":"G104/J104","v":29.110410774000702},{"$f":"IF(L108=L109,L108,J113*H104^J112+K113*H104^K112+L113*H104^L112)","v":1.0000000000000004},{"$f":"K104*L104","v":29.110410774000716},{"$f":"1/K104*M104-1","v":0},{"$f":"I104*H104","v":116.30602713686721},null,1,{"$f":"$B$58","v":150},{"$f":"R110*R104^R109+S110*R104^S109+T110*R104^T109+U110*R104^U109","v":48.889555151164579},{"$f":"V110*R104^W110","v":690.2886353284365},{"$f":"X110*R104^X109+Y110*R104^Y109+Z110*R104^Z109","v":1.8702853434746169},{"$f":"CONCATENATE($A$70, \" ; \",K102)","v":"HFBsf; HL; 4L; mit Edelstahlgitter ; q Sek [W/K] bei wok 200 kg/h"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A104,Matrix_Rohdaten,$AO$70,0)","v":85.135583000000139},{"$f":"K104","v":29.110410774000702},{"$f":"IF(AQ108=AQ109,AQ108,AO113*AO104^AO112+AP113*AO104^AP112+AQ113*AO104^AQ112)","v":0.80605372973855749},{"$f":"AP104*AQ104","v":23.464555178604755},{"$f":"1/M104*AR104","v":0.80605372973855716}]
["V18",{"$f":"VLOOKUP(A105,Matrix_Rohdaten,$B$71,0)","v":"V18"},{"$f":"VLOOKUP(A105,Matrix_Rohdaten,$C$71,0)","v":4},{"$f":"VLOOKUP(A105,Matrix_Rohdaten,$D$71,0)","v":46.5},{"$f":"VLOOKUP(A105,Matrix_Rohdaten,$E$71,0)","v":204.3686087878788},{"$f":"VLOOKUP(A105,Matrix_Rohdaten,$F$71,0)","v":250},{"$f":"VLOOKUP(A105,Matrix_Rohdaten,$G$71,0)","v":37.806210863636366},{"$f":"VLOOKUP(A105,Matrix_Rohdaten,$H$71,0)/D105*D$107","v":88.657873387096899},{"$f":"VLOOKUP(A105,Matrix_Rohdaten,$I$71,0)/$D$107*D105","v":1.7737921433594221},{"$f":"IF(G108=G109,G108,E113*H105^E112+F113*H105^F112+G113*H105^G112)","v":1.0035866455753542},{"$f":"G105/J105","v":37.671097986723552},{"$f":"IF(L108=L109,L108,J113*H105^J112+K113*H105^K112+L113*H105^L112)","v":1.0000000000000004},{"$f":"K105*L105","v":37.671097986723566},{"$f":"1/K105*M105-1","v":0},157.26063926098689,{"$f":"CONCATENATE(A102,\": Auslegung2\")","v":"Messreihe 3: Auslegung2"},2,"Primärdruck Soll [Pa]","q sek [W/K] Auslegung 2","V_Prim soll [m³/h] Auslegung 2","Induktionsverhältnis",{"$f":"CONCATENATE($A$70, \" ; \",M102)","v":"HFBsf; HL; 4L; mit Edelstahlgitter ; q Sek [W/K] bei w_soll 200 kg/h"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A105,Matrix_Rohdaten,$AO$70,0)","v":109.93576300000016},{"$f":"K105","v":37.671097986723552},{"$f":"IF(AQ108=AQ109,AQ108,AO113*AO105^AO112+AP113*AO105^AP112+AQ113*AO105^AQ112)","v":0.80605372973855749},{"$f":"AP105*AQ105","v":30.364929035545185},{"$f":"1/M105*AR105","v":0.80605372973855727}]
["V19",{"$f":"VLOOKUP(A106,Matrix_Rohdaten,$B$71,0)","v":"V19"},{"$f":"VLOOKUP(A106,Matrix_Rohdaten,$C$71,0)","v":4},{"$f":"VLOOKUP(A106,Matrix_Rohdaten,$D$71,0)","v":46.5},{"$f":"VLOOKUP(A106,Matrix_Rohdaten,$E$71,0)","v":204.41847927272727},{"$f":"VLOOKUP(A106,Matrix_Rohdaten,$F$71,0)","v":300},{"$f":"VLOOKUP(A106,Matrix_Rohdaten,$G$71,0)","v":41.451914060606093},{"$f":"VLOOKUP(A106,Matrix_Rohdaten,$H$71,0)/D106*D$107","v":97.270825806451782},{"$f":"VLOOKUP(A106,Matrix_Rohdaten,$I$71,0)/$D$107*D106","v":1.8295262597097899},{"$f":"IF(G108=G109,G108,E113*H106^E112+F113*H106^F112+G113*H106^G112)","v":1.0035866455753542},{"$f":"G106/J106","v":41.303772069268412},{"$f":"IF(L108=L109,L108,J113*H106^J112+K113*H106^K112+L113*H106^L112)","v":1.0000000000000004},{"$f":"K106*L106","v":41.303772069268433},{"$f":"1/K106*M106-1","v":0},177.95953011656025,null,2,{"$f":"$B$59","v":150},{"$f":"R113*R106^R112+S113*R106^S112+T113*R106^T112+U113*R106^U112","v":29.617394516585446},{"$f":"V113*R106^W113","v":68.201596860773648},{"$f":"X113*R106^X112+Y113*R106^Y112+Z113*R106^Z112","v":1.6799021649378538},{"$f":"CONCATENATE(\"im Mittel \", ROUND(AVERAGE(N103:N106)*100,0), \" % Kühlleistung bei \", ROUND($B$62,0), \" kg/h\")","v":"im Mittel 0 % Kühlleistung bei 200 kg/h"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A106,Matrix_Rohdaten,$AO$70,0)","v":120.6158240000002},{"$f":"K106","v":41.303772069268412},{"$f":"IF(AQ108=AQ109,AQ108,AO113*AO106^AO112+AP113*AO106^AP112+AQ113*AO106^AQ112)","v":0.80605372973855749},{"$f":"AP106*AQ106","v":33.293059528705058},{"$f":"1/M106*AR106","v":0.80605372973855705}]
[null,null,"Düsenanzahl HFBsf-Standard (2x25 Düsen je 6,8mm)",{"$f":"25+25/2","v":37.5},{"$f":"CONCATENATE(\"w_mess = \", ROUND(E108,0),\" kg/h\")","v":"w_mess = 204 kg/h"},"Faktor: Wassermenge zu Nennwassermenge [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa]","Primärvolumenstrom[m³/h]",{"$f":"CONCATENATE(\"w_soll = \", ROUND($B$62,0),\" kg/h\")","v":"w_soll = 200 kg/h"},"Faktor: Wassermenge zu Nennwassermenge  [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa]","Primärvolumenstrom[m³/h]",null,null,null,"Polynom  y =","axn+bx(n-1)+...+nx+m",null,null,"Umrechnung: Druck D Volumenstrom",null,"y =","axn+bx(n-1)+...+nx+m",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"CONCATENATE(\"w_soll = \", ROUND($B$63,0),\" kg/h\")","v":"w_soll = 100 kg/h"},"Faktor: Wassermenge zu Nennwassermenge  [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa]","Primärvolumenstrom[m³/h]"]
[null,null,null,null,{"$f":"AVERAGE(E103:E106)","v":204.30808228030301},{"$f":"E108/$B$64","v":1.021540411401515},{"$f":"$B$66*F108^$B$65+$C$66*F108^$C$65+$D$66*F108^$D$65+$E$66*F108^$E$65+$F$66","v":1.0035866455753542},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607},{"$f":"$B$62","v":200},{"$f":"J108/$B$64","v":1},{"$f":"$B$66*K108^$B$65+$C$66*K108^$C$65+$D$66*K108^$D$65+$E$66*K108^$E$65+$F$66","v":1.0000000000000004},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607},null,null,null,"a =","b =","c =","m =","y =","mxb","a =","b =","m =",null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO108/$B$64","v":0.5},{"$f":"$B$66*AP108^$B$65+$C$66*AP108^$C$65+$D$66*AP108^$D$65+$E$66*AP108^$E$65+$F$66","v":0.80605372973855749},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607}]
[null,null,null,null,{"$f":"AVERAGE(E103:E106)","v":204.30808228030301},{"$f":"E109/$B$64","v":1.021540411401515},{"$f":"IFERROR($B$67*F109^$B$65+$C$67*F109^$C$65+$D$67*F109^$D$65+$E$67*F109^$E$65+$F$67,G108)","v":1.0035866455753542},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857},{"$f":"$B$62","v":200},{"$f":"J109/$B$64","v":1},{"$f":"IFERROR($B$67*K109^$B$65+$C$67*K109^$C$65+$D$67*K109^$D$65+$E$67*K109^$E$65+$F$67,L108)","v":1.0000000000000004},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857},null,null,1,3,2,1,0,null,null,2,1,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO109/$B$64","v":0.5},{"$f":"IFERROR($B$67*AP109^$B$65+$C$67*AP109^$C$65+$D$67*AP109^$D$65+$E$67*AP109^$E$65+$F$67,AQ108)","v":0.80605372973855749},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857}]
[null,null,null,null,{"$f":"AVERAGE(E103:E106)","v":204.30808228030301},{"$f":"E110/$B$64","v":1.021540411401515},{"$f":"IFERROR($B$68*F110^$B$65+$C$68*F110^$C$65+$D$68*F110^$D$65+$E$68*F110^$E$65+$F$68,G108)","v":1.0035866455753542},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857},{"$f":"$B$62","v":200},{"$f":"J110/$B$64","v":1},{"$f":"IFERROR($B$68*K110^$B$65+$C$68*K110^$C$65+$D$68*K110^$D$65+$E$68*K110^$E$65+$F$68,L108)","v":1.0000000000000004},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857},null,null,1,{"$f":"LINEST(M103:M106,H103:H106^{1,2,3},0,0)","v":-2.3351223059853856E-5},3.9232206197897055E-3,0.26284979355268645,0,{"$f":"INDEX(LOGEST(Auswertung_Leistung!F103:F106,LN(Auswertung_Leistung!H103:H106),,TRUE),1,2)","v":4.2122870232909455E-2},{"$f":"LN(INDEX(LOGEST(F103:F106,LN(H103:H106),,TRUE),1,1))","v":1.9367353045000755},{"$f":"LINEST(I103:I106,$H$73:$H$76^{0,1,2},0,0)","v":-2.6714856512257836E-5},9.4998995060215571E-3,1.0463846890971846,null,null,"Für Vergleich mit \"ohne Schieber\"",null,null,"Akustik",null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO110/$B$64","v":0.5},{"$f":"IFERROR($B$68*AP110^$B$65+$C$68*AP110^$C$65+$D$68*AP110^$D$65+$E$68*AP110^$E$65+$F$68,AQ108)","v":0.80605372973855749},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857}]
[null,null,null,null,"a =","b =","m =",null,null,"a =","b =","m =",null,"Korrektur\nWassermenge",null,null,null,"a =","b =","c =","m =","y =","mxb","a =","b =","m =",null,null,null,null,null,"Druckverlust [Pa] → \nSchallleistung [dBA]",null,null,null,null,null,null,null,null,"a =","b =","m ="]
[null,null,null,null,2,1,0,null,null,2,1,0,"Auslegung 1",{"$f":"J113*P104^2+K113*P104+L113","v":0},null,null,2,3,2,1,0,null,null,2,1,0,null,null,"Umrechnung: Druck _Volumenstrom",null,null,null,null,null,null,null,null,null,null,null,2,1,0]
[null,null,null,null,{"$f":"LINEST(G108:G110,I108:I110^{0,1,2},0,0)","v":-1.2497297020622392E-4},2.2398322463311915E-2,0,null,null,{"$f":"LINEST(L108:L110,N108:N110^{0,1,2},0,0)","v":-1.245263383656661E-4},2.2318274722026722E-2,0,"Auslegung 2",{"$f":"J113*R106^2+K113*R106+L113","v":0.54589859507652116},null,null,2,{"$f":"LINEST(M103:M106,F103:F106^{1,2,3},0,0)","v":1.8387988310100543E-6},-1.2214199954404927E-3,0.33928932239558396,0,{"$f":"INDEX(LOGEST(Auswertung_Leistung!H103:H106,LN(Auswertung_Leistung!F103:F106),,TRUE),1,2)","v":5.1326052866512075},{"$f":"LN(INDEX(LOGEST(H103:H106,LN(F103:F106),,TRUE),1,1))","v":0.51627277654528081},{"$f":"LINEST(I103:I106,$F$73:$F$76^{0,1,2},0,0)","v":-4.5602617555813023E-6},2.9744360781192389E-3,1.3363426427205474,null,null,"y =","mxb",null,"m","b",null,null,null,null,null,null,null,{"$f":"LINEST(AQ108:AQ110,AS108:AS110^{0,1,2},0,0)","v":-1.0037491949032032E-4},1.7989728581018466E-2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"CONCATENATE(\"H\",P115)","v":"H4"},{"$f":"$F$1","v":2},{"$f":"R112","v":3},2,1,0,null,null,{"$f":"X112","v":2},{"$f":"Y112","v":1},0,"V_Prim Min [m³/h]","V_Prim Max [m³/h]",null,null,null,"y = m∙LN(x) + b",null,null,null,null,null,null,null,null,"Korrekturfaktor Mittel"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"C103","v":4},{"$f":"$F$1","v":2},{"$f":"R113","v":1.8387988310100543E-6},-1.2214199954404927E-3,0.33928932239558396,0,{"$f":"IF(Q115=1,V110,V113)","v":5.1326052866512075},{"$f":"IF(Q115=1,W110,W113)","v":0.51627277654528081},{"$f":"X113","v":-4.5602617555813023E-6},{"$f":"Y113","v":2.9744360781192389E-3},1.3363426427205474,{"$f":"V113*$K$2^W113","v":36.630806586501116},{"$f":"V113*$K$3^W113","v":98.381681885788808},{"$f":"V110","v":4.2122870232909455E-2},{"$f":"W110","v":1.9367353045000755},"Schieberstelung 4",15.74924536350807,-47.551168528904682,null,null,null,null,null,null,null,{"$f":"AVERAGE(AS103:AS106)","v":0.80605372973855716}]
[]
["Messreihe 4","Messung (Kontrolle)","Schieberstellung","Anzahl Düsen","Wasser-\nmenge [kg/h]","Primärdruck [Pa]","spez. Kühlleistung q Sek [W/K]","Primärvolumenstrom [m³/h]","Induktionsverhältnis i [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok",{"$f":"CONCATENATE(\"q Sek [W/K] bei wok \", G$21, \" kg/h\")","v":"q Sek [W/K] bei wok 200 kg/h"},{"$f":"CONCATENATE(\"Korrektur bei \", ROUND(AVERAGE($B$62),0), \" kg/h (Mittelwert)\")","v":"Korrektur bei 200 kg/h (Mittelwert)"},{"$f":"CONCATENATE(\"q Sek [W/K] bei w_soll \", ROUND($B$62,0), \" kg/h\")","v":"q Sek [W/K] bei w_soll 200 kg/h"},{"$f":"CONCATENATE(\"q Sek Abweichung von Nennwassermenge bei \", $B$62, \" kg/h\")","v":"q Sek Abweichung von Nennwassermenge bei 200 kg/h"},null,null,null,"x - Achse","y - Achse","y - Achse","y - Achse",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Primärvolumenstrom [m³/h]",{"$f":"K117","v":"q Sek [W/K] bei wok 200 kg/h"},{"$f":"CONCATENATE(\"Korrektur bei \", ROUND(AVERAGE($B$63),0), \" kg/h (Mittelwert)\")","v":"Korrektur bei 100 kg/h (Mittelwert)"},{"$f":"CONCATENATE(\"q Sek [W/K] bei w_soll \", ROUND($B$63,0), \" kg/h\")","v":"q Sek [W/K] bei w_soll 100 kg/h"},"Korrektur kühlen heizen bei \ngleichem Wärmetauscher"]
["V20",{"$f":"VLOOKUP(A118,Matrix_Rohdaten,$B$71,0)","v":"V20"},{"$f":"VLOOKUP(A118,Matrix_Rohdaten,$C$71,0)","v":3.5},{"$f":"VLOOKUP(A118,Matrix_Rohdaten,$D$71,0)","v":34.75},{"$f":"VLOOKUP(A118,Matrix_Rohdaten,$E$71,0)","v":200.06402603076913},{"$f":"VLOOKUP(A118,Matrix_Rohdaten,$F$71,0)","v":50},{"$f":"VLOOKUP(A118,Matrix_Rohdaten,$G$71,0)","v":10.818601784615382},{"$f":"VLOOKUP(A118,Matrix_Rohdaten,$H$71,0)","v":38.234565000000018},{"$f":"VLOOKUP(A118,Matrix_Rohdaten,$I$71,0)","v":1.2405021223645469},{"$f":"IF(G123=G124,G123,E128*H118^E127+F128*H118^F127+G128*H118^G127)","v":1.0011311180174833},{"$f":"G118/J118","v":10.806378495195721},{"$f":"IF(L123=L124,L123,J128*H118^J127+K128*H118^K127+L128*H118^L127)","v":1.0000000000000004},{"$f":"K118*L118","v":10.806378495195727},{"$f":"1/K118*M118-1","v":0},null,{"$f":"CONCATENATE(A117,\": Auslegung1\")","v":"Messreihe 4: Auslegung1"},1,"V_Prim soll [m³/h]","q sek [W/K] Auslegung 1","Primärdruck [Pa]","Induktionsverhältnis","Titel für Diagramme:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A118,Matrix_Rohdaten,$AO$70,0)","v":38.234565000000018},{"$f":"K118","v":10.806378495195721},{"$f":"IF(AQ123=AQ124,AQ123,AO128*AO118^AO127+AP128*AO118^AP127+AQ128*AO118^AQ127)","v":0.80605372973855749},{"$f":"AP118*AQ118","v":8.7105216910190517},{"$f":"1/M118*AR118","v":0.80605372973855716}]
["V21",{"$f":"VLOOKUP(A119,Matrix_Rohdaten,$B$71,0)","v":"V21"},{"$f":"VLOOKUP(A119,Matrix_Rohdaten,$C$71,0)","v":3.5},{"$f":"VLOOKUP(A119,Matrix_Rohdaten,$D$71,0)","v":34.75},{"$f":"VLOOKUP(A119,Matrix_Rohdaten,$E$71,0)","v":200.25050950769236},{"$f":"VLOOKUP(A119,Matrix_Rohdaten,$F$71,0)","v":150},{"$f":"VLOOKUP(A119,Matrix_Rohdaten,$G$71,0)","v":22.813904215384614},{"$f":"VLOOKUP(A119,Matrix_Rohdaten,$H$71,0)","v":68.64624599999992},{"$f":"VLOOKUP(A119,Matrix_Rohdaten,$I$71,0)","v":1.3938357523419989},{"$f":"IF(G123=G124,G123,E128*H119^E127+F128*H119^F127+G128*H119^G127)","v":1.0011311180174833},{"$f":"G119/J119","v":22.788128153045985},{"$f":"IF(L123=L124,L123,J128*H119^J127+K128*H119^K127+L128*H119^L127)","v":1.0000000000000004},{"$f":"K119*L119","v":22.788128153045996},{"$f":"1/K119*M119-1","v":0},null,null,1,{"$f":"$B$58","v":150},{"$f":"R125*R119^R124+S125*R119^S124+T125*R119^T124+U125*R119^U124","v":43.887365353420833},{"$f":"V125*R119^W125","v":674.71283121504678},{"$f":"X125*R119^X124+Y125*R119^Y124+Z125*R119^Z124","v":1.4453017798415737},{"$f":"CONCATENATE($A$70, \" ; \",K117)","v":"HFBsf; HL; 4L; mit Edelstahlgitter ; q Sek [W/K] bei wok 200 kg/h"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A119,Matrix_Rohdaten,$AO$70,0)","v":68.64624599999992},{"$f":"K119","v":22.788128153045985},{"$f":"IF(AQ123=AQ124,AQ123,AO128*AO119^AO127+AP128*AO119^AP127+AQ128*AO119^AQ127)","v":0.80605372973855749},{"$f":"AP119*AQ119","v":18.368455691522943},{"$f":"1/M119*AR119","v":0.80605372973855716}]
["V22",{"$f":"VLOOKUP(A120,Matrix_Rohdaten,$B$71,0)","v":"V22"},{"$f":"VLOOKUP(A120,Matrix_Rohdaten,$C$71,0)","v":3.5},{"$f":"VLOOKUP(A120,Matrix_Rohdaten,$D$71,0)","v":34.75},{"$f":"VLOOKUP(A120,Matrix_Rohdaten,$E$71,0)","v":201.2171045692308},{"$f":"VLOOKUP(A120,Matrix_Rohdaten,$F$71,0)","v":250},{"$f":"VLOOKUP(A120,Matrix_Rohdaten,$G$71,0)","v":30.00132553846154},{"$f":"VLOOKUP(A120,Matrix_Rohdaten,$H$71,0)","v":89.076154999999986},{"$f":"VLOOKUP(A120,Matrix_Rohdaten,$I$71,0)","v":1.4155143730806468},{"$f":"IF(G123=G124,G123,E128*H120^E127+F128*H120^F127+G128*H120^G127)","v":1.0011311180174833},{"$f":"G120/J120","v":29.967428839763233},{"$f":"IF(L123=L124,L123,J128*H120^J127+K128*H120^K127+L128*H120^L127)","v":1.0000000000000004},{"$f":"K120*L120","v":29.967428839763247},{"$f":"1/K120*M120-1","v":0},null,{"$f":"CONCATENATE(A117,\": Auslegung2\")","v":"Messreihe 4: Auslegung2"},2,"Primärdruck Soll [Pa]","q sek [W/K] Auslegung 2","V_Prim soll [m³/h] Auslegung 2","Induktionsverhältnis",{"$f":"CONCATENATE($A$70, \" ; \",M117)","v":"HFBsf; HL; 4L; mit Edelstahlgitter ; q Sek [W/K] bei w_soll 200 kg/h"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A120,Matrix_Rohdaten,$AO$70,0)","v":89.076154999999986},{"$f":"K120","v":29.967428839763233},{"$f":"IF(AQ123=AQ124,AQ123,AO128*AO120^AO127+AP128*AO120^AP127+AQ128*AO120^AQ127)","v":0.80605372973855749},{"$f":"AP120*AQ120","v":24.155357786965965},{"$f":"1/M120*AR120","v":0.80605372973855693}]
["V23",{"$f":"VLOOKUP(A121,Matrix_Rohdaten,$B$71,0)","v":"V23"},{"$f":"VLOOKUP(A121,Matrix_Rohdaten,$C$71,0)","v":3.5},{"$f":"VLOOKUP(A121,Matrix_Rohdaten,$D$71,0)","v":34.75},{"$f":"VLOOKUP(A121,Matrix_Rohdaten,$E$71,0)","v":203.78141501538454},{"$f":"VLOOKUP(A121,Matrix_Rohdaten,$F$71,0)","v":300},{"$f":"VLOOKUP(A121,Matrix_Rohdaten,$G$71,0)","v":33.584705384615376},{"$f":"VLOOKUP(A121,Matrix_Rohdaten,$H$71,0)","v":97.709718000000052},{"$f":"VLOOKUP(A121,Matrix_Rohdaten,$I$71,0)","v":1.4557371019177556},{"$f":"IF(G123=G124,G123,E128*H121^E127+F128*H121^F127+G128*H121^G127)","v":1.0011311180174833},{"$f":"G121/J121","v":33.546760039906047},{"$f":"IF(L123=L124,L123,J128*H121^J127+K128*H121^K127+L128*H121^L127)","v":1.0000000000000004},{"$f":"K121*L121","v":33.546760039906061},{"$f":"1/K121*M121-1","v":0},null,null,2,{"$f":"$B$59","v":150},{"$f":"R128*R121^R127+S128*R121^S127+T128*R121^T127+U128*R121^U127","v":22.964241258245501},{"$f":"V128*R121^W128","v":68.186102981531889},{"$f":"X128*R121^X127+Y128*R121^Y127+Z128*R121^Z127","v":1.3780057931596197},{"$f":"CONCATENATE(\"im Mittel \", ROUND(AVERAGE(N118:N121)*100,0), \" % Kühlleistung bei \", ROUND($B$62,0), \" kg/h\")","v":"im Mittel 0 % Kühlleistung bei 200 kg/h"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A121,Matrix_Rohdaten,$AO$70,0)","v":97.709718000000052},{"$f":"K121","v":33.546760039906047},{"$f":"IF(AQ123=AQ124,AQ123,AO128*AO121^AO127+AP128*AO121^AP127+AQ128*AO121^AQ127)","v":0.80605372973855749},{"$f":"AP121*AQ121","v":27.040491050810669},{"$f":"1/M121*AR121","v":0.80605372973855716}]
[null,null,null,null,{"$f":"CONCATENATE(\"w_mess = \", ROUND(E123,0),\" kg/h\")","v":"w_mess = 201 kg/h"},"Faktor: Wassermenge zu Nennwassermenge [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa]","Primärvolumenstrom[m³/h]",{"$f":"CONCATENATE(\"w_soll = \", ROUND($B$62,0),\" kg/h\")","v":"w_soll = 200 kg/h"},"Faktor: Wassermenge zu Nennwassermenge  [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa]","Primärvolumenstrom[m³/h]",null,null,null,"Polynom  y =","axn+bx(n-1)+...+nx+m",null,null,"Umrechnung: Druck D Volumenstrom",null,"y =","axn+bx(n-1)+...+nx+m",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"CONCATENATE(\"w_soll = \", ROUND($B$63,0),\" kg/h\")","v":"w_soll = 100 kg/h"},"Faktor: Wassermenge zu Nennwassermenge  [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa]","Primärvolumenstrom[m³/h]"]
[null,null,null,null,{"$f":"AVERAGE(E118:E121)","v":201.32826378076919},{"$f":"E123/$B$64","v":1.0066413189038459},{"$f":"$B$66*F123^$B$65+$C$66*F123^$C$65+$D$66*F123^$D$65+$E$66*F123^$E$65+$F$66","v":1.0011311180174833},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607},{"$f":"$B$62","v":200},{"$f":"J123/$B$64","v":1},{"$f":"$B$66*K123^$B$65+$C$66*K123^$C$65+$D$66*K123^$D$65+$E$66*K123^$E$65+$F$66","v":1.0000000000000004},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607},null,null,null,"a =","b =","c =","m =","y =","mxb","a =","b =","m =",null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO123/$B$64","v":0.5},{"$f":"$B$66*AP123^$B$65+$C$66*AP123^$C$65+$D$66*AP123^$D$65+$E$66*AP123^$E$65+$F$66","v":0.80605372973855749},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607}]
[null,null,null,null,{"$f":"AVERAGE(E118:E121)","v":201.32826378076919},{"$f":"E124/$B$64","v":1.0066413189038459},{"$f":"IFERROR($B$67*F124^$B$65+$C$67*F124^$C$65+$D$67*F124^$D$65+$E$67*F124^$E$65+$F$67,G123)","v":1.0011311180174833},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857},{"$f":"$B$62","v":200},{"$f":"J124/$B$64","v":1},{"$f":"IFERROR($B$67*K124^$B$65+$C$67*K124^$C$65+$D$67*K124^$D$65+$E$67*K124^$E$65+$F$67,L123)","v":1.0000000000000004},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857},null,null,1,3,2,1,0,null,null,2,1,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO124/$B$64","v":0.5},{"$f":"IFERROR($B$67*AP124^$B$65+$C$67*AP124^$C$65+$D$67*AP124^$D$65+$E$67*AP124^$E$65+$F$67,AQ123)","v":0.80605372973855749},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857}]
[null,null,null,null,{"$f":"AVERAGE(E118:E121)","v":201.32826378076919},{"$f":"E125/$B$64","v":1.0066413189038459},{"$f":"IFERROR($B$68*F125^$B$65+$C$68*F125^$C$65+$D$68*F125^$D$65+$E$68*F125^$E$65+$F$68,G123)","v":1.0011311180174833},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857},{"$f":"$B$62","v":200},{"$f":"J125/$B$64","v":1},{"$f":"IFERROR($B$68*K125^$B$65+$C$68*K125^$C$65+$D$68*K125^$D$65+$E$68*K125^$E$65+$F$68,L123)","v":1.0000000000000004},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857},null,null,1,{"$f":"LINEST(M118:M121,H118:H121^{1,2,3},0,0)","v":-1.6838504511603034E-5},3.2393582752556632E-3,0.18554504591219095,0,{"$f":"INDEX(LOGEST(Auswertung_Leistung!F118:F121,LN(Auswertung_Leistung!H118:H121),,TRUE),1,2)","v":4.7732616792876846E-2},{"$f":"LN(INDEX(LOGEST(F118:F121,LN(H118:H121),,TRUE),1,1))","v":1.9072287102856782},{"$f":"LINEST(I118:I121,$H$73:$H$76^{0,1,2},0,0)","v":-2.7731531488509839E-5},7.691944321224416E-3,0.91546959014938278,null,null,"Für Vergleich mit \"ohne Schieber\"",null,null,"Akustik",null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO125/$B$64","v":0.5},{"$f":"IFERROR($B$68*AP125^$B$65+$C$68*AP125^$C$65+$D$68*AP125^$D$65+$E$68*AP125^$E$65+$F$68,AQ123)","v":0.80605372973855749},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857}]
[null,null,null,null,"a =","b =","m =",null,null,"a =","b =","m =",null,"Korrektur\nWassermenge",null,null,null,"a =","b =","c =","m =","y =","mxb","a =","b =","m =",null,null,null,null,null,"Druckverlust [Pa] → \nSchallleistung [dBA]",null,null,null,null,null,null,null,null,"a =","b =","m ="]
[null,null,null,null,2,1,0,null,null,2,1,0,"Auslegung 1",{"$f":"J128*P119^2+K128*P119+L128","v":0},null,null,2,3,2,1,0,null,null,2,1,0,null,null,"Umrechnung: Druck _Volumenstrom",null,null,null,null,null,null,null,null,null,null,null,2,1,0]
[null,null,null,null,{"$f":"LINEST(G123:G125,I123:I125^{0,1,2},0,0)","v":-1.2466719235067244E-4},2.2343519324686603E-2,0,null,null,{"$f":"LINEST(L123:L125,N123:N125^{0,1,2},0,0)","v":-1.245263383656661E-4},2.2318274722026722E-2,0,"Auslegung 2",{"$f":"J128*R121^2+K128*R121+L128","v":0.54589859507652116},null,null,2,{"$f":"LINEST(M118:M121,F118:F121^{1,2,3},0,0)","v":1.300167937369223E-6},-8.5865951036070878E-4,0.25264008968493545,0,{"$f":"INDEX(LOGEST(Auswertung_Leistung!H118:H121,LN(Auswertung_Leistung!F118:F121),,TRUE),1,2)","v":4.9302012748615898},{"$f":"LN(INDEX(LOGEST(H118:H121,LN(F118:F121),,TRUE),1,1))","v":0.52425706672694061},{"$f":"LINEST(I118:I121,$F$73:$F$76^{0,1,2},0,0)","v":-3.5750582172881409E-6},2.0425584738612158E-3,1.1520608319694206,null,null,"y =","mxb",null,"m","b",null,null,null,null,null,null,null,{"$f":"LINEST(AQ123:AQ125,AS123:AS125^{0,1,2},0,0)","v":-1.0037491949032032E-4},1.7989728581018466E-2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"CONCATENATE(\"H\",P130)","v":"H3,5"},{"$f":"$F$1","v":2},{"$f":"R127","v":3},2,1,0,null,null,{"$f":"X127","v":2},{"$f":"Y127","v":1},0,"V_Prim Min [m³/h]","V_Prim Max [m³/h]",null,null,null,"y = m∙LN(x) + b",null,null,null,null,null,null,null,null,"Korrekturfaktor Mittel"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"C118","v":3.5},{"$f":"$F$1","v":2},{"$f":"R128","v":1.300167937369223E-6},-8.5865951036070878E-4,0.25264008968493545,0,{"$f":"IF(Q130=1,V125,V128)","v":4.9302012748615898},{"$f":"IF(Q130=1,W125,W128)","v":0.52425706672694061},{"$f":"X128","v":-3.5750582172881409E-6},{"$f":"Y128","v":2.0425584738612158E-3},1.1520608319694206,{"$f":"V128*$K$2^W128","v":36.272124446051805},{"$f":"V128*$K$3^W128","v":98.918243580174746},{"$f":"V125","v":4.7732616792876846E-2},{"$f":"W125","v":1.9072287102856782},"Schieberstellung 3.2",13.411149229140813,-36.185444222433873,null,null,null,null,null,null,null,{"$f":"AVERAGE(AS118:AS121)","v":0.80605372973855705}]
[]
["Messreihe 5","Messung (Kontrolle)","Schieberstellung","Anzahl Düsen","Wasser-\nmenge [kg/h]","Primärdruck [Pa]","spez. Kühlleistung q Sek [W/K]","Primärvolumenstrom [m³/h]","Induktionsverhältnis i [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok",{"$f":"CONCATENATE(\"q Sek [W/K] bei wok \", G$21, \" kg/h\")","v":"q Sek [W/K] bei wok 200 kg/h"},{"$f":"CONCATENATE(\"Korrektur bei \", ROUND(AVERAGE($B$62),0), \" kg/h (Mittelwert)\")","v":"Korrektur bei 200 kg/h (Mittelwert)"},{"$f":"CONCATENATE(\"q Sek [W/K] bei w_soll \", ROUND($B$62,0), \" kg/h\")","v":"q Sek [W/K] bei w_soll 200 kg/h"},{"$f":"CONCATENATE(\"q Sek Abweichung von Nennwassermenge bei \", $B$62, \" kg/h\")","v":"q Sek Abweichung von Nennwassermenge bei 200 kg/h"},"Sekundärvolumenstrom [m³/h]",null,null,"x - Achse","y - Achse","y - Achse","y - Achse",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Primärvolumenstrom [m³/h]",{"$f":"K132","v":"q Sek [W/K] bei wok 200 kg/h"},{"$f":"CONCATENATE(\"Korrektur bei \", ROUND(AVERAGE($B$63),0), \" kg/h (Mittelwert)\")","v":"Korrektur bei 100 kg/h (Mittelwert)"},{"$f":"CONCATENATE(\"q Sek [W/K] bei w_soll \", ROUND($B$63,0), \" kg/h\")","v":"q Sek [W/K] bei w_soll 100 kg/h"},"Korrektur kühlen heizen bei \ngleichem Wärmetauscher"]
["V24",{"$f":"VLOOKUP(A133,Matrix_Rohdaten,$B$71,0)","v":"V24"},{"$f":"VLOOKUP(A133,Matrix_Rohdaten,$C$71,0)","v":3},{"$f":"VLOOKUP(A133,Matrix_Rohdaten,$D$71,0)","v":32},{"$f":"VLOOKUP(A133,Matrix_Rohdaten,$E$71,0)","v":198.80338695384617},{"$f":"VLOOKUP(A133,Matrix_Rohdaten,$F$71,0)","v":50},{"$f":"VLOOKUP(A133,Matrix_Rohdaten,$G$71,0)","v":11.851510938461541},{"$f":"VLOOKUP(A133,Matrix_Rohdaten,$H$71,0)/D133*D$137","v":25.043767968750032},{"$f":"VLOOKUP(A133,Matrix_Rohdaten,$I$71,0)/$D$137*D133","v":1.9840395632746353},{"$f":"IF(G138=G139,G138,E143*H133^E142+F143*H133^F142+G143*H133^G142)","v":0.99930304908338896},{"$f":"G133/J133","v":11.859776620648104},{"$f":"IF(L138=L139,L138,J143*H133^J142+K143*H133^K142+L143*H133^L142)","v":1.0000000000000004},{"$f":"K133*L133","v":11.859776620648109},{"$f":"1/K133*M133-1","v":0},{"$f":"I133*H133","v":49.68782646347011},{"$f":"CONCATENATE(A132,\": Auslegung1\")","v":"Messreihe 5: Auslegung1"},1,"V_Prim soll [m³/h]","q sek [W/K] Auslegung 1","Primärdruck [Pa]","Induktionsverhältnis","Titel für Diagramme:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A133,Matrix_Rohdaten,$AO$70,0)/$D$136*$D$137","v":25.043767968750032},{"$f":"K133","v":11.859776620648104},{"$f":"IF(AQ138=AQ139,AQ138,AO143*AO133^AO142+AP143*AO133^AP142+AQ143*AO133^AQ142)","v":0.80605372973855749},{"$f":"AP133*AQ133","v":9.5596171789395488},{"$f":"1/M133*AR133","v":0.80605372973855716}]
["V25",{"$f":"VLOOKUP(A134,Matrix_Rohdaten,$B$71,0)","v":"V25"},{"$f":"VLOOKUP(A134,Matrix_Rohdaten,$C$71,0)","v":3},{"$f":"VLOOKUP(A134,Matrix_Rohdaten,$D$71,0)","v":32},{"$f":"VLOOKUP(A134,Matrix_Rohdaten,$E$71,0)","v":199.29034539999998},{"$f":"VLOOKUP(A134,Matrix_Rohdaten,$F$71,0)","v":150},{"$f":"VLOOKUP(A134,Matrix_Rohdaten,$G$71,0)","v":23.980817369230767},{"$f":"VLOOKUP(A134,Matrix_Rohdaten,$H$71,0)/D134*D$137","v":45.202025000000027},{"$f":"VLOOKUP(A134,Matrix_Rohdaten,$I$71,0)/$D$137*D134","v":2.2108581002879051},{"$f":"IF(G138=G139,G138,E143*H134^E142+F143*H134^F142+G143*H134^G142)","v":0.99930304908338896},{"$f":"G134/J134","v":23.99754247845754},{"$f":"IF(L138=L139,L138,J143*H134^J142+K143*H134^K142+L143*H134^L142)","v":1.0000000000000004},{"$f":"K134*L134","v":23.99754247845755},{"$f":"1/K134*M134-1","v":0},{"$f":"I134*H134","v":99.935263120666448},null,1,{"$f":"$B$58","v":150},{"$f":"R140*R134^R139+S140*R134^S139+T140*R134^T139+U140*R134^U139","v":-8.3747745584611124},{"$f":"V140*R134^W140","v":1443.9534099660448},{"$f":"X140*R134^X139+Y140*R134^Y139+Z140*R134^Z139","v":2.3731037102962738},{"$f":"CONCATENATE($A$70, \" ; \",K132)","v":"HFBsf; HL; 4L; mit Edelstahlgitter ; q Sek [W/K] bei wok 200 kg/h"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A134,Matrix_Rohdaten,$AO$70,0)/$D$136*$D$137","v":45.202025000000027},{"$f":"K134","v":23.99754247845754},{"$f":"IF(AQ138=AQ139,AQ138,AO143*AO134^AO142+AP143*AO134^AP142+AQ143*AO134^AQ142)","v":0.80605372973855749},{"$f":"AP134*AQ134","v":19.343308619320165},{"$f":"1/M134*AR134","v":0.80605372973855705}]
["V26",{"$f":"VLOOKUP(A135,Matrix_Rohdaten,$B$71,0)","v":"V26"},{"$f":"VLOOKUP(A135,Matrix_Rohdaten,$C$71,0)","v":3},{"$f":"VLOOKUP(A135,Matrix_Rohdaten,$D$71,0)","v":32},{"$f":"VLOOKUP(A135,Matrix_Rohdaten,$E$71,0)","v":199.42056293846159},{"$f":"VLOOKUP(A135,Matrix_Rohdaten,$F$71,0)","v":250},{"$f":"VLOOKUP(A135,Matrix_Rohdaten,$G$71,0)","v":32.250682076923077},{"$f":"VLOOKUP(A135,Matrix_Rohdaten,$H$71,0)/D135*D$137","v":59.105739843749937},{"$f":"VLOOKUP(A135,Matrix_Rohdaten,$I$71,0)/$D$137*D135","v":2.3431316767795778},{"$f":"IF(G138=G139,G138,E143*H135^E142+F143*H135^F142+G143*H135^G142)","v":0.99930304908338896},{"$f":"G135/J135","v":32.273174895748618},{"$f":"IF(L138=L139,L138,J143*H135^J142+K143*H135^K142+L143*H135^L142)","v":1.0000000000000004},{"$f":"K135*L135","v":32.273174895748632},{"$f":"1/K135*M135-1","v":0},138.4925313073833,{"$f":"CONCATENATE(A132,\": Auslegung2\")","v":"Messreihe 5: Auslegung2"},2,"Primärdruck Soll [Pa]","q sek [W/K] Auslegung 2","V_Prim soll [m³/h] Auslegung 2","Induktionsverhältnis",{"$f":"CONCATENATE($A$70, \" ; \",M132)","v":"HFBsf; HL; 4L; mit Edelstahlgitter ; q Sek [W/K] bei w_soll 200 kg/h"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A135,Matrix_Rohdaten,$AO$70,0)/$D$136*$D$137","v":59.105739843749937},{"$f":"K135","v":32.273174895748618},{"$f":"IF(AQ138=AQ139,AQ138,AO143*AO135^AO142+AP143*AO135^AP142+AQ143*AO135^AQ142)","v":0.80605372973855749},{"$f":"AP135*AQ135","v":26.013912995222956},{"$f":"1/M135*AR135","v":0.80605372973855716}]
["V27",{"$f":"VLOOKUP(A136,Matrix_Rohdaten,$B$71,0)","v":"V27"},{"$f":"VLOOKUP(A136,Matrix_Rohdaten,$C$71,0)","v":3},{"$f":"VLOOKUP(A136,Matrix_Rohdaten,$D$71,0)","v":32},{"$f":"VLOOKUP(A136,Matrix_Rohdaten,$E$71,0)","v":199.2652703076923},{"$f":"VLOOKUP(A136,Matrix_Rohdaten,$F$71,0)","v":300},{"$f":"VLOOKUP(A136,Matrix_Rohdaten,$G$71,0)","v":34.81429476923077},{"$f":"VLOOKUP(A136,Matrix_Rohdaten,$H$71,0)/D136*D$137","v":64.799350781250041},{"$f":"VLOOKUP(A136,Matrix_Rohdaten,$I$71,0)/$D$137*D136","v":2.3342331729077923},{"$f":"IF(G138=G139,G138,E143*H136^E142+F143*H136^F142+G143*H136^G142)","v":0.99930304908338896},{"$f":"G136/J136","v":34.838575546391247},{"$f":"IF(L138=L139,L138,J143*H136^J142+K143*H136^K142+L143*H136^L142)","v":1.0000000000000004},{"$f":"K136*L136","v":34.838575546391262},{"$f":"1/K136*M136-1","v":0},151.25679417648232,null,2,{"$f":"$B$59","v":150},{"$f":"R143*R136^R142+S143*R136^S142+T143*R136^T142+U143*R136^U142","v":24.640234445271584},{"$f":"V143*R136^W143","v":44.996897409165456},{"$f":"X143*R136^X142+Y143*R136^Y142+Z143*R136^Z142","v":2.2188140665033873},{"$f":"CONCATENATE(\"im Mittel \", ROUND(AVERAGE(N133:N136)*100,0), \" % Kühlleistung bei \", ROUND($B$62,0), \" kg/h\")","v":"im Mittel 0 % Kühlleistung bei 200 kg/h"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A136,Matrix_Rohdaten,$AO$70,0)/$D$136*$D$137","v":64.799350781250041},{"$f":"K136","v":34.838575546391247},{"$f":"IF(AQ138=AQ139,AQ138,AO143*AO136^AO142+AP143*AO136^AP142+AQ143*AO136^AQ142)","v":0.80605372973855749},{"$f":"AP136*AQ136","v":28.081763757947169},{"$f":"1/M136*AR136","v":0.80605372973855716}]
[null,null,"Düsenanzahl HFBsf-Standard (2x25 Düsen je 6,8mm)",{"$f":"25+0","v":25},{"$f":"CONCATENATE(\"w_mess = \", ROUND(E138,0),\" kg/h\")","v":"w_mess = 199 kg/h"},"Faktor: Wassermenge zu Nennwassermenge [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa]","Primärvolumenstrom[m³/h]",{"$f":"CONCATENATE(\"w_soll = \", ROUND($B$62,0),\" kg/h\")","v":"w_soll = 200 kg/h"},"Faktor: Wassermenge zu Nennwassermenge  [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa]","Primärvolumenstrom[m³/h]",null,null,null,"Polynom  y =","axn+bx(n-1)+...+nx+m",null,null,"Umrechnung: Druck D Volumenstrom",null,"y =","axn+bx(n-1)+...+nx+m",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"CONCATENATE(\"w_soll = \", ROUND($B$63,0),\" kg/h\")","v":"w_soll = 100 kg/h"},"Faktor: Wassermenge zu Nennwassermenge  [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa]","Primärvolumenstrom[m³/h]"]
[null,null,null,null,{"$f":"AVERAGE(E133:E136)","v":199.19489139999999},{"$f":"E138/$B$64","v":0.99597445699999998},{"$f":"$B$66*F138^$B$65+$C$66*F138^$C$65+$D$66*F138^$D$65+$E$66*F138^$E$65+$F$66","v":0.99930304908338896},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607},{"$f":"$B$62","v":200},{"$f":"J138/$B$64","v":1},{"$f":"$B$66*K138^$B$65+$C$66*K138^$C$65+$D$66*K138^$D$65+$E$66*K138^$E$65+$F$66","v":1.0000000000000004},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607},null,null,null,"a =","b =","c =","m =","y =","mxb","a =","b =","m =",null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO138/$B$64","v":0.5},{"$f":"$B$66*AP138^$B$65+$C$66*AP138^$C$65+$D$66*AP138^$D$65+$E$66*AP138^$E$65+$F$66","v":0.80605372973855749},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607}]
[null,null,null,null,{"$f":"AVERAGE(E133:E136)","v":199.19489139999999},{"$f":"E139/$B$64","v":0.99597445699999998},{"$f":"IFERROR($B$67*F139^$B$65+$C$67*F139^$C$65+$D$67*F139^$D$65+$E$67*F139^$E$65+$F$67,G138)","v":0.99930304908338896},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857},{"$f":"$B$62","v":200},{"$f":"J139/$B$64","v":1},{"$f":"IFERROR($B$67*K139^$B$65+$C$67*K139^$C$65+$D$67*K139^$D$65+$E$67*K139^$E$65+$F$67,L138)","v":1.0000000000000004},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857},null,null,1,3,2,1,0,null,null,2,1,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO139/$B$64","v":0.5},{"$f":"IFERROR($B$67*AP139^$B$65+$C$67*AP139^$C$65+$D$67*AP139^$D$65+$E$67*AP139^$E$65+$F$67,AQ138)","v":0.80605372973855749},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857}]
[null,null,null,null,{"$f":"AVERAGE(E133:E136)","v":199.19489139999999},{"$f":"E140/$B$64","v":0.99597445699999998},{"$f":"IFERROR($B$68*F140^$B$65+$C$68*F140^$C$65+$D$68*F140^$D$65+$E$68*F140^$E$65+$F$68,G138)","v":0.99930304908338896},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857},{"$f":"$B$62","v":200},{"$f":"J140/$B$64","v":1},{"$f":"IFERROR($B$68*K140^$B$65+$C$68*K140^$C$65+$D$68*K140^$D$65+$E$68*K140^$E$65+$F$68,L138)","v":1.0000000000000004},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857},null,null,1,{"$f":"LINEST(M133:M136,H133:H136^{1,2,3},0,0)","v":-6.9429290013921192E-5},7.9298537722505332E-3,0.31684912908590612,0,{"$f":"INDEX(LOGEST(Auswertung_Leistung!F133:F136,LN(Auswertung_Leistung!H133:H136),,TRUE),1,2)","v":0.11664528105576454},{"$f":"LN(INDEX(LOGEST(F133:F136,LN(H133:H136),,TRUE),1,1))","v":1.8807510897220623},{"$f":"LINEST(I133:I136,$H$73:$H$76^{0,1,2},0,0)","v":-3.9112194532825748E-5},1.1926122182405293E-2,1.4642097599240593,null,null,"Für Vergleich mit \"ohne Schieber\"",null,null,"Akustik",null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO140/$B$64","v":0.5},{"$f":"IFERROR($B$68*AP140^$B$65+$C$68*AP140^$C$65+$D$68*AP140^$D$65+$E$68*AP140^$E$65+$F$68,AQ138)","v":0.80605372973855749},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857}]
[null,null,null,null,"a =","b =","m =",null,null,"a =","b =","m =",null,"Korrektur\nWassermenge",null,null,null,"a =","b =","c =","m =","y =","mxb","a =","b =","m =",null,null,null,null,null,"Druckverlust [Pa] → \nSchallleistung [dBA]",null,null,null,null,null,null,null,null,"a =","b =","m ="]
[null,null,null,null,2,1,0,null,null,2,1,0,"Auslegung 1",{"$f":"J143*P134^2+K143*P134+L143","v":0},null,null,2,3,2,1,0,null,null,2,1,0,null,null,"Umrechnung: Druck _Volumenstrom",null,null,null,null,null,null,null,null,null,null,null,2,1,0]
[null,null,null,null,{"$f":"LINEST(G138:G140,I138:I140^{0,1,2},0,0)","v":-1.2443954962003447E-4},2.2302719980005117E-2,0,null,null,{"$f":"LINEST(L138:L140,N138:N140^{0,1,2},0,0)","v":-1.245263383656661E-4},2.2318274722026722E-2,0,"Auslegung 2",{"$f":"J143*R136^2+K143*R136+L143","v":0.54589859507652116},null,null,2,{"$f":"LINEST(M133:M136,F133:F136^{1,2,3},0,0)","v":1.1934813121242958E-6},-8.5228473617651713E-4,0.2652576105388248,0,{"$f":"INDEX(LOGEST(Auswertung_Leistung!H133:H136,LN(Auswertung_Leistung!F133:F136),,TRUE),1,2)","v":3.1349733420374779},{"$f":"LN(INDEX(LOGEST(H133:H136,LN(F133:F136),,TRUE),1,1))","v":0.53166369409440295},{"$f":"LINEST(I133:I136,$F$73:$F$76^{0,1,2},0,0)","v":-6.238881607021443E-6},3.6193892523382555E-3,1.8162805148106314,null,null,"y =","mxb",null,"m","b",null,null,null,null,null,null,null,{"$f":"LINEST(AQ138:AQ140,AS138:AS140^{0,1,2},0,0)","v":-1.0037491949032032E-4},1.7989728581018466E-2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"CONCATENATE(\"H\",P145)","v":"H3"},{"$f":"$F$1","v":2},{"$f":"R142","v":3},2,1,0,null,null,{"$f":"X142","v":2},{"$f":"Y142","v":1},0,"V_Prim Min [m³/h]","V_Prim Max [m³/h]",null,null,null,"y = m∙LN(x) + b",null,null,null,null,null,null,null,null,"Korrekturfaktor Mittel"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"C133","v":3},{"$f":"$F$1","v":2},{"$f":"R143","v":1.1934813121242958E-6},-8.5228473617651713E-4,0.2652576105388248,0,{"$f":"IF(Q145=1,V140,V143)","v":3.1349733420374779},{"$f":"IF(Q145=1,W140,W143)","v":0.53166369409440295},{"$f":"X143","v":-6.238881607021443E-6},{"$f":"Y143","v":3.6193892523382555E-3},1.8162805148106314,{"$f":"V143*$K$2^W143","v":23.723945867037322},{"$f":"V143*$K$3^W143","v":65.621458991696059},{"$f":"V140","v":0.11664528105576454},{"$f":"W140","v":1.8807510897220623},"Schieberstellung 3",13.403868570620824,-34.747978990563283,null,null,null,null,null,null,null,{"$f":"AVERAGE(AS133:AS136)","v":0.80605372973855705}]
[]
["Messreihe 6","Messung (Kontrolle)","Schieberstellung","Anzahl Düsen","Wasser-\nmenge [kg/h]","Primärdruck [Pa]","spez. Kühlleistung q Sek [W/K]","Primärvolumenstrom [m³/h]","Induktionsverhältnis i [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok",{"$f":"CONCATENATE(\"q Sek [W/K] bei wok \", G$21, \" kg/h\")","v":"q Sek [W/K] bei wok 200 kg/h"},{"$f":"CONCATENATE(\"Korrektur bei \", ROUND(AVERAGE($B$62),0), \" kg/h (Mittelwert)\")","v":"Korrektur bei 200 kg/h (Mittelwert)"},{"$f":"CONCATENATE(\"q Sek [W/K] bei w_soll \", ROUND($B$62,0), \" kg/h\")","v":"q Sek [W/K] bei w_soll 200 kg/h"},{"$f":"CONCATENATE(\"q Sek Abweichung von Nennwassermenge bei \", $B$62, \" kg/h\")","v":"q Sek Abweichung von Nennwassermenge bei 200 kg/h"},"Sekundärvolumenstrom [m³/h]",null,null,"x - Achse","y - Achse","y - Achse","y - Achse",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Primärvolumenstrom [m³/h]",{"$f":"K147","v":"q Sek [W/K] bei wok 200 kg/h"},{"$f":"CONCATENATE(\"Korrektur bei \", ROUND(AVERAGE($B$63),0), \" kg/h (Mittelwert)\")","v":"Korrektur bei 100 kg/h (Mittelwert)"},{"$f":"CONCATENATE(\"q Sek [W/K] bei w_soll \", ROUND($B$63,0), \" kg/h\")","v":"q Sek [W/K] bei w_soll 100 kg/h"},"Korrektur kühlen heizen bei \ngleichem Wärmetauscher"]
["V28",{"$f":"VLOOKUP(A148,Matrix_Rohdaten,$B$71,0)","v":"V28"},{"$f":"VLOOKUP(A148,Matrix_Rohdaten,$C$71,0)","v":2.5},{"$f":"VLOOKUP(A148,Matrix_Rohdaten,$D$71,0)","v":17.25},{"$f":"VLOOKUP(A148,Matrix_Rohdaten,$E$71,0)","v":199.14518212307689},{"$f":"VLOOKUP(A148,Matrix_Rohdaten,$F$71,0)","v":50},{"$f":"VLOOKUP(A148,Matrix_Rohdaten,$G$71,0)","v":10.555556784615382},{"$f":"VLOOKUP(A148,Matrix_Rohdaten,$H$71,0)","v":31.660904000000027},{"$f":"VLOOKUP(A148,Matrix_Rohdaten,$I$71,0)","v":1.4086129993313252},{"$f":"IF(G153=G154,G153,E158*H148^E157+F158*H148^F157+G158*H148^G157)","v":0.99929482151910698},{"$f":"G148/J148","v":10.563005588850192},{"$f":"IF(L153=L154,L153,J158*H148^J157+K158*H148^K157+L158*H148^L157)","v":1.0000000000000004},{"$f":"K148*L148","v":10.563005588850197},{"$f":"1/K148*M148-1","v":0},{"$f":"I148*H148","v":44.597960944981189},{"$f":"CONCATENATE(A147,\": Auslegung1\")","v":"Messreihe 6: Auslegung1"},1,"V_Prim soll [m³/h]","q sek [W/K] Auslegung 1","Primärdruck [Pa]","Induktionsverhältnis","Titel für Diagramme:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A148,Matrix_Rohdaten,$AO$70,0)","v":31.660904000000027},{"$f":"K148","v":10.563005588850192},{"$f":"IF(AQ153=AQ154,AQ153,AO158*AO148^AO157+AP158*AO148^AP157+AQ158*AO148^AQ157)","v":0.80605372973855749},{"$f":"AP148*AQ148","v":8.5143500521419249},{"$f":"1/M148*AR148","v":0.80605372973855705}]
["V29",{"$f":"VLOOKUP(A149,Matrix_Rohdaten,$B$71,0)","v":"V29"},{"$f":"VLOOKUP(A149,Matrix_Rohdaten,$C$71,0)","v":2.5},{"$f":"VLOOKUP(A149,Matrix_Rohdaten,$D$71,0)","v":17.25},{"$f":"VLOOKUP(A149,Matrix_Rohdaten,$E$71,0)","v":199.20555646153838},{"$f":"VLOOKUP(A149,Matrix_Rohdaten,$F$71,0)","v":150},{"$f":"VLOOKUP(A149,Matrix_Rohdaten,$G$71,0)","v":22.394639061538459},{"$f":"VLOOKUP(A149,Matrix_Rohdaten,$H$71,0)","v":57.435316999999948},{"$f":"VLOOKUP(A149,Matrix_Rohdaten,$I$71,0)","v":1.658083364914184},{"$f":"IF(G153=G154,G153,E158*H149^E157+F158*H149^F157+G158*H149^G157)","v":0.99929482151910698},{"$f":"G149/J149","v":22.41044242328265},{"$f":"IF(L153=L154,L153,J158*H149^J157+K158*H149^K157+L158*H149^L157)","v":1.0000000000000004},{"$f":"K149*L149","v":22.41044242328266},{"$f":"1/K149*M149-1","v":0},{"$f":"I149*H149","v":95.232543676272741},null,1,{"$f":"$B$58","v":150},{"$f":"R155*R149^R154+S155*R149^S154+T155*R149^T154+U155*R149^U154","v":45.208088151675817},{"$f":"V155*R149^W155","v":922.1029509565127},{"$f":"X155*R149^X154+Y155*R149^Y154+Z155*R149^Z154","v":1.7355017032599127},{"$f":"CONCATENATE($A$70, \" ; \",K147)","v":"HFBsf; HL; 4L; mit Edelstahlgitter ; q Sek [W/K] bei wok 200 kg/h"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A149,Matrix_Rohdaten,$AO$70,0)","v":57.435316999999948},{"$f":"K149","v":22.41044242328265},{"$f":"IF(AQ153=AQ154,AQ153,AO158*AO149^AO157+AP158*AO149^AP157+AQ158*AO149^AQ157)","v":0.80605372973855749},{"$f":"AP149*AQ149","v":18.064020700378176},{"$f":"1/M149*AR149","v":0.80605372973855716}]
["V30",{"$f":"VLOOKUP(A150,Matrix_Rohdaten,$B$71,0)","v":"V30"},{"$f":"VLOOKUP(A150,Matrix_Rohdaten,$C$71,0)","v":2.5},{"$f":"VLOOKUP(A150,Matrix_Rohdaten,$D$71,0)","v":17.25},{"$f":"VLOOKUP(A150,Matrix_Rohdaten,$E$71,0)","v":199.12272516923073},{"$f":"VLOOKUP(A150,Matrix_Rohdaten,$F$71,0)","v":250},{"$f":"VLOOKUP(A150,Matrix_Rohdaten,$G$71,0)","v":29.43040924615385},{"$f":"VLOOKUP(A150,Matrix_Rohdaten,$H$71,0)","v":74.853723999999985},{"$f":"VLOOKUP(A150,Matrix_Rohdaten,$I$71,0)","v":1.6804284004923256},{"$f":"IF(G153=G154,G153,E158*H150^E157+F158*H150^F157+G158*H150^G157)","v":0.99929482151910698},{"$f":"G150/J150","v":29.451177582822215},{"$f":"IF(L153=L154,L153,J158*H150^J157+K158*H150^K157+L158*H150^L157)","v":1.0000000000000004},{"$f":"K150*L150","v":29.451177582822229},{"$f":"1/K150*M150-1","v":0},125.78632369221398,{"$f":"CONCATENATE(A147,\": Auslegung2\")","v":"Messreihe 6: Auslegung2"},2,"Primärdruck Soll [Pa]","q sek [W/K] Auslegung 2","V_Prim soll [m³/h] Auslegung 2","Induktionsverhältnis",{"$f":"CONCATENATE($A$70, \" ; \",M147)","v":"HFBsf; HL; 4L; mit Edelstahlgitter ; q Sek [W/K] bei w_soll 200 kg/h"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A150,Matrix_Rohdaten,$AO$70,0)","v":74.853723999999985},{"$f":"K150","v":29.451177582822215},{"$f":"IF(AQ153=AQ154,AQ153,AO158*AO150^AO157+AP158*AO150^AP157+AQ158*AO150^AQ157)","v":0.80605372973855749},{"$f":"AP150*AQ150","v":23.739231535826441},{"$f":"1/M150*AR150","v":0.80605372973855716}]
["V31",{"$f":"VLOOKUP(A151,Matrix_Rohdaten,$B$71,0)","v":"V31"},{"$f":"VLOOKUP(A151,Matrix_Rohdaten,$C$71,0)","v":2.5},{"$f":"VLOOKUP(A151,Matrix_Rohdaten,$D$71,0)","v":17.25},{"$f":"VLOOKUP(A151,Matrix_Rohdaten,$E$71,0)","v":199.26832221538459},{"$f":"VLOOKUP(A151,Matrix_Rohdaten,$F$71,0)","v":300},{"$f":"VLOOKUP(A151,Matrix_Rohdaten,$G$71,0)","v":33.207610430769236},{"$f":"VLOOKUP(A151,Matrix_Rohdaten,$H$71,0)","v":82.068952999999979},{"$f":"VLOOKUP(A151,Matrix_Rohdaten,$I$71,0)","v":1.757073347791404},{"$f":"IF(G153=G154,G153,E158*H151^E157+F158*H151^F157+G158*H151^G157)","v":0.99929482151910698},{"$f":"G151/J151","v":33.231044248070582},{"$f":"IF(L153=L154,L153,J158*H151^J157+K158*H151^K157+L158*H151^L157)","v":1.0000000000000004},{"$f":"K151*L151","v":33.231044248070596},{"$f":"1/K151*M151-1","v":0},144.20116999744536,null,2,{"$f":"$B$59","v":150},{"$f":"R158*R151^R157+S158*R151^S157+T158*R151^T157+U158*R151^U157","v":22.521918945582765},{"$f":"V158*R151^W158","v":57.007300381040082},{"$f":"X158*R151^X157+Y158*R151^Y157+Z158*R151^Z157","v":1.6278030778263899},{"$f":"CONCATENATE(\"im Mittel \", ROUND(AVERAGE(N148:N151)*100,0), \" % Kühlleistung bei \", ROUND($B$62,0), \" kg/h\")","v":"im Mittel 0 % Kühlleistung bei 200 kg/h"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A151,Matrix_Rohdaten,$AO$70,0)","v":82.068952999999979},{"$f":"K151","v":33.231044248070582},{"$f":"IF(AQ153=AQ154,AQ153,AO158*AO151^AO157+AP158*AO151^AP157+AQ158*AO151^AQ157)","v":0.80605372973855749},{"$f":"AP151*AQ151","v":26.786007159264329},{"$f":"1/M151*AR151","v":0.80605372973855716}]
[null,null,null,null,{"$f":"CONCATENATE(\"w_mess = \", ROUND(E153,0),\" kg/h\")","v":"w_mess = 199 kg/h"},"Faktor: Wassermenge zu Nennwassermenge [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa]","Primärvolumenstrom[m³/h]",{"$f":"CONCATENATE(\"w_soll = \", ROUND($B$62,0),\" kg/h\")","v":"w_soll = 200 kg/h"},"Faktor: Wassermenge zu Nennwassermenge  [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa]","Primärvolumenstrom[m³/h]",null,null,null,"Polynom  y =","axn+bx(n-1)+...+nx+m",null,null,"Umrechnung: Druck D Volumenstrom",null,"y =","axn+bx(n-1)+...+nx+m",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"CONCATENATE(\"w_soll = \", ROUND($B$63,0),\" kg/h\")","v":"w_soll = 100 kg/h"},"Faktor: Wassermenge zu Nennwassermenge  [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa]","Primärvolumenstrom[m³/h]"]
[null,null,null,null,{"$f":"AVERAGE(E148:E151)","v":199.18544649230765},{"$f":"E153/$B$64","v":0.99592723246153825},{"$f":"$B$66*F153^$B$65+$C$66*F153^$C$65+$D$66*F153^$D$65+$E$66*F153^$E$65+$F$66","v":0.99929482151910698},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607},{"$f":"$B$62","v":200},{"$f":"J153/$B$64","v":1},{"$f":"$B$66*K153^$B$65+$C$66*K153^$C$65+$D$66*K153^$D$65+$E$66*K153^$E$65+$F$66","v":1.0000000000000004},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607},null,null,null,"a =","b =","c =","m =","y =","mxb","a =","b =","m =",null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO153/$B$64","v":0.5},{"$f":"$B$66*AP153^$B$65+$C$66*AP153^$C$65+$D$66*AP153^$D$65+$E$66*AP153^$E$65+$F$66","v":0.80605372973855749},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607}]
[null,null,null,null,{"$f":"AVERAGE(E148:E151)","v":199.18544649230765},{"$f":"E154/$B$64","v":0.99592723246153825},{"$f":"IFERROR($B$67*F154^$B$65+$C$67*F154^$C$65+$D$67*F154^$D$65+$E$67*F154^$E$65+$F$67,G153)","v":0.99929482151910698},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857},{"$f":"$B$62","v":200},{"$f":"J154/$B$64","v":1},{"$f":"IFERROR($B$67*K154^$B$65+$C$67*K154^$C$65+$D$67*K154^$D$65+$E$67*K154^$E$65+$F$67,L153)","v":1.0000000000000004},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857},null,null,1,3,2,1,0,null,null,2,1,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO154/$B$64","v":0.5},{"$f":"IFERROR($B$67*AP154^$B$65+$C$67*AP154^$C$65+$D$67*AP154^$D$65+$E$67*AP154^$E$65+$F$67,AQ153)","v":0.80605372973855749},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857}]
[null,null,null,null,{"$f":"AVERAGE(E148:E151)","v":199.18544649230765},{"$f":"E155/$B$64","v":0.99592723246153825},{"$f":"IFERROR($B$68*F155^$B$65+$C$68*F155^$C$65+$D$68*F155^$D$65+$E$68*F155^$E$65+$F$68,G153)","v":0.99929482151910698},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857},{"$f":"$B$62","v":200},{"$f":"J155/$B$64","v":1},{"$f":"IFERROR($B$68*K155^$B$65+$C$68*K155^$C$65+$D$68*K155^$D$65+$E$68*K155^$E$65+$F$68,L153)","v":1.0000000000000004},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857},null,null,1,{"$f":"LINEST(M148:M151,H148:H151^{1,2,3},0,0)","v":-2.3330462461049644E-5},3.9369926932612343E-3,0.23577375572893727,0,{"$f":"INDEX(LOGEST(Auswertung_Leistung!F148:F151,LN(Auswertung_Leistung!H148:H151),,TRUE),1,2)","v":7.5862199311944364E-2},{"$f":"LN(INDEX(LOGEST(F148:F151,LN(H148:H151),,TRUE),1,1))","v":1.8771060109481925},{"$f":"LINEST(I148:I151,$H$73:$H$76^{0,1,2},0,0)","v":-4.4321383552403886E-5},1.228096701346963E-2,0.89058778116855564,null,null,"Für Vergleich mit \"ohne Schieber\"",null,null,"Akustik",null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO155/$B$64","v":0.5},{"$f":"IFERROR($B$68*AP155^$B$65+$C$68*AP155^$C$65+$D$68*AP155^$D$65+$E$68*AP155^$E$65+$F$68,AQ153)","v":0.80605372973855749},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857}]
[null,null,null,null,"a =","b =","m =",null,null,"a =","b =","m =",null,"Korrektur\nWassermenge",null,null,null,"a =","b =","c =","m =","y =","mxb","a =","b =","m =",null,null,null,null,null,"Druckverlust [Pa] → \nSchallleistung [dBA]",null,null,null,null,null,null,null,null,"a =","b =","m ="]
[null,null,null,null,2,1,0,null,null,2,1,0,"Auslegung 1",{"$f":"J158*P149^2+K158*P149+L158","v":0},null,null,2,3,2,1,0,null,null,2,1,0,null,null,"Umrechnung: Druck _Volumenstrom",null,null,null,null,null,null,null,null,null,null,null,2,1,0]
[null,null,null,null,{"$f":"LINEST(G153:G155,I153:I155^{0,1,2},0,0)","v":-1.2443852507162479E-4},2.2302536354969128E-2,0,null,null,{"$f":"LINEST(L153:L155,N153:N155^{0,1,2},0,0)","v":-1.245263383656661E-4},2.2318274722026722E-2,0,"Auslegung 2",{"$f":"J158*R151^2+K158*R151+L158","v":0.54589859507652116},null,null,2,{"$f":"LINEST(M148:M151,F148:F151^{1,2,3},0,0)","v":1.318233830942029E-6},-8.5472084690557692E-4,0.24869399214352597,0,{"$f":"INDEX(LOGEST(Auswertung_Leistung!H148:H151,LN(Auswertung_Leistung!F148:F151),,TRUE),1,2)","v":3.9521644378270393},{"$f":"LN(INDEX(LOGEST(H148:H151,LN(F148:F151),,TRUE),1,1))","v":0.53265021141261049},{"$f":"LINEST(I148:I151,$F$73:$F$76^{0,1,2},0,0)","v":-5.6030119535549684E-6},3.2216623143982589E-3,1.2706214996216378,null,null,"y =","mxb",null,"m","b",null,null,null,null,null,null,null,{"$f":"LINEST(AQ153:AQ155,AS153:AS155^{0,1,2},0,0)","v":-1.0037491949032032E-4},1.7989728581018466E-2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"CONCATENATE(\"H\",P160)","v":"H2,5"},{"$f":"$F$1","v":2},{"$f":"R157","v":3},2,1,0,null,null,{"$f":"X157","v":2},{"$f":"Y157","v":1},0,"V_Prim Min [m³/h]","V_Prim Max [m³/h]",null,null,null,"y = m∙LN(x) + b",null,null,null,null,null,null,null,null,"Korrekturfaktor Mittel"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"C148","v":2.5},{"$f":"$F$1","v":2},{"$f":"R158","v":1.318233830942029E-6},-8.5472084690557692E-4,0.24869399214352597,0,{"$f":"IF(Q160=1,V155,V158)","v":3.9521644378270393},{"$f":"IF(Q160=1,W155,W158)","v":0.53265021141261049},{"$f":"X158","v":-5.6030119535549684E-6},{"$f":"Y158","v":3.2216623143982589E-3},1.2706214996216378,{"$f":"V158*$K$2^W158","v":30.020574634206334},{"$f":"V158*$K$3^W158","v":83.195117726866584},{"$f":"V155","v":7.5862199311944364E-2},{"$f":"W155","v":1.8771060109481925},"Schieberstellung 2.2",14.000029494751457,-40.759609728616624,null,null,null,null,null,null,null,{"$f":"AVERAGE(AS148:AS151)","v":0.80605372973855705}]
[]
["Messreihe 7","Messung (Kontrolle)","Schieberstellung","Anzahl Düsen","Wasser-\nmenge [kg/h]","Primärdruck [Pa]","spez. Kühlleistung q Sek [W/K]","Primärvolumenstrom [m³/h]","Induktionsverhältnis i [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok",{"$f":"CONCATENATE(\"q Sek [W/K] bei wok \", G$21, \" kg/h\")","v":"q Sek [W/K] bei wok 200 kg/h"},{"$f":"CONCATENATE(\"Korrektur bei \", ROUND(AVERAGE($B$62),0), \" kg/h (Mittelwert)\")","v":"Korrektur bei 200 kg/h (Mittelwert)"},{"$f":"CONCATENATE(\"q Sek [W/K] bei w_soll \", ROUND($B$62,0), \" kg/h\")","v":"q Sek [W/K] bei w_soll 200 kg/h"},{"$f":"CONCATENATE(\"q Sek Abweichung von Nennwassermenge bei \", $B$62, \" kg/h\")","v":"q Sek Abweichung von Nennwassermenge bei 200 kg/h"},"Sekundärvolumenstrom [m³/h]",null,null,"x - Achse","y - Achse","y - Achse","y - Achse",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Primärvolumenstrom [m³/h]",{"$f":"K162","v":"q Sek [W/K] bei wok 200 kg/h"},{"$f":"CONCATENATE(\"Korrektur bei \", ROUND(AVERAGE($B$63),0), \" kg/h (Mittelwert)\")","v":"Korrektur bei 100 kg/h (Mittelwert)"},{"$f":"CONCATENATE(\"q Sek [W/K] bei w_soll \", ROUND($B$63,0), \" kg/h\")","v":"q Sek [W/K] bei w_soll 100 kg/h"},"Korrektur kühlen heizen bei \ngleichem Wärmetauscher"]
["V32",{"$f":"VLOOKUP(A163,Matrix_Rohdaten,$B$71,0)","v":"V32"},{"$f":"VLOOKUP(A163,Matrix_Rohdaten,$C$71,0)","v":2},{"$f":"VLOOKUP(A163,Matrix_Rohdaten,$D$71,0)","v":23},{"$f":"VLOOKUP(A163,Matrix_Rohdaten,$E$71,0)","v":199.03427481538461},{"$f":"VLOOKUP(A163,Matrix_Rohdaten,$F$71,0)","v":50},{"$f":"VLOOKUP(A163,Matrix_Rohdaten,$G$71,0)","v":7.2829364000000023},{"$f":"VLOOKUP(A163,Matrix_Rohdaten,$H$71,0)/D163*D$167","v":12.070105434782613},{"$f":"VLOOKUP(A163,Matrix_Rohdaten,$I$71,0)/$D$167*D163","v":3.5648253294680998},{"$f":"IF(G168=G169,G168,E173*H163^E172+F173*H163^F172+G173*H163^G172)","v":0.99918770487012609},{"$f":"G163/J163","v":7.2888571031272198},{"$f":"IF(L168=L169,L168,J173*H163^J172+K173*H163^K172+L173*H163^L172)","v":1.0000000000000004},{"$f":"K163*L163","v":7.2888571031272233},{"$f":"1/K163*M163-1","v":0},{"$f":"I163*H163","v":43.027817583263634},{"$f":"CONCATENATE(A162,\": Auslegung1\")","v":"Messreihe 7: Auslegung1"},1,"V_Prim soll [m³/h]","q sek [W/K] Auslegung 1","Primärdruck [Pa]","Induktionsverhältnis","Titel für Diagramme:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A163,Matrix_Rohdaten,$AO$70,0)/$D$166*$D$167","v":12.070105434782613},{"$f":"K163","v":7.2888571031272198},{"$f":"IF(AQ168=AQ169,AQ168,AO173*AO163^AO172+AP173*AO163^AP172+AQ173*AO163^AQ172)","v":0.80605372973855749},{"$f":"AP163*AQ163","v":5.8752104535070728},{"$f":"1/M163*AR163","v":0.80605372973855716}]
["V33",{"$f":"VLOOKUP(A164,Matrix_Rohdaten,$B$71,0)","v":"V33"},{"$f":"VLOOKUP(A164,Matrix_Rohdaten,$C$71,0)","v":2},{"$f":"VLOOKUP(A164,Matrix_Rohdaten,$D$71,0)","v":23},{"$f":"VLOOKUP(A164,Matrix_Rohdaten,$E$71,0)","v":199.20383052307699},{"$f":"VLOOKUP(A164,Matrix_Rohdaten,$F$71,0)","v":150},{"$f":"VLOOKUP(A164,Matrix_Rohdaten,$G$71,0)","v":13.477221030769231},{"$f":"VLOOKUP(A164,Matrix_Rohdaten,$H$71,0)/D164*D$167","v":22.418384239130464},{"$f":"VLOOKUP(A164,Matrix_Rohdaten,$I$71,0)/$D$167*D164","v":3.1280877485033529},{"$f":"IF(G168=G169,G168,E173*H164^E172+F173*H164^F172+G173*H164^G172)","v":0.99918770487012609},{"$f":"G164/J164","v":13.488177411591542},{"$f":"IF(L168=L169,L168,J173*H164^J172+K173*H164^K172+L173*H164^L172)","v":1.0000000000000004},{"$f":"K164*L164","v":13.488177411591547},{"$f":"1/K164*M164-1","v":0},{"$f":"I164*H164","v":70.12667307966467},null,1,{"$f":"$B$58","v":150},{"$f":"R170*R164^R169+S170*R164^S169+T170*R164^T169+U170*R164^U169","v":568.10532785840678},{"$f":"V170*R164^W170","v":4528.7122901445373},{"$f":"X170*R164^X169+Y170*R164^Y169+Z170*R164^Z169","v":4.8855347728836254},{"$f":"CONCATENATE($A$70, \" ; \",K162)","v":"HFBsf; HL; 4L; mit Edelstahlgitter ; q Sek [W/K] bei wok 200 kg/h"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A164,Matrix_Rohdaten,$AO$70,0)/$D$166*$D$167","v":22.418384239130464},{"$f":"K164","v":13.488177411591542},{"$f":"IF(AQ168=AQ169,AQ168,AO173*AO164^AO172+AP173*AO164^AP172+AQ173*AO164^AQ172)","v":0.80605372973855749},{"$f":"AP164*AQ164","v":10.872195709988725},{"$f":"1/M164*AR164","v":0.80605372973855727}]
["V34",{"$f":"VLOOKUP(A165,Matrix_Rohdaten,$B$71,0)","v":"V34"},{"$f":"VLOOKUP(A165,Matrix_Rohdaten,$C$71,0)","v":2},{"$f":"VLOOKUP(A165,Matrix_Rohdaten,$D$71,0)","v":23},{"$f":"VLOOKUP(A165,Matrix_Rohdaten,$E$71,0)","v":199.23695481538468},{"$f":"VLOOKUP(A165,Matrix_Rohdaten,$F$71,0)","v":250},{"$f":"VLOOKUP(A165,Matrix_Rohdaten,$G$71,0)","v":18.991304753846158},{"$f":"VLOOKUP(A165,Matrix_Rohdaten,$H$71,0)/D165*D$167","v":29.674134782608654},{"$f":"VLOOKUP(A165,Matrix_Rohdaten,$I$71,0)/$D$167*D165","v":3.6059711243620054},{"$f":"IF(G168=G169,G168,E173*H165^E172+F173*H165^F172+G173*H165^G172)","v":0.99918770487012609},{"$f":"G165/J165","v":19.006743839301585},{"$f":"IF(L168=L169,L168,J173*H165^J172+K173*H165^K172+L173*H165^L172)","v":1.0000000000000004},{"$f":"K165*L165","v":19.006743839301592},{"$f":"1/K165*M165-1","v":0},107.00407316651302,{"$f":"CONCATENATE(A162,\": Auslegung2\")","v":"Messreihe 7: Auslegung2"},2,"Primärdruck Soll [Pa]","q sek [W/K] Auslegung 2","V_Prim soll [m³/h] Auslegung 2","Induktionsverhältnis",{"$f":"CONCATENATE($A$70, \" ; \",M162)","v":"HFBsf; HL; 4L; mit Edelstahlgitter ; q Sek [W/K] bei w_soll 200 kg/h"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A165,Matrix_Rohdaten,$AO$70,0)/$D$166*$D$167","v":29.674134782608654},{"$f":"K165","v":19.006743839301585},{"$f":"IF(AQ168=AQ169,AQ168,AO173*AO165^AO172+AP173*AO165^AP172+AQ173*AO165^AQ172)","v":0.80605372973855749},{"$f":"AP165*AQ165","v":15.320456761854393},{"$f":"1/M165*AR165","v":0.80605372973855727}]
["V35",{"$f":"VLOOKUP(A166,Matrix_Rohdaten,$B$71,0)","v":"V35"},{"$f":"VLOOKUP(A166,Matrix_Rohdaten,$C$71,0)","v":2},{"$f":"VLOOKUP(A166,Matrix_Rohdaten,$D$71,0)","v":23},{"$f":"VLOOKUP(A166,Matrix_Rohdaten,$E$71,0)","v":198.77536586153849},{"$f":"VLOOKUP(A166,Matrix_Rohdaten,$F$71,0)","v":300},{"$f":"VLOOKUP(A166,Matrix_Rohdaten,$G$71,0)","v":21.329262000000011},{"$f":"VLOOKUP(A166,Matrix_Rohdaten,$H$71,0)/D166*D$167","v":32.862561413043508},{"$f":"VLOOKUP(A166,Matrix_Rohdaten,$I$71,0)/$D$167*D166","v":3.8385945892221911},{"$f":"IF(G168=G169,G168,E173*H166^E172+F173*H166^F172+G173*H166^G172)","v":0.99918770487012609},{"$f":"G166/J166","v":21.346601740633286},{"$f":"IF(L168=L169,L168,J173*H166^J172+K173*H166^K172+L173*H166^L172)","v":1.0000000000000004},{"$f":"K166*L166","v":21.346601740633297},{"$f":"1/K166*M166-1","v":0},126.14605042809077,null,2,{"$f":"$B$59","v":150},{"$f":"R173*R166^R172+S173*R166^S172+T173*R166^T172+U173*R166^U172","v":14.077825879340136},{"$f":"V173*R166^W173","v":22.333419421843232},{"$f":"X173*R166^X172+Y173*R166^Y172+Z173*R166^Z172","v":3.1982990212426312},{"$f":"CONCATENATE(\"im Mittel \", ROUND(AVERAGE(N163:N166)*100,0), \" % Kühlleistung bei \", ROUND($B$62,0), \" kg/h\")","v":"im Mittel 0 % Kühlleistung bei 200 kg/h"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A166,Matrix_Rohdaten,$AO$70,0)/$D$166*$D$167","v":32.862561413043508},{"$f":"K166","v":21.346601740633286},{"$f":"IF(AQ168=AQ169,AQ168,AO173*AO166^AO172+AP173*AO166^AP172+AQ173*AO166^AQ172)","v":0.80605372973855749},{"$f":"AP166*AQ166","v":17.206507950281043},{"$f":"1/M166*AR166","v":0.80605372973855705}]
[null,null,"Düsenanzahl HFBsf-Standard (2x25 Düsen je 6,8mm)",{"$f":"25/2+0","v":12.5},{"$f":"CONCATENATE(\"w_mess = \", ROUND(E168,0),\" kg/h\")","v":"w_mess = 199 kg/h"},"Faktor: Wassermenge zu Nennwassermenge [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa]","Primärvolumenstrom[m³/h]",{"$f":"CONCATENATE(\"w_soll = \", ROUND($B$62,0),\" kg/h\")","v":"w_soll = 200 kg/h"},"Faktor: Wassermenge zu Nennwassermenge  [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa]","Primärvolumenstrom[m³/h]",null,null,null,"Polynom  y =","axn+bx(n-1)+...+nx+m",null,null,"Umrechnung: Druck D Volumenstrom",null,"y =","axn+bx(n-1)+...+nx+m",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"CONCATENATE(\"w_soll = \", ROUND($B$63,0),\" kg/h\")","v":"w_soll = 100 kg/h"},"Faktor: Wassermenge zu Nennwassermenge  [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa]","Primärvolumenstrom[m³/h]"]
[null,null,null,null,{"$f":"AVERAGE(E163:E166)","v":199.06260650384618},{"$f":"E168/$B$64","v":0.99531303251923087},{"$f":"$B$66*F168^$B$65+$C$66*F168^$C$65+$D$66*F168^$D$65+$E$66*F168^$E$65+$F$66","v":0.99918770487012609},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607},{"$f":"$B$62","v":200},{"$f":"J168/$B$64","v":1},{"$f":"$B$66*K168^$B$65+$C$66*K168^$C$65+$D$66*K168^$D$65+$E$66*K168^$E$65+$F$66","v":1.0000000000000004},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607},null,null,null,"a =","b =","c =","m =","y =","mxb","a =","b =","m =",null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO168/$B$64","v":0.5},{"$f":"$B$66*AP168^$B$65+$C$66*AP168^$C$65+$D$66*AP168^$D$65+$E$66*AP168^$E$65+$F$66","v":0.80605372973855749},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607}]
[null,null,null,null,{"$f":"AVERAGE(E163:E166)","v":199.06260650384618},{"$f":"E169/$B$64","v":0.99531303251923087},{"$f":"IFERROR($B$67*F169^$B$65+$C$67*F169^$C$65+$D$67*F169^$D$65+$E$67*F169^$E$65+$F$67,G168)","v":0.99918770487012609},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857},{"$f":"$B$62","v":200},{"$f":"J169/$B$64","v":1},{"$f":"IFERROR($B$67*K169^$B$65+$C$67*K169^$C$65+$D$67*K169^$D$65+$E$67*K169^$E$65+$F$67,L168)","v":1.0000000000000004},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857},null,null,1,3,2,1,0,null,null,2,1,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO169/$B$64","v":0.5},{"$f":"IFERROR($B$67*AP169^$B$65+$C$67*AP169^$C$65+$D$67*AP169^$D$65+$E$67*AP169^$E$65+$F$67,AQ168)","v":0.80605372973855749},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857}]
[null,null,null,null,{"$f":"AVERAGE(E163:E166)","v":199.06260650384618},{"$f":"E170/$B$64","v":0.99531303251923087},{"$f":"IFERROR($B$68*F170^$B$65+$C$68*F170^$C$65+$D$68*F170^$D$65+$E$68*F170^$E$65+$F$68,G168)","v":0.99918770487012609},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857},{"$f":"$B$62","v":200},{"$f":"J170/$B$64","v":1},{"$f":"IFERROR($B$68*K170^$B$65+$C$68*K170^$C$65+$D$68*K170^$D$65+$E$68*K170^$E$65+$F$68,L168)","v":1.0000000000000004},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857},null,null,1,{"$f":"LINEST(M163:M166,H163:H166^{1,2,3},0,0)","v":1.7574282688176813E-4},-5.3739661111814304E-3,0.63925016422680969,0,{"$f":"INDEX(LOGEST(Auswertung_Leistung!F163:F166,LN(Auswertung_Leistung!H163:H166),,TRUE),1,2)","v":0.57887890593354574},{"$f":"LN(INDEX(LOGEST(F163:F166,LN(H163:H166),,TRUE),1,1))","v":1.7891653165650234},{"$f":"LINEST(I163:I166,$H$73:$H$76^{0,1,2},0,0)","v":4.0289547401197096E-4},-6.7944150779383108E-2,6.0120092245217442,null,null,"Für Vergleich mit \"ohne Schieber\"",null,null,"Akustik",null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO170/$B$64","v":0.5},{"$f":"IFERROR($B$68*AP170^$B$65+$C$68*AP170^$C$65+$D$68*AP170^$D$65+$E$68*AP170^$E$65+$F$68,AQ168)","v":0.80605372973855749},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857}]
[null,null,null,null,"a =","b =","m =",null,null,"a =","b =","m =",null,"Korrektur\nWassermenge",null,null,null,"a =","b =","c =","m =","y =","mxb","a =","b =","m =",null,null,null,null,null,"Druckverlust [Pa] → \nSchallleistung [dBA]",null,null,null,null,null,null,null,null,"a =","b =","m ="]
[null,null,null,null,2,1,0,null,null,2,1,0,"Auslegung 1",{"$f":"J173*P164^2+K173*P164+L173","v":0},null,null,2,3,2,1,0,null,null,2,1,0,null,null,"Umrechnung: Druck _Volumenstrom",null,null,null,null,null,null,null,null,null,null,null,2,1,0]
[null,null,null,null,{"$f":"LINEST(G168:G170,I168:I170^{0,1,2},0,0)","v":-1.2442518622752936E-4},2.2300145696168092E-2,0,null,null,{"$f":"LINEST(L168:L170,N168:N170^{0,1,2},0,0)","v":-1.245263383656661E-4},2.2318274722026722E-2,0,"Auslegung 2",{"$f":"J173*R166^2+K173*R166+L173","v":0.54589859507652116},null,null,2,{"$f":"LINEST(M163:M166,F163:F166^{1,2,3},0,0)","v":1.0681682729256487E-6},-6.267466257264873E-4,0.16383038024708024,0,{"$f":"INDEX(LOGEST(Auswertung_Leistung!H163:H166,LN(Auswertung_Leistung!F163:F166),,TRUE),1,2)","v":1.3574790846713629},{"$f":"LN(INDEX(LOGEST(H163:H166,LN(F163:F166),,TRUE),1,1))","v":0.5589021462522783},{"$f":"LINEST(I163:I166,$F$73:$F$76^{0,1,2},0,0)","v":3.2390906020706945E-5},-9.9328104681782377E-3,3.9594252060034605,null,null,"y =","mxb",null,"m","b",null,null,null,null,null,null,null,{"$f":"LINEST(AQ168:AQ170,AS168:AS170^{0,1,2},0,0)","v":-1.0037491949032032E-4},1.7989728581018466E-2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"CONCATENATE(\"H\",P175)","v":"H2"},{"$f":"$F$1","v":2},{"$f":"R172","v":3},2,1,0,null,null,{"$f":"X172","v":2},{"$f":"Y172","v":1},0,"V_Prim Min [m³/h]","V_Prim Max [m³/h]",null,null,null,"y = m∙LN(x) + b",null,null,null,null,null,null,null,null,"Korrekturfaktor Mittel"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"C163","v":2},{"$f":"$F$1","v":2},{"$f":"R173","v":1.0681682729256487E-6},-6.267466257264873E-4,0.16383038024708024,0,{"$f":"IF(Q175=1,V170,V173)","v":1.3574790846713629},{"$f":"IF(Q175=1,W170,W173)","v":0.5589021462522783},{"$f":"X173","v":3.2390906020706945E-5},{"$f":"Y173","v":-9.9328104681782377E-3},3.9594252060034605,{"$f":"V173*$K$2^W173","v":11.395074504856202},{"$f":"V173*$K$3^W173","v":33.205777924310411},{"$f":"V170","v":0.57887890593354574},{"$f":"W170","v":1.7891653165650234},"Schieberstellung 2",16.830784568547649,-57.07445881371855,null,null,null,null,null,null,null,{"$f":"AVERAGE(AS163:AS166)","v":0.80605372973855727}]
[]
["Messreihe 8","Messung (Kontrolle)","Schieberstellung","Anzahl Düsen","Wasser-\nmenge [kg/h]","Primärdruck [Pa]","spez. Kühlleistung q Sek [W/K]","Primärvolumenstrom [m³/h]","Induktionsverhältnis i [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok",{"$f":"CONCATENATE(\"q Sek [W/K] bei wok \", G$21, \" kg/h\")","v":"q Sek [W/K] bei wok 200 kg/h"},{"$f":"CONCATENATE(\"Korrektur bei \", ROUND(AVERAGE($B$62),0), \" kg/h (Mittelwert)\")","v":"Korrektur bei 200 kg/h (Mittelwert)"},{"$f":"CONCATENATE(\"q Sek [W/K] bei w_soll \", ROUND($B$62,0), \" kg/h\")","v":"q Sek [W/K] bei w_soll 200 kg/h"},{"$f":"CONCATENATE(\"q Sek Abweichung von Nennwassermenge bei \", $B$62, \" kg/h\")","v":"q Sek Abweichung von Nennwassermenge bei 200 kg/h"},"Sekundärvolumenstrom [m³/h]",null,null,"x - Achse","y - Achse","y - Achse","y - Achse",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Primärvolumenstrom [m³/h]",{"$f":"K177","v":"q Sek [W/K] bei wok 200 kg/h"},{"$f":"CONCATENATE(\"Korrektur bei \", ROUND(AVERAGE($B$63),0), \" kg/h (Mittelwert)\")","v":"Korrektur bei 100 kg/h (Mittelwert)"},{"$f":"CONCATENATE(\"q Sek [W/K] bei w_soll \", ROUND($B$63,0), \" kg/h\")","v":"q Sek [W/K] bei w_soll 100 kg/h"},"Korrektur kühlen heizen bei \ngleichem Wärmetauscher"]
["V36",{"$f":"VLOOKUP(A178,Matrix_Rohdaten,$B$71,0)","v":"V36"},{"$f":"VLOOKUP(A178,Matrix_Rohdaten,$C$71,0)","v":1.5},{"$f":"VLOOKUP(A178,Matrix_Rohdaten,$D$71,0)","v":11.5},{"$f":"VLOOKUP(A178,Matrix_Rohdaten,$E$71,0)","v":198.84523673846158},{"$f":"VLOOKUP(A178,Matrix_Rohdaten,$F$71,0)","v":50},{"$f":"VLOOKUP(A178,Matrix_Rohdaten,$G$71,0)","v":4.5136230923076939},{"$f":"VLOOKUP(A178,Matrix_Rohdaten,$H$71,0)","v":11.034172000000009},{"$f":"VLOOKUP(A178,Matrix_Rohdaten,$I$71,0)","v":5.4043682907550155},{"$f":"IF(G183=G184,G183,E188*H178^E187+F188*H178^F187+G188*H178^G187)","v":0.99975653868072889},{"$f":"G178/J178","v":4.5147222525434412},{"$f":"IF(L183=L184,L183,J188*H178^J187+K188*H178^K187+L188*H178^L187)","v":1.0000000000000004},{"$f":"K178*L178","v":4.5147222525434429},{"$f":"1/K178*M178-1","v":0},{"$f":"I178*H178","v":59.632729271536896},{"$f":"CONCATENATE(A177,\": Auslegung1\")","v":"Messreihe 8: Auslegung1"},1,"V_Prim soll [m³/h]","q sek [W/K] Auslegung 1","Primärdruck [Pa]","Induktionsverhältnis","Titel für Diagramme:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A178,Matrix_Rohdaten,$AO$70,0)","v":11.034172000000009},{"$f":"K178","v":4.5147222525434412},{"$f":"IF(AQ183=AQ184,AQ183,AO188*AO178^AO187+AP188*AO178^AP187+AQ188*AO178^AQ187)","v":0.80605372973855749},{"$f":"AP178*AQ178","v":3.6391087103963025},{"$f":"1/M178*AR178","v":0.80605372973855716}]
["V37",{"$f":"VLOOKUP(A179,Matrix_Rohdaten,$B$71,0)","v":"V37"},{"$f":"VLOOKUP(A179,Matrix_Rohdaten,$C$71,0)","v":1.5},{"$f":"VLOOKUP(A179,Matrix_Rohdaten,$D$71,0)","v":11.5},{"$f":"VLOOKUP(A179,Matrix_Rohdaten,$E$71,0)","v":198.94390980000003},{"$f":"VLOOKUP(A179,Matrix_Rohdaten,$F$71,0)","v":150},{"$f":"VLOOKUP(A179,Matrix_Rohdaten,$G$71,0)","v":4.721667292307691},{"$f":"VLOOKUP(A179,Matrix_Rohdaten,$H$71,0)","v":23.312959000000021},{"$f":"VLOOKUP(A179,Matrix_Rohdaten,$I$71,0)","v":3.9071050119395019},{"$f":"IF(G183=G184,G183,E188*H179^E187+F188*H179^F187+G188*H179^G187)","v":0.99975653868072889},{"$f":"G179/J179","v":4.7228171155933296},{"$f":"IF(L183=L184,L183,J188*H179^J187+K188*H179^K187+L188*H179^L187)","v":1.0000000000000004},{"$f":"K179*L179","v":4.7228171155933314},{"$f":"1/K179*M179-1","v":0},{"$f":"I179*H179","v":91.0861789520402},null,1,{"$f":"$B$58","v":150},{"$f":"R185*R179^R184+S185*R179^S184+T185*R179^T184+U185*R179^U184","v":1161.2723262077679},{"$f":"V185*R179^W185","v":2861.0108401870289},{"$f":"X185*R179^X184+Y185*R179^Y184+Z185*R179^Z184","v":21.763035621449163},{"$f":"CONCATENATE($A$70, \" ; \",K177)","v":"HFBsf; HL; 4L; mit Edelstahlgitter ; q Sek [W/K] bei wok 200 kg/h"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A179,Matrix_Rohdaten,$AO$70,0)","v":23.312959000000021},{"$f":"K179","v":4.7228171155933296},{"$f":"IF(AQ183=AQ184,AQ183,AO188*AO179^AO187+AP188*AO179^AP187+AQ188*AO179^AQ187)","v":0.80605372973855749},{"$f":"AP179*AQ179","v":3.8068443508970993},{"$f":"1/M179*AR179","v":0.80605372973855716}]
["V38",{"$f":"VLOOKUP(A180,Matrix_Rohdaten,$B$71,0)","v":"V38"},{"$f":"VLOOKUP(A180,Matrix_Rohdaten,$C$71,0)","v":1.5},{"$f":"VLOOKUP(A180,Matrix_Rohdaten,$D$71,0)","v":11.5},{"$f":"VLOOKUP(A180,Matrix_Rohdaten,$E$71,0)","v":198.76488416923075},{"$f":"VLOOKUP(A180,Matrix_Rohdaten,$F$71,0)","v":250},{"$f":"VLOOKUP(A180,Matrix_Rohdaten,$G$71,0)","v":5.8311037384615387},{"$f":"VLOOKUP(A180,Matrix_Rohdaten,$H$71,0)","v":31.223653000000009},{"$f":"VLOOKUP(A180,Matrix_Rohdaten,$I$71,0)","v":13.459946017162652},{"$f":"IF(G183=G184,G183,E188*H180^E187+F188*H180^F187+G188*H180^G187)","v":0.99975653868072889},{"$f":"G180/J180","v":5.8325237323841046},{"$f":"IF(L183=L184,L183,J188*H180^J187+K188*H180^K187+L188*H180^L187)","v":1.0000000000000004},{"$f":"K180*L180","v":5.8325237323841073},{"$f":"1/K180*M180-1","v":0},420.26868383861881,{"$f":"CONCATENATE(A177,\": Auslegung2\")","v":"Messreihe 8: Auslegung2"},2,"Primärdruck Soll [Pa]","q sek [W/K] Auslegung 2","V_Prim soll [m³/h] Auslegung 2","Induktionsverhältnis",{"$f":"CONCATENATE($A$70, \" ; \",M177)","v":"HFBsf; HL; 4L; mit Edelstahlgitter ; q Sek [W/K] bei w_soll 200 kg/h"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A180,Matrix_Rohdaten,$AO$70,0)","v":31.223653000000009},{"$f":"K180","v":5.8325237323841046},{"$f":"IF(AQ183=AQ184,AQ183,AO188*AO180^AO187+AP188*AO180^AP187+AQ188*AO180^AQ187)","v":0.80605372973855749},{"$f":"AP180*AQ180","v":4.7013275082768597},{"$f":"1/M180*AR180","v":0.80605372973855716}]
["V39",{"$f":"VLOOKUP(A181,Matrix_Rohdaten,$B$71,0)","v":"V39"},{"$f":"VLOOKUP(A181,Matrix_Rohdaten,$C$71,0)","v":1.5},{"$f":"VLOOKUP(A181,Matrix_Rohdaten,$D$71,0)","v":11.5},{"$f":"VLOOKUP(A181,Matrix_Rohdaten,$E$71,0)","v":202.31644723076928},{"$f":"VLOOKUP(A181,Matrix_Rohdaten,$F$71,0)","v":300},{"$f":"VLOOKUP(A181,Matrix_Rohdaten,$G$71,0)","v":6.1112054307692301},{"$f":"VLOOKUP(A181,Matrix_Rohdaten,$H$71,0)","v":34.648263000000028},{"$f":"VLOOKUP(A181,Matrix_Rohdaten,$I$71,0)","v":11.353720866780604},{"$f":"IF(G183=G184,G183,E188*H181^E187+F188*H181^F187+G188*H181^G187)","v":0.99975653868072889},{"$f":"G181/J181","v":6.1126936352259627},{"$f":"IF(L183=L184,L183,J188*H181^J187+K188*H181^K187+L188*H181^L187)","v":1.0000000000000004},{"$f":"K181*L181","v":6.1126936352259653},{"$f":"1/K181*M181-1","v":0},393.38670662080267,null,2,{"$f":"$B$59","v":150},{"$f":"R188*R181^R187+S188*R181^S187+T188*R181^T187+U188*R181^U187","v":5.4942656108275294},{"$f":"V188*R181^W188","v":22.583547405470053},{"$f":"X188*R181^X187+Y188*R181^Y187+Z188*R181^Z187","v":6.1234738078205293},{"$f":"CONCATENATE(\"im Mittel \", ROUND(AVERAGE(N178:N181)*100,0), \" % Kühlleistung bei \", ROUND($B$62,0), \" kg/h\")","v":"im Mittel 0 % Kühlleistung bei 200 kg/h"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(A181,Matrix_Rohdaten,$AO$70,0)","v":34.648263000000028},{"$f":"K181","v":6.1126936352259627},{"$f":"IF(AQ183=AQ184,AQ183,AO188*AO181^AO187+AP188*AO181^AP187+AQ188*AO181^AQ187)","v":0.80605372973855749},{"$f":"AP181*AQ181","v":4.9271595034230282},{"$f":"1/M181*AR181","v":0.80605372973855705}]
[null,null,null,null,{"$f":"CONCATENATE(\"w_mess = \", ROUND(E183,0),\" kg/h\")","v":"w_mess = 200 kg/h"},"Faktor: Wassermenge zu Nennwassermenge [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa]","Primärvolumenstrom[m³/h]",{"$f":"CONCATENATE(\"w_soll = \", ROUND($B$62,0),\" kg/h\")","v":"w_soll = 200 kg/h"},"Faktor: Wassermenge zu Nennwassermenge  [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa]","Primärvolumenstrom[m³/h]",null,null,null,"Polynom  y =","axn+bx(n-1)+...+nx+m",null,null,"Umrechnung: Druck D Volumenstrom",null,"y =","axn+bx(n-1)+...+nx+m",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"CONCATENATE(\"w_soll = \", ROUND($B$63,0),\" kg/h\")","v":"w_soll = 100 kg/h"},"Faktor: Wassermenge zu Nennwassermenge  [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa]","Primärvolumenstrom[m³/h]"]
[null,null,null,null,{"$f":"AVERAGE(E178:E181)","v":199.71761948461543},{"$f":"E183/$B$64","v":0.99858809742307708},{"$f":"$B$66*F183^$B$65+$C$66*F183^$C$65+$D$66*F183^$D$65+$E$66*F183^$E$65+$F$66","v":0.99975653868072889},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607},{"$f":"$B$62","v":200},{"$f":"J183/$B$64","v":1},{"$f":"$B$66*K183^$B$65+$C$66*K183^$C$65+$D$66*K183^$D$65+$E$66*K183^$E$65+$F$66","v":1.0000000000000004},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607},null,null,null,"a =","b =","c =","m =","y =","mxb","a =","b =","m =",null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO183/$B$64","v":0.5},{"$f":"$B$66*AP183^$B$65+$C$66*AP183^$C$65+$D$66*AP183^$D$65+$E$66*AP183^$E$65+$F$66","v":0.80605372973855749},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607}]
[null,null,null,null,{"$f":"AVERAGE(E178:E181)","v":199.71761948461543},{"$f":"E184/$B$64","v":0.99858809742307708},{"$f":"IFERROR($B$67*F184^$B$65+$C$67*F184^$C$65+$D$67*F184^$D$65+$E$67*F184^$E$65+$F$67,G183)","v":0.99975653868072889},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857},{"$f":"$B$62","v":200},{"$f":"J184/$B$64","v":1},{"$f":"IFERROR($B$67*K184^$B$65+$C$67*K184^$C$65+$D$67*K184^$D$65+$E$67*K184^$E$65+$F$67,L183)","v":1.0000000000000004},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857},null,null,1,3,2,1,0,null,null,2,1,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO184/$B$64","v":0.5},{"$f":"IFERROR($B$67*AP184^$B$65+$C$67*AP184^$C$65+$D$67*AP184^$D$65+$E$67*AP184^$E$65+$F$67,AQ183)","v":0.80605372973855749},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857}]
[null,null,null,null,{"$f":"AVERAGE(E178:E181)","v":199.71761948461543},{"$f":"E185/$B$64","v":0.99858809742307708},{"$f":"IFERROR($B$68*F185^$B$65+$C$68*F185^$C$65+$D$68*F185^$D$65+$E$68*F185^$E$65+$F$68,G183)","v":0.99975653868072889},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857},{"$f":"$B$62","v":200},{"$f":"J185/$B$64","v":1},{"$f":"IFERROR($B$68*K185^$B$65+$C$68*K185^$C$65+$D$68*K185^$D$65+$E$68*K185^$E$65+$F$68,L183)","v":1.0000000000000004},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857},null,null,1,{"$f":"LINEST(M178:M181,H178:H181^{1,2,3},0,0)","v":5.3856793475036391E-4},-3.3904788373610974E-2,0.70975523221024484,0,{"$f":"INDEX(LOGEST(Auswertung_Leistung!F178:F181,LN(Auswertung_Leistung!H178:H181),,TRUE),1,2)","v":1.1698017697233125},{"$f":"LN(INDEX(LOGEST(F178:F181,LN(H178:H181),,TRUE),1,1))","v":1.5571071365576725},{"$f":"LINEST(I178:I181,$H$73:$H$76^{0,1,2},0,0)","v":2.6272092145806E-3},-0.36071483791900688,16.758053981236699,null,null,"Für Vergleich mit \"ohne Schieber\"",null,null,"Akustik",null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO185/$B$64","v":0.5},{"$f":"IFERROR($B$68*AP185^$B$65+$C$68*AP185^$C$65+$D$68*AP185^$D$65+$E$68*AP185^$E$65+$F$68,AQ183)","v":0.80605372973855749},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857}]
[null,null,null,null,"a =","b =","m =",null,null,"a =","b =","m =",null,"Korrektur\nWassermenge",null,null,null,"a =","b =","c =","m =","y =","mxb","a =","b =","m =",null,null,null,null,null,"Druckverlust [Pa] → \nSchallleistung [dBA]",null,null,null,null,null,null,null,null,"a =","b =","m ="]
[null,null,null,null,2,1,0,null,null,2,1,0,"Auslegung 1",{"$f":"J188*P179^2+K188*P179+L188","v":0},null,null,2,3,2,1,0,null,null,2,1,0,null,null,"Umrechnung: Druck _Volumenstrom",null,null,null,null,null,null,null,null,null,null,null,2,1,0]
[null,null,null,null,{"$f":"LINEST(G183:G185,I183:I185^{0,1,2},0,0)","v":-1.2449602101903887E-4},2.2312841085418613E-2,0,null,null,{"$f":"LINEST(L183:L185,N183:N185^{0,1,2},0,0)","v":-1.245263383656661E-4},2.2318274722026722E-2,0,"Auslegung 2",{"$f":"J188*R181^2+K188*R181+L188","v":0.54589859507652116},null,null,2,{"$f":"LINEST(M178:M181,F178:F181^{1,2,3},0,0)","v":1.1852188836156399E-6},-6.3484312403449172E-4,0.10518748112933873,0,{"$f":"INDEX(LOGEST(Auswertung_Leistung!H178:H181,LN(Auswertung_Leistung!F178:F181),,TRUE),1,2)","v":0.90942895781418287},{"$f":"LN(INDEX(LOGEST(H178:H181,LN(F178:F181),,TRUE),1,1))","v":0.64106841888285515},{"$f":"LINEST(I178:I181,$F$73:$F$76^{0,1,2},0,0)","v":1.3139514298453762E-4},-1.2438867038609282E-2,5.0329131464598253,null,null,"y =","mxb",null,"m","b",null,null,null,null,null,null,null,{"$f":"LINEST(AQ183:AQ185,AS183:AS185^{0,1,2},0,0)","v":-1.0037491949032032E-4},1.7989728581018466E-2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"CONCATENATE(\"H\",P190)","v":"H1,5"},{"$f":"$F$1","v":2},{"$f":"R187","v":3},2,1,0,null,null,{"$f":"X187","v":2},{"$f":"Y187","v":1},0,"V_Prim Min [m³/h]","V_Prim Max [m³/h]",null,null,null,"y = m∙LN(x) + b",null,null,null,null,null,null,null,null,"Korrekturfaktor Mittel"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"C178","v":1.5},{"$f":"$F$1","v":2},{"$f":"R188","v":1.1852188836156399E-6},-6.3484312403449172E-4,0.10518748112933873,0,{"$f":"IF(Q190=1,V185,V188)","v":0.90942895781418287},{"$f":"IF(Q190=1,W185,W188)","v":0.64106841888285515},{"$f":"X188","v":1.3139514298453762E-4},{"$f":"Y188","v":-1.2438867038609282E-2},5.0329131464598253,{"$f":"V188*$K$2^W188","v":10.437370764005138},{"$f":"V188*$K$3^W188","v":35.593848600878445},{"$f":"V185","v":1.1698017697233125},{"$f":"W185","v":1.5571071365576725},"Schieberstellung 1.2",15.084279285984852,-48.764869762899565,null,null,null,null,null,null,null,{"$f":"AVERAGE(AS178:AS181)","v":0.80605372973855716}]
[]
["Messreihe 9","Messung (Kontrolle)","Schieberstellung","Anzahl Düsen","Wasser-\nmenge [kg/h]","Primärdruck [Pa]","spez. Kühlleistung q Sek [W/K]","Primärvolumenstrom [m³/h]","Induktionsverhältnis i [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok",{"$f":"CONCATENATE(\"q Sek [W/K] bei wok \", G$21, \" kg/h\")","v":"q Sek [W/K] bei wok 200 kg/h"},{"$f":"CONCATENATE(\"Korrektur bei \", ROUND(AVERAGE($B$62),0), \" kg/h (Mittelwert)\")","v":"Korrektur bei 200 kg/h (Mittelwert)"},{"$f":"CONCATENATE(\"q Sek [W/K] bei w_soll \", ROUND($B$62,0), \" kg/h\")","v":"q Sek [W/K] bei w_soll 200 kg/h"},{"$f":"CONCATENATE(\"q Sek Abweichung von Nennwassermenge bei \", $B$62, \" kg/h\")","v":"q Sek Abweichung von Nennwassermenge bei 200 kg/h"},"Sekundärvolumenstrom [m³/h]",null,null,"x - Achse","y - Achse","y - Achse","y - Achse",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Primärvolumenstrom [m³/h]",{"$f":"K192","v":"q Sek [W/K] bei wok 200 kg/h"},{"$f":"CONCATENATE(\"Korrektur bei \", ROUND(AVERAGE($B$63),0), \" kg/h (Mittelwert)\")","v":"Korrektur bei 100 kg/h (Mittelwert)"},{"$f":"CONCATENATE(\"q Sek [W/K] bei w_soll \", ROUND($B$63,0), \" kg/h\")","v":"q Sek [W/K] bei w_soll 100 kg/h"},"Korrektur kühlen heizen bei \ngleichem Wärmetauscher"]
["V40",{"$f":"VLOOKUP(A193,Matrix_Rohdaten,$B$71,0)","v":"V40"},{"$f":"VLOOKUP(A193,Matrix_Rohdaten,$C$71,0)","v":1},{"$f":"VLOOKUP(A193,Matrix_Rohdaten,$D$71,0)","v":0},{"$f":"VLOOKUP(A193,Matrix_Rohdaten,$E$71,0)","v":202.2512661230769},{"$f":"VLOOKUP(A193,Matrix_Rohdaten,$F$71,0)","v":50},{"$f":"VLOOKUP(A193,Matrix_Rohdaten,$G$71,0)","v":4.6370206769230764},{"$f":"H163/D163*$D$197","v":0.52478719281663533},{"$f":"VLOOKUP(A193,Matrix_Rohdaten,$I$71,0)/$D$197*D193","v":0},{"$f":"IF(G198=G199,G198,E203*H193^E202+F203*H193^F202+G203*H193^G202)","v":1.0019291941188604},{"$f":"G193/J193","v":4.6280921886911095},{"$f":"IF(L198=L199,L198,J203*H193^J202+K203*H193^K202+L203*H193^L202)","v":1.0000000000000004},{"$f":"K193*L193","v":4.6280921886911113},{"$f":"1/K193*M193-1","v":0},{"$f":"I193*H193","v":0},{"$f":"CONCATENATE(A192,\": Auslegung1\")","v":"Messreihe 9: Auslegung1"},1,"V_Prim soll [m³/h]","q sek [W/K] Auslegung 1","Primärdruck [Pa]","Induktionsverhältnis","Titel für Diagramme:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"H193","v":0.52478719281663533},{"$f":"K193","v":4.6280921886911095},{"$f":"IF(AQ198=AQ199,AQ198,AO203*AO193^AO202+AP203*AO193^AP202+AQ203*AO193^AQ202)","v":0.80605372973855749},{"$f":"AP193*AQ193","v":3.7304909702683524},{"$f":"1/M193*AR193","v":0.80605372973855716}]
["V41",{"$f":"VLOOKUP(A194,Matrix_Rohdaten,$B$71,0)","v":"V41"},{"$f":"VLOOKUP(A194,Matrix_Rohdaten,$C$71,0)","v":1},{"$f":"VLOOKUP(A194,Matrix_Rohdaten,$D$71,0)","v":0},{"$f":"VLOOKUP(A194,Matrix_Rohdaten,$E$71,0)","v":202.34788846153842},{"$f":"VLOOKUP(A194,Matrix_Rohdaten,$F$71,0)","v":150},{"$f":"VLOOKUP(A194,Matrix_Rohdaten,$G$71,0)","v":5.0486205692307697},{"$f":"H164/D164*$D$197","v":0.97471235822306368},{"$f":"VLOOKUP(A194,Matrix_Rohdaten,$I$71,0)/$D$197*D194","v":0},{"$f":"IF(G198=G199,G198,E203*H194^E202+F203*H194^F202+G203*H194^G202)","v":1.0019291941188604},{"$f":"G194/J194","v":5.0388995538459618},{"$f":"IF(L198=L199,L198,J203*H194^J202+K203*H194^K202+L203*H194^L202)","v":1.0000000000000004},{"$f":"K194*L194","v":5.0388995538459644},{"$f":"1/K194*M194-1","v":0},{"$f":"I194*H194","v":0},null,1,{"$f":"$B$58","v":150},{"$f":"R200*R194^R199+S200*R194^S199+T200*R194^T199+U200*R194^U199","v":18421217.593419481},{"$f":"V200*R194^W200","v":674977.5727115284},{"$f":"X200*R194^X199+Y200*R194^Y199+Z200*R194^Z199","v":0},{"$f":"CONCATENATE($A$70, \" ; \",K192)","v":"HFBsf; HL; 4L; mit Edelstahlgitter ; q Sek [W/K] bei wok 200 kg/h"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"H194","v":0.97471235822306368},{"$f":"K194","v":5.0388995538459618},{"$f":"IF(AQ198=AQ199,AQ198,AO203*AO194^AO202+AP203*AO194^AP202+AQ203*AO194^AQ202)","v":0.80605372973855749},{"$f":"AP194*AQ194","v":4.0616237791554912},{"$f":"1/M194*AR194","v":0.80605372973855716}]
["V42",{"$f":"VLOOKUP(A195,Matrix_Rohdaten,$B$71,0)","v":"V42"},{"$f":"VLOOKUP(A195,Matrix_Rohdaten,$C$71,0)","v":1},{"$f":"VLOOKUP(A195,Matrix_Rohdaten,$D$71,0)","v":0},{"$f":"VLOOKUP(A195,Matrix_Rohdaten,$E$71,0)","v":202.26438781538459},{"$f":"VLOOKUP(A195,Matrix_Rohdaten,$F$71,0)","v":250},{"$f":"VLOOKUP(A195,Matrix_Rohdaten,$G$71,0)","v":6.2036659076923089},1.290179773156898,{"$f":"VLOOKUP(A195,Matrix_Rohdaten,$I$71,0)/$D$197*D195","v":0},{"$f":"IF(G198=G199,G198,E203*H195^E202+F203*H195^F202+G203*H195^G202)","v":1.0019291941188604},{"$f":"G195/J195","v":6.1917208761923339},{"$f":"IF(L198=L199,L198,J203*H195^J202+K203*H195^K202+L203*H195^L202)","v":1.0000000000000004},{"$f":"K195*L195","v":6.1917208761923366},{"$f":"1/K195*M195-1","v":0},0,{"$f":"CONCATENATE(A192,\": Auslegung2\")","v":"Messreihe 9: Auslegung2"},2,"Primärdruck Soll [Pa]","q sek [W/K] Auslegung 2","V_Prim soll [m³/h] Auslegung 2","Induktionsverhältnis",{"$f":"CONCATENATE($A$70, \" ; \",M192)","v":"HFBsf; HL; 4L; mit Edelstahlgitter ; q Sek [W/K] bei w_soll 200 kg/h"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.290179773156898,{"$f":"K195","v":6.1917208761923339},{"$f":"IF(AQ198=AQ199,AQ198,AO203*AO195^AO202+AP203*AO195^AP202+AQ203*AO195^AQ202)","v":0.80605372973855749},{"$f":"AP195*AQ195","v":4.9908597057549198},{"$f":"1/M195*AR195","v":0.80605372973855716}]
["V42",{"$f":"VLOOKUP(A196,Matrix_Rohdaten,$B$71,0)","v":"V42"},{"$f":"VLOOKUP(A196,Matrix_Rohdaten,$C$71,0)","v":1},{"$f":"VLOOKUP(A196,Matrix_Rohdaten,$D$71,0)","v":0},{"$f":"VLOOKUP(A196,Matrix_Rohdaten,$E$71,0)","v":202.26438781538459},{"$f":"VLOOKUP(A196,Matrix_Rohdaten,$F$71,0)","v":250},{"$f":"VLOOKUP(A196,Matrix_Rohdaten,$G$71,0)","v":6.2036659076923089},{"$f":"H166/D166*$D$197","v":1.4288070179584134},{"$f":"VLOOKUP(A196,Matrix_Rohdaten,$I$71,0)/$D$197*D196","v":0},{"$f":"IF(G198=G199,G198,E203*H196^E202+F203*H196^F202+G203*H196^G202)","v":1.0019291941188604},{"$f":"G196/J196","v":6.1917208761923339},{"$f":"IF(L198=L199,L198,J203*H196^J202+K203*H196^K202+L203*H196^L202)","v":1.0000000000000004},{"$f":"K196*L196","v":6.1917208761923366},{"$f":"1/K196*M196-1","v":0},0,null,2,{"$f":"$B$59","v":150},{"$f":"R203*R196^R202+S203*R196^S202+T203*R196^T202+U203*R196^U202","v":5.0388995538459618},{"$f":"V203*R196^W203","v":0.99667446261545201},{"$f":"X203*R196^X202+Y203*R196^Y202+Z203*R196^Z202","v":0},{"$f":"CONCATENATE(\"im Mittel \", ROUND(AVERAGE(N193:N196)*100,0), \" % Kühlleistung bei \", ROUND($B$62,0), \" kg/h\")","v":"im Mittel 0 % Kühlleistung bei 200 kg/h"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.4288070179584134,{"$f":"K196","v":6.1917208761923339},{"$f":"IF(AQ198=AQ199,AQ198,AO203*AO196^AO202+AP203*AO196^AP202+AQ203*AO196^AQ202)","v":0.80605372973855749},{"$f":"AP196*AQ196","v":4.9908597057549198},{"$f":"1/M196*AR196","v":0.80605372973855716}]
[null,null,"Düsenanzahl HFBsf-Standard (2x25 Düsen je 6,8mm)",{"$f":"1+0","v":1},{"$f":"CONCATENATE(\"w_mess = \", ROUND(E198,0),\" kg/h\")","v":"w_mess = 202 kg/h"},"Faktor: Wassermenge zu Nennwassermenge [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa]","Primärvolumenstrom[m³/h]",{"$f":"CONCATENATE(\"w_soll = \", ROUND($B$62,0),\" kg/h\")","v":"w_soll = 200 kg/h"},"Faktor: Wassermenge zu Nennwassermenge  [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa]","Primärvolumenstrom[m³/h]",null,null,null,"Polynom  y =","axn+bx(n-1)+...+nx+m",null,null,"Umrechnung: Druck D Volumenstrom",null,"y =","axn+bx(n-1)+...+nx+m",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"CONCATENATE(\"w_soll = \", ROUND($B$63,0),\" kg/h\")","v":"w_soll = 100 kg/h"},"Faktor: Wassermenge zu Nennwassermenge  [-]","Kühlleistung Korrekturfaktor für \nw_soll ≠ w_ok [-]","Primärdruck [Pa]","Primärvolumenstrom[m³/h]"]
[null,null,null,null,{"$f":"AVERAGE(E193:E196)","v":202.28198255384612},{"$f":"E198/$B$64","v":1.0114099127692306},{"$f":"$B$66*F198^$B$65+$C$66*F198^$C$65+$D$66*F198^$D$65+$E$66*F198^$E$65+$F$66","v":1.0019291941188604},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607},{"$f":"$B$62","v":200},{"$f":"J198/$B$64","v":1},{"$f":"$B$66*K198^$B$65+$C$66*K198^$C$65+$D$66*K198^$D$65+$E$66*K198^$E$65+$F$66","v":1.0000000000000004},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607},null,null,null,"a =","b =","c =","m =","y =","mxb","a =","b =","m =",null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO198/$B$64","v":0.5},{"$f":"$B$66*AP198^$B$65+$C$66*AP198^$C$65+$D$66*AP198^$D$65+$E$66*AP198^$E$65+$F$66","v":0.80605372973855749},{"$f":"$G$66","v":150},{"$f":"$H$66","v":89.589565162337607}]
[null,null,null,null,{"$f":"AVERAGE(E193:E196)","v":202.28198255384612},{"$f":"E199/$B$64","v":1.0114099127692306},{"$f":"IFERROR($B$67*F199^$B$65+$C$67*F199^$C$65+$D$67*F199^$D$65+$E$67*F199^$E$65+$F$67,G198)","v":1.0019291941188604},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857},{"$f":"$B$62","v":200},{"$f":"J199/$B$64","v":1},{"$f":"IFERROR($B$67*K199^$B$65+$C$67*K199^$C$65+$D$67*K199^$D$65+$E$67*K199^$E$65+$F$67,L198)","v":1.0000000000000004},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857},null,null,1,3,2,1,0,null,null,2,1,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO199/$B$64","v":0.5},{"$f":"IFERROR($B$67*AP199^$B$65+$C$67*AP199^$C$65+$D$67*AP199^$D$65+$E$67*AP199^$E$65+$F$67,AQ198)","v":0.80605372973855749},{"$f":"$G$67","v":150},{"$f":"$H$67","v":89.635769935064857}]
[null,null,null,null,{"$f":"AVERAGE(E193:E196)","v":202.28198255384612},{"$f":"E200/$B$64","v":1.0114099127692306},{"$f":"IFERROR($B$68*F200^$B$65+$C$68*F200^$C$65+$D$68*F200^$D$65+$E$68*F200^$E$65+$F$68,G198)","v":1.0019291941188604},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857},{"$f":"$B$62","v":200},{"$f":"J200/$B$64","v":1},{"$f":"IFERROR($B$68*K200^$B$65+$C$68*K200^$C$65+$D$68*K200^$D$65+$E$68*K200^$E$65+$F$68,L198)","v":1.0000000000000004},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857},null,null,1,{"$f":"LINEST(M193:M196,H193:H196^{1,2,3},0,0)","v":5.5606163636211319},-15.473170930547775,15.224747569913953,0,{"$f":"INDEX(LOGEST(Auswertung_Leistung!F193:F196,LN(Auswertung_Leistung!H193:H196),,TRUE),1,2)","v":150.81260622900083},{"$f":"LN(INDEX(LOGEST(F193:F196,LN(H193:H196),,TRUE),1,1))","v":1.6777107497390498},{"$f":"LINEST(I193:I196,$H$73:$H$76^{0,1,2},0,0)","v":0},0,0,null,null,"Für Vergleich mit \"ohne Schieber\"",null,null,"Akustik",null,null,null,null,null,null,null,null,{"$f":"$B$63","v":100},{"$f":"AO200/$B$64","v":0.5},{"$f":"IFERROR($B$68*AP200^$B$65+$C$68*AP200^$C$65+$D$68*AP200^$D$65+$E$68*AP200^$E$65+$F$68,AQ198)","v":0.80605372973855749},{"$f":"$G$68","v":150},{"$f":"$H$68","v":89.635769935064857}]
[null,null,null,null,"a =","b =","m =",null,null,"a =","b =","m =",null,"Korrektur\nWassermenge",null,null,null,"a =","b =","c =","m =","y =","mxb","a =","b =","m =",null,null,null,null,null,"Druckverlust [Pa] → \nSchallleistung [dBA]",null,null,null,null,null,null,null,null,"a =","b =","m ="]
[null,null,null,null,2,1,0,null,null,2,1,0,"Auslegung 1",{"$f":"J203*P194^2+K203*P194+L203","v":0},null,null,2,3,2,1,0,null,null,2,1,0,null,null,"Umrechnung: Druck _Volumenstrom",null,null,null,null,null,null,null,null,null,null,null,2,1,0]
[null,null,null,null,{"$f":"LINEST(G198:G200,I198:I200^{0,1,2},0,0)","v":-1.2476657384531266E-4},2.2361331006366097E-2,0,null,null,{"$f":"LINEST(L198:L200,N198:N200^{0,1,2},0,0)","v":-1.245263383656661E-4},2.2318274722026722E-2,0,"Auslegung 2",{"$f":"J203*R196^2+K203*R196+L203","v":0.54589859507652116},null,null,2,{"$f":"LINEST(M193:M196,F193:F196^{1,2,3},0,0)","v":2.5071699946989425E-6},-1.0911257997549479E-3,0.14085020877482238,0,{"$f":"INDEX(LOGEST(Auswertung_Leistung!H193:H196,LN(Auswertung_Leistung!F193:F196),,TRUE),1,2)","v":5.1763215932067716E-2},{"$f":"LN(INDEX(LOGEST(H193:H196,LN(F193:F196),,TRUE),1,1))","v":0.59029329540744668},{"$f":"LINEST(I193:I196,$F$73:$F$76^{0,1,2},0,0)","v":0},0,0,null,null,"y =","mxb",null,"m","b",null,null,null,null,null,null,null,{"$f":"LINEST(AQ198:AQ200,AS198:AS200^{0,1,2},0,0)","v":-1.0037491949032032E-4},1.7989728581018466E-2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"CONCATENATE(\"H\",P205)","v":"H1"},{"$f":"$F$1","v":2},{"$f":"R202","v":3},2,1,0,null,null,{"$f":"X202","v":2},{"$f":"Y202","v":1},0,"V_Prim Min [m³/h]","V_Prim Max [m³/h]",null,null,null,"y = m∙LN(x) + b",null,null,null,null,null,null,null,null,"Korrekturfaktor Mittel"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"C193","v":1},{"$f":"$F$1","v":2},{"$f":"R203","v":2.5071699946989425E-6},-1.0911257997549479E-3,0.14085020877482238,0,{"$f":"IF(Q205=1,V200,V203)","v":5.1763215932067716E-2},{"$f":"IF(Q205=1,W200,W203)","v":0.59029329540744668},{"$f":"X203","v":0},{"$f":"Y203","v":0},0,{"$f":"V203*$K$2^W203","v":0.48966776252032507},{"$f":"V203*$K$3^W203","v":1.5152587103055677},{"$f":"V200","v":150.81260622900083},{"$f":"W200","v":1.6777107497390498},"Schieberstellung 1",12.555952471013207,-31.782369286247885,null,null,null,null,null,null,null,{"$f":"AVERAGE(AS193:AS196)","v":0.80605372973855716}]
[]
[]
[]
["BG","WT bzw. Laufradlänge","Verhältnis"]
["Baugröße 800",{"$f":"VLOOKUP(A210,A212:C215,2,0)","v":820},{"$f":"VLOOKUP(A210,A212:C215,3,0)","v":1}]
[null,null,null,null,null,null,null,"DpK, Messung=",{"$f":"H44*J224^I44","v":28.201307810721179},"kPa","2- Leiter Druckverlust Wasserseitig"]
["Baugröße 630",590,{"$f":"B212/$B$210","v":0.71951219512195119},null,null,null,"manuell einstellen","mit = 1 ; ohne = 2 Eurocoil Korrektur",2," -","aus VKB Auslegetool"]
["Baugröße 800",820,{"$f":"B213/$B$210","v":1},null,null,null,null,"Korrekturfaktor",{"$f":"IF(I212=2,1,I219/I211)","v":1}]
["Baugröße 1000",980,{"$f":"B214/$B$210","v":1.1951219512195121},"WT-Länge von 1020 mm korrigiert, da nicht 62 Düsen, sondern 60 Düsen auf BG1000",null,null,null,"2L = 1 ; 4L = 2",{"$f":"C351","v":2}]
["Baugröße 1200",1200,{"$f":"B215/$B$210","v":1.4634146341463414},"nicht vorhanden"]
[null,null,null,null,null,null,null,null,null,null,null,null,"4 - Leiter","4 - Leiter","2 - Leiter (aus VKB Auslegetool)","2 - Leiter (aus VKB Auslegetool)"]
[null,null,null,null,null,null,null,null,null,null,null,null,"kühlen","heizen","kühlen","heizen"]
[null,null,null,null,null,null,null,null,"DpK, Eurocoil =","Verhältnis","DpK, Eurocoil =","Verhältnis","DpK, Auslegung =","DpH, Auslegung =","DpK, Auslegung =","DpH, Auslegung ="]
[null,null,null,null,null,null,null,{"$f":"A210","v":"Baugröße 800"},{"$f":"'BG;WT2,5;k'!G2","v":22},{"$f":"'BG;WT2,5;k'!H2","v":1},{"$f":"'BG;WT2,5;h'!G2","v":2},{"$f":"'BG;WT2,5;h'!H2","v":1},{"$f":"H44*B3^I44*I213","v":28.201307810721179},{"$f":"H44*B4^I44*I213","v":7.9656023504001645},{"$f":"O221","v":4.2482909095097838},{"$f":"P221","v":1.3031051123704902}]
["Grenzwerte für Auslegung",null,null,null,null,null,null,{"$f":"A212","v":"Baugröße 630"},{"$f":"'BG;WT2,5;k'!G3","v":18},{"$f":"'BG;WT2,5;k'!H3","v":0.81818181818181823},{"$f":"'BG;WT2,5;h'!G3","v":1},{"$f":"'BG;WT2,5;h'!H3","v":0.5},{"$f":"$M$219*J220","v":23.073797299680965},{"$f":"(1.3/(100^1.802884))*B4^1.802884","v":1.3},{"$f":"((7/(300^1.757224))*B3^1.757224)","v":3.4329403193568822},{"$f":"((7/(300^1.757224))*B4^1.757224)","v":1.0155214949854232}]
[null,null,null,null,null,null,null,{"$f":"A213","v":"Baugröße 800"},{"$f":"'BG;WT2,5;k'!G4","v":22},{"$f":"'BG;WT2,5;k'!H4","v":1},{"$f":"'BG;WT2,5;h'!G4","v":2},{"$f":"'BG;WT2,5;h'!H4","v":1},{"$f":"$M$219*J221","v":28.201307810721179},{"$f":"((1.6/(100^1.788496))*B4^1.788496)","v":1.6},{"$f":"((8.45/(300^1.704291))*B3^1.7049291)","v":4.2482909095097838},{"$f":"((8.45/(300^1.704291))*B4^1.7049291)","v":1.3031051123704902}]
[null,null,null,null,null,null,null,"Baugröße 1000",{"$f":"'BG;WT2,5;k'!G5","v":26},{"$f":"'BG;WT2,5;k'!H5","v":1.1818181818181819},{"$f":"'BG;WT2,5;h'!G5","v":2},{"$f":"'BG;WT2,5;h'!H5","v":1},{"$f":"$M$219*J222","v":33.328818321761396},{"$f":"((1.8/(100^1.769775))*B4^1.769775)","v":1.8},{"$f":"((9.85/(300^1.775618))*B3^1.775618)","v":4.7947439659182631},{"$f":"((9.85/(300^1.775618))*B4^1.775618)","v":1.4003969055470078}]
[null,null,null,null,null,null,null,"Baugröße 1200",{"$f":"'BG;WT2,5;k'!G6","v":29},{"$f":"'BG;WT2,5;k'!H6","v":1.3181818181818181},{"$f":"'BG;WT2,5;h'!G6","v":2},{"$f":"'BG;WT2,5;h'!H6","v":1},{"$f":"$M$219*J223","v":37.174451205041549},{"$f":"N221*J223","v":2.1090909090909089},{"$f":"O221*J223","v":5.6000198352628967},{"$f":"P221*J223","v":1.7177294663065552}]
[null,null,null,null,null,null,null,null,{"$f":"'BG;WT2,5;k'!G7","v":"Wassermenge ="},{"$f":"'BG;WT2,5;k'!H7","v":200},{"$f":"'BG;WT2,5;h'!G7","v":"Wassermenge ="},{"$f":"'BG;WT2,5;h'!H7","v":100}]
["Grenzen der Messung",null,null,"Grenzenerweiterung der Auslegung",null,null,null,null,null,"kg/h",null,"kg/h"]
["kühlen",null,null,"kühlen",null,null,null,null,null,null,null,null,null,null,null,null,"Heizen"]
["Primärdruck [Pa]","Primärvolumenstrom [m³/h]","Wasser-Massenstrom [kg/h]","Primärdruck [Pa]",null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'BG;WT2,5;h'!I1","v":"Polynom 6 Ordnung - BG;WT2,5;h"},{"$f":"'BG;WT2,5;h'!J1","v":6},{"$f":"'BG;WT2,5;h'!K1","v":5},{"$f":"'BG;WT2,5;h'!L1","v":4},{"$f":"'BG;WT2,5;h'!M1","v":3},{"$f":"'BG;WT2,5;h'!N1","v":2},{"$f":"'BG;WT2,5;h'!O1","v":1},{"$f":"'BG;WT2,5;h'!P1","v":0}]
[null,null,50,{"$f":"K2","v":45},null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'BG;WT2,5;h'!I3","v":"BG 630"},{"$f":"'BG;WT2,5;h'!J3","v":-1.0632921310143854E-15},{"$f":"'BG;WT2,5;h'!K3","v":3.5858514113277551E-12},{"$f":"'BG;WT2,5;h'!L3","v":-4.7665713730329927E-9},{"$f":"'BG;WT2,5;h'!M3","v":3.1844233640596841E-6},{"$f":"'BG;WT2,5;h'!N3","v":-1.1456303236966005E-3},{"$f":"'BG;WT2,5;h'!O3","v":0.2418965836022402},{"$f":"'BG;WT2,5;h'!P3","v":0}]
[null,null,300,{"$f":"K3","v":305},null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'BG;WT2,5;h'!I4","v":"BG 800"},{"$f":"'BG;WT2,5;h'!J4","v":-1.1272515986343666E-15},{"$f":"'BG;WT2,5;h'!K4","v":3.805556241997797E-12},{"$f":"'BG;WT2,5;h'!L4","v":-5.0700197601788311E-9},{"$f":"'BG;WT2,5;h'!M4","v":3.4046035050996859E-6},{"$f":"'BG;WT2,5;h'!N4","v":-1.240901202992864E-3},{"$f":"'BG;WT2,5;h'!O4","v":0.27137689994379355},{"$f":"'BG;WT2,5;h'!P4","v":0}]
[null,null,null,null,null,null,null,{"$f":"IF($I$214=2,M216,N216)","v":"4 - Leiter"},{"$f":"IF($I$214=2,M216,N216)","v":"4 - Leiter"},null,null,null,null,null,null,null,{"$f":"'BG;WT2,5;h'!I5","v":"BG 1000"},{"$f":"'BG;WT2,5;h'!J5","v":-1.0533899171333763E-15},{"$f":"'BG;WT2,5;h'!K5","v":3.5924964377269486E-12},{"$f":"'BG;WT2,5;h'!L5","v":-4.8503157076668502E-9},{"$f":"'BG;WT2,5;h'!M5","v":3.3199387011673363E-6},{"$f":"'BG;WT2,5;h'!N5","v":-1.247468164390513E-3},{"$f":"'BG;WT2,5;h'!O5","v":0.28700192016743137},{"$f":"'BG;WT2,5;h'!P5","v":0}]
["heizen",null,null,null,null,null,null,{"$f":"IF($I$214=2,M217,N217)","v":"kühlen"},{"$f":"IF($I$214=2,M217,N217)","v":"kühlen"},null,null,null,null,null,null,null,{"$f":"'BG;WT2,5;h'!I6","v":"BG 1200"},{"$f":"'BG;WT2,5;h'!J6","v":-1.1243960372549887E-15},{"$f":"'BG;WT2,5;h'!K6","v":3.7947227790113298E-12},{"$f":"'BG;WT2,5;h'!L6","v":-5.0752622583859397E-9},{"$f":"'BG;WT2,5;h'!M6","v":3.4500448791136683E-6},{"$f":"'BG;WT2,5;h'!N6","v":-1.2955328331244712E-3},{"$f":"'BG;WT2,5;h'!O6","v":0.30220703780447411},{"$f":"'BG;WT2,5;h'!P6","v":0}]
["Primärdruck [Pa]","Primärvolumenstrom [m³/h]","Wasser-Massenstrom [kg/h]",null,null,null,null,"DpK, Auslegung =","DpH, Auslegung ="]
[null,null,50,null,null,null,null,{"$f":"IF($I$214=2,M219,O219)","v":28.201307810721179},{"$f":"IF($I$214=2,N219,P219)","v":7.9656023504001645},null,null,null,null,null,null,null,"Kühlen"]
[null,null,300,null,null,null,null,{"$f":"IF($I$214=2,M220,O220)","v":23.073797299680965},{"$f":"IF($I$214=2,N220,P220)","v":1.3},null,null,null,null,null,null,null,{"$f":"'BG;WT2,5;k 100kg_h'!I1","v":"Polynom 6 Ordnung - BG;WT2,5;k 100kg_h"},{"$f":"'BG;WT2,5;k 100kg_h'!J1","v":6},{"$f":"'BG;WT2,5;k 100kg_h'!K1","v":5},{"$f":"'BG;WT2,5;k 100kg_h'!L1","v":4},{"$f":"'BG;WT2,5;k 100kg_h'!M1","v":3},{"$f":"'BG;WT2,5;k 100kg_h'!N1","v":2},{"$f":"'BG;WT2,5;k 100kg_h'!O1","v":1},{"$f":"'BG;WT2,5;k 100kg_h'!P1","v":0}]
[null,null,null,null,null,null,null,{"$f":"IF($I$214=2,M221,O221)","v":28.201307810721179},1.6,null,null,null,null,null,null,null,{"$f":"'BG;WT2,5;k 100kg_h'!I3","v":"BG 630"},{"$f":"'BG;WT2,5;k 100kg_h'!J3","v":-2.1585851685865881E-16},{"$f":"'BG;WT2,5;k 100kg_h'!K3","v":9.6767155892923754E-13},{"$f":"'BG;WT2,5;k 100kg_h'!L3","v":-1.76717709481768E-9},{"$f":"'BG;WT2,5;k 100kg_h'!M3","v":1.7202353252286216E-6},{"$f":"'BG;WT2,5;k 100kg_h'!N3","v":-9.8993263846897822E-4},{"$f":"'BG;WT2,5;k 100kg_h'!O3","v":0.36491528136314816},{"$f":"'BG;WT2,5;k 100kg_h'!P3","v":0}]
["gesamt",null,null,null,null,null,null,33.328818321761396,1.8,null,null,null,null,null,null,null,{"$f":"'BG;WT2,5;k 100kg_h'!I4","v":"BG 800"},{"$f":"'BG;WT2,5;k 100kg_h'!J4","v":1.0830659638580856E-16},{"$f":"'BG;WT2,5;k 100kg_h'!K4","v":-1.2111372094670782E-13},{"$f":"'BG;WT2,5;k 100kg_h'!L4","v":-3.6536770359835539E-10},{"$f":"'BG;WT2,5;k 100kg_h'!M4","v":8.7368153028134265E-7},{"$f":"'BG;WT2,5;k 100kg_h'!N4","v":-7.7215094251533052E-4},{"$f":"'BG;WT2,5;k 100kg_h'!O4","v":0.3648995012270973},{"$f":"'BG;WT2,5;k 100kg_h'!P4","v":0}]
["Primärdruck [Pa]","Primärvolumenstrom",{"$f":"CONCATENATE(C227, \" \", A226)","v":"Wasser-Massenstrom [kg/h] kühlen"},{"$f":"CONCATENATE(C232, \" \", A231)","v":"Wasser-Massenstrom [kg/h] heizen"},null,null,null,37.174451205041549,2.1090909090909089,null,null,null,null,null,null,null,{"$f":"'BG;WT2,5;k 100kg_h'!I5","v":"BG 1000"},{"$f":"'BG;WT2,5;k 100kg_h'!J5","v":3.8400710421018372E-16},{"$f":"'BG;WT2,5;k 100kg_h'!K5","v":-1.0502095553434736E-12},{"$f":"'BG;WT2,5;k 100kg_h'!L5","v":8.4104538271664022E-10},{"$f":"'BG;WT2,5;k 100kg_h'!M5","v":1.3456305784766211E-7},{"$f":"'BG;WT2,5;k 100kg_h'!N5","v":-5.7569750565271026E-4},{"$f":"'BG;WT2,5;k 100kg_h'!O5","v":0.35976596437670394},{"$f":"'BG;WT2,5;k 100kg_h'!P5","v":0}]
[{"$f":"D228","v":45},{"$f":"E228","v":0},{"$f":"C228","v":50},{"$f":"C233","v":50},null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'BG;WT2,5;k 100kg_h'!I6","v":"BG 1200"},{"$f":"'BG;WT2,5;k 100kg_h'!J6","v":6.5952356269416348E-16},{"$f":"'BG;WT2,5;k 100kg_h'!K6","v":-1.9358022327234007E-12},{"$f":"'BG;WT2,5;k 100kg_h'!L6","v":1.9476342196471649E-9},{"$f":"'BG;WT2,5;k 100kg_h'!M6","v":-5.2879885604381321E-7},{"$f":"'BG;WT2,5;k 100kg_h'!N6","v":-3.9622250780243888E-4},{"$f":"'BG;WT2,5;k 100kg_h'!O6","v":0.35118500195987817},{"$f":"'BG;WT2,5;k 100kg_h'!P6","v":0}]
[{"$f":"D229","v":305},{"$f":"E229","v":0},{"$f":"C229","v":300},{"$f":"C234","v":300}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'BG;WT2,5;k'!I8","v":"Korrekturfaktoren - BG;WT2,5;k"},{"$f":"'BG;WT2,5;k'!J8","v":6},{"$f":"'BG;WT2,5;k'!K8","v":5},{"$f":"'BG;WT2,5;k'!L8","v":4},{"$f":"'BG;WT2,5;k'!M8","v":3},{"$f":"'BG;WT2,5;k'!N8","v":2},{"$f":"'BG;WT2,5;k'!O8","v":1},{"$f":"'BG;WT2,5;k'!P8","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'BG;WT2,5;k'!I9","v":"BG 630"},{"$f":"'BG;WT2,5;k'!J9","v":3.4816233818189494E-13},{"$f":"'BG;WT2,5;k'!K9","v":-1.2563474610047514E-10},{"$f":"'BG;WT2,5;k'!L9","v":1.6251742736909859E-8},{"$f":"'BG;WT2,5;k'!M9","v":-9.3568170018377565E-7},{"$f":"'BG;WT2,5;k'!N9","v":3.4348469144301678E-5},{"$f":"'BG;WT2,5;k'!O9","v":-1.1160363694072517E-3},{"$f":"'BG;WT2,5;k'!P9","v":0.74734760780225895}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'BG;WT2,5;k'!I10","v":"BG 800"},{"$f":"'BG;WT2,5;k'!J10","v":1.0475346449154691E-26},{"$f":"'BG;WT2,5;k'!K10","v":-4.8955168558711517E-24},{"$f":"'BG;WT2,5;k'!L10","v":8.4629729763327543E-22},{"$f":"'BG;WT2,5;k'!M10","v":-6.8854819969857664E-20},{"$f":"'BG;WT2,5;k'!N10","v":2.7225990865238E-18},{"$f":"'BG;WT2,5;k'!O10","v":-4.5667947962183834E-17},{"$f":"'BG;WT2,5;k'!P10","v":1.0000000000000002}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'BG;WT2,5;k'!I11","v":"BG 1000"},{"$f":"'BG;WT2,5;k'!J11","v":7.8693165984620388E-15},{"$f":"'BG;WT2,5;k'!K11","v":-2.935344341039698E-11},{"$f":"'BG;WT2,5;k'!L11","v":7.661484403257628E-9},{"$f":"'BG;WT2,5;k'!M11","v":-6.6987564862412183E-7},{"$f":"'BG;WT2,5;k'!N11","v":1.525204034465662E-5},{"$f":"'BG;WT2,5;k'!O11","v":-2.7499345363208601E-4},{"$f":"'BG;WT2,5;k'!P11","v":1.25171812029343}]
["kühlen",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'BG;WT2,5;k'!I12","v":"BG 1200"},{"$f":"'BG;WT2,5;k'!J12","v":-4.7324727316282315E-13},{"$f":"'BG;WT2,5;k'!K12","v":8.3072357948498334E-11},{"$f":"'BG;WT2,5;k'!L12","v":-6.7343997792567237E-10},{"$f":"'BG;WT2,5;k'!M12","v":-2.8421661850020901E-7},{"$f":"'BG;WT2,5;k'!N12","v":-2.6365020864954163E-5},{"$f":"'BG;WT2,5;k'!O12","v":1.4753152096046846E-3},{"$f":"'BG;WT2,5;k'!P12","v":1.4483517003839317}]
[]
[]
[]
[]
[]
[]
["Gemessene Baugröße"]
[{"$f":"A210","v":"Baugröße 800"},null,null,"DpK =",{"$f":"H233","v":28.201307810721179},"[kPa]","[kPa]"]
[null,null,null,"DpH =",{"$f":"I233","v":7.9656023504001645},"[kPa]","[kPa]"]
[{"$f":"IF($A$252=$A$271,A273,IF($A$252=$A$290,A292,IF($A$252=$A$309,A311,IF($A$252=$A$328,A330,\"-\"))))","v":"bei 200 kg/h Kühlwassermassenstrom"},{"$f":"IF($A$252=B263,$A$276,IF($A$252=$A$290,B292,IF($A$252=$A$309,B311,IF($A$252=$A$328,B330,\"-\"))))","v":0}]
["Schieberstellung",{"$f":"IF($A$252=$A$271,B274,IF($A$252=$A$290,B293,IF($A$252=$A$309,B312,IF($A$252=$A$328,B331,\"-\"))))","v":"Primärdruck (Baugröße 800 = Baugröße 800)"},"Primärvolumenstrom Baugröße 800","Primärvolumenstrom Baugröße 800","Primärvolumenstrom Baugröße 800","Primärdruck Baugröße 800","Primärvolumenstrom Baugröße 800","Primärdruck Baugröße 800","Induktionsverhältnis i","Sekundärvolumenstrom - Baugröße 800","Sekundärvolumenstrom - Baugröße 800","Korrektur Total \nbei Sollwassermenge","Korrektur Sensibel\nbei Sollwassermenge","Zelle",{"$f":"IF($A$252=$A$271,O274,IF($A$252=$A$290,O293,IF($A$252=$A$309,O312,IF($A$252=$A$328,O331,\"-\"))))","v":"qSK1)  - aus Primärdruck der gemessenen BG"},"Korrektur Baugröße","qSK1)  - BG korrigiert","qSK2)  - BG und Kondsations berücksichtigt","qtotoal2)  - BG und Kondsations berücksichtigt",{"$f":"IF($A$252=$A$271,T274,IF($A$252=$A$290,T293,IF($A$252=$A$309,T312,IF($A$252=$A$328,T331,\"-\"))))","v":"Schallleistungspegel"},"Primärvolumenstrom Minimal","Primärvolumenstrom Minimal","Primärdruck Minimal","Primärdruck Maximal","Korrektur heizen (bei anderem Massenstrom, gleicher WT)","spez. Leistung Eurocoil 4L kühlen","spez. Leistung Eurocoil 4L heizen","Korrektur Heizen / Kühlen 4 Leiter","Leistung (messung) zu Leistung Eurocoil"]
["[-]",{"$f":"IF($A$252=$A$271,B275,IF($A$252=$A$290,B294,IF($A$252=$A$309,B313,IF($A$252=$A$328,B332,\"-\"))))","v":"Pa"},"[m³/h]","[m³/h]","[m³/h]","[Pa]","[m³/h]","[Pa]","[-]","[m³/h]","[m³/h]","[-]","[-]","[-]","[W/K]","[-]","[W/K]","[W/K]","[W/K]",{"$f":"IF($A$252=$A$271,T275,IF($A$252=$A$290,T294,IF($A$252=$A$309,T313,IF($A$252=$A$328,T332,\"-\"))))","v":"[dB(A)]"},"[m³/h]","[m³/h]","[m³/h]","[m³/h]","[-]","[-]","[-]","[-]","[-]"]
[5,{"$f":"IF($A$252=$A$271,B276,IF($A$252=$A$290,B295,IF($A$252=$A$309,B314,IF($A$252=$A$328,B333,\"-\"))))","v":120},80.73043386129882,80.73043386129882,80.73043386129882,120,80.73043386129882,120,2.0317546050552298,164.02443076580053,164.02443076580053,1.4203588067994268,0.93069193474908996,"H5",41.134218578828666,1,41.134218578828666,38.283285473522014,58.425349619251897,{"$f":"IF($A$252=$A$271,T276,IF($A$252=$A$290,T295,IF($A$252=$A$309,T314,IF($A$252=$A$328,T333,\"-\"))))+10*LOG(D77/D76)","v":26.821830328457246},{"$f":"IF($A$252=$A$271,U276,IF($A$252=$A$290,U295,IF($A$252=$A$309,U314,IF($A$252=$A$328,U333,\"-\"))))","v":49.797088153619242},127.82028754345181,45,305,0.80605372973855705,42.657223386637845,22.911497499711633,0.53710709888559094,0.96429667271109232]
[4.5,{"$f":"IF($A$252=$A$271,B277,IF($A$252=$A$290,B296,IF($A$252=$A$309,B315,IF($A$252=$A$328,B334,\"-\"))))","v":120},96.944857405303324,96.944857405303324,96.944857405303324,120,96.944857405303324,120,1.5977671256887627,154.89530616677845,154.89530616677845,1.431542005216897,0.93382245854282908,"H4,5",37.757955145535455,1,37.757955145535455,35.259226503553784,54.052098821929476,{"$f":"IF($A$252=$A$271,T277,IF($A$252=$A$290,T296,IF($A$252=$A$309,T315,IF($A$252=$A$328,T334,\"-\"))))","v":28.029613342122026},58.896333262093655,155.72819534846124,45,305,0.80605372973855705,41.022613505223546,22.320492596141335,0.54410215949062324,0.92041807967031675]
[4,{"$f":"IF($A$252=$A$271,B278,IF($A$252=$A$290,B297,IF($A$252=$A$309,B316,IF($A$252=$A$328,B335,\"-\"))))","v":120},60.780258355806176,60.780258355806176,60.780258355806176,120,60.780258355806176,120,1.6276072028144852,98.926386288835431,98.926386288835431,1.500638422150776,0.95423647266969258,"H4",26.303715133112355,1,26.303715133112355,25.099964346729546,39.472365574057214,{"$f":"IF($A$252=$A$271,T278,IF($A$252=$A$290,T297,IF($A$252=$A$309,T316,IF($A$252=$A$328,T335,\"-\"))))+10*LOG(D107/D106)","v":25.979779900693913},{"$f":"IF($A$252=$A$271,U278,IF($A$252=$A$290,U297,IF($A$252=$A$309,U316,IF($A$252=$A$328,U335,\"-\"))))","v":36.630806586501116},98.381681885788808,45,305,0.80605372973855716,29.351391816913299,17.547885518013025,0.59785531219345178,0.89616585466162568]
[3.5,{"$f":"IF($A$252=$A$271,B279,IF($A$252=$A$290,B298,IF($A$252=$A$309,B317,IF($A$252=$A$328,B336,\"-\"))))","v":120},60.65828271271986,60.65828271271986,60.65828271271986,120,60.65828271271986,120,1.3456870105038172,81.627063125975369,81.627063125975369,1.5218505309956356,0.96083516452126294,"H3,5",20.198804008772065,1,20.198804008772065,19.407721172901251,30.73956060622654,{"$f":"IF($A$252=$A$271,T279,IF($A$252=$A$290,T298,IF($A$252=$A$309,T317,IF($A$252=$A$328,T336,\"-\"))))","v":28.020321973295566},36.272124446051805,98.918243580174746,45,305,0.80605372973855705,25.09940013834094,15.523668382064885,0.61848762506285915,0.8047524601162519]
[3,{"$f":"IF($A$252=$A$271,B280,IF($A$252=$A$290,B299,IF($A$252=$A$309,B318,IF($A$252=$A$328,B337,\"-\"))))","v":120},39.963087522579428,39.963087522579428,39.963087522579428,120,39.963087522579428,120,2.1607673299501133,86.350933922726639,86.350933922726639,1.5160778851913599,0.95902503721811339,"H3",21.62034877106791,1,21.62034877106791,20.734455784841995,32.778132641940253,{"$f":"IF($A$252=$A$271,T280,IF($A$252=$A$290,T299,IF($A$252=$A$309,T318,IF($A$252=$A$328,T337,\"-\"))))+10*LOG(D137/D136)","v":27.278731719662325},{"$f":"IF($A$252=$A$271,U280,IF($A$252=$A$290,U299,IF($A$252=$A$309,U318,IF($A$252=$A$328,U337,\"-\"))))","v":23.723945867037322},65.621458991696059,45,305,0.80605372973855705,26.293572146444326,16.10894038351643,0.61265697539293229,0.82226745953921765]
[2.5,{"$f":"IF($A$252=$A$271,B281,IF($A$252=$A$290,B300,IF($A$252=$A$309,B319,IF($A$252=$A$328,B338,\"-\"))))","v":120},50.618740670748814,50.618740670748814,50.618740670748814,120,50.618740670748814,120,1.5765376052182374,79.802348196225324,79.802348196225324,1.5240756803566906,0.96153573290491057,"H2,5",19.813206921650636,1,19.813206921650636,19.051106438605991,30.196826819162585,{"$f":"IF($A$252=$A$271,T281,IF($A$252=$A$290,T300,IF($A$252=$A$309,T319,IF($A$252=$A$328,T338,\"-\"))))","v":26.26541587621108},30.020574634206334,83.195117726866584,45,305,0.80605372973855705,24.63129503794131,15.2906113199261,0.62077983704766226,0.8043916038978447]
[2,{"$f":"IF($A$252=$A$271,B282,IF($A$252=$A$290,B301,IF($A$252=$A$309,B320,IF($A$252=$A$328,B339,\"-\"))))","v":120},19.714783300680438,19.714783300680438,19.714783300680438,120,19.714783300680438,120,3.2339169965202519,63.7559727987841,63.7559727987841,1.5435105748695772,0.96772069093466051,"H2",12.480288994803733,1,12.480288994803733,12.077433889115708,19.263458040907967,{"$f":"IF($A$252=$A$271,T282,IF($A$252=$A$290,T301,IF($A$252=$A$309,T320,IF($A$252=$A$328,T339,\"-\"))))+10*LOG(D167/D166)","v":18.206426872556072},{"$f":"IF($A$252=$A$271,U282,IF($A$252=$A$290,U301,IF($A$252=$A$309,U320,IF($A$252=$A$328,U339,\"-\"))))","v":11.395074504856202},33.205777924310411,45,305,0.80605372973855727,20.346128254429384,13.060341639261571,0.64190795791421962,0.61339871835747195]
[2,{"$f":"IF($A$252=$A$271,B283,IF($A$252=$A$290,B302,IF($A$252=$A$309,B321,IF($A$252=$A$328,B340,\"-\"))))","v":120},19.714783300680438,19.714783300680438,19.714783300680438,120,19.714783300680438,120,3.2339169965202519,63.7559727987841,63.7559727987841,1.5435105748695772,0.96772069093466051,"H2",12.480288994803733,1,12.480288994803733,12.077433889115708,19.263458040907967,{"$f":"IF($A$252=$A$271,T283,IF($A$252=$A$290,T302,IF($A$252=$A$309,T321,IF($A$252=$A$328,T340,\"-\"))))","v":23.502783332746802},11.395074504856202,33.205777924310411,45,305,0.80605372973855727,20.346128254429384,13.060341639261571,0.64190795791421962,0.61339871835747195]
[2,{"$f":"IF($A$252=$A$271,B284,IF($A$252=$A$290,B303,IF($A$252=$A$309,B322,IF($A$252=$A$328,B341,\"-\"))))","v":120},19.714783300680438,19.714783300680438,19.714783300680438,120,19.714783300680438,120,3.2339169965202519,63.7559727987841,63.7559727987841,1.5435105748695772,0.96772069093466051,"H2",12.480288994803733,1,12.480288994803733,12.077433889115708,19.263458040907967,{"$f":"IF($A$252=$A$271,T284,IF($A$252=$A$290,T303,IF($A$252=$A$309,T322,IF($A$252=$A$328,T341,\"-\"))))","v":23.502783332746802},11.395074504856202,33.205777924310411,45,305,0.80605372973855727,20.346128254429384,13.060341639261571,0.64190795791421962,0.61339871835747195]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrektur für Heizen 2-Leiter",null,null,"Korrektur für Heizen 4-Leiter"]
[{"$f":"A212","v":"Baugröße 630"},null,null,"DpK =",{"$f":"H234","v":23.073797299680965},"[kPa]"]
[null,null,null,"DpH =",{"$f":"I234","v":1.3},"[kPa]",null,null,null,null,null,null,null,null,"mit evtl. Korrektur 2L bzw. 4L",null,null,null,null,null,"Grenzwerte Auslegung","Grenzwerte Auslegung","Grenzwerte Auslegung","Grenzwerte Auslegung","Korrektur heizen / kühlen\n (da anderer Massenstrom) bei gleichem Wärmetauscher",null,null,"Korrektur Heizen / Kühlen 4 Leiter",null,5,null,"Abweichung \"ohne Schieber\" zu \"mit Schieber\""]
[{"$f":"CONCATENATE(\"bei \", ROUND($B$3,0), \" kg/h Kühlwassermassenstrom\")","v":"bei 200 kg/h Kühlwassermassenstrom"},null,null,null,null,null,null,null,null,"für kondensierende Auslegung",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"CONCATENATE(\"H\",AD272)","v":"H5"}]
["Schieberstellung",{"$f":"CONCATENATE($H$2,\" (\", $A$271,\" = \", $A$252,\")\")","v":"Primärdruck (Baugröße 630 = Baugröße 800)"},{"$f":"IF($F$1=2,G274,H274)","v":"Primärvolumenstrom Baugröße 630"},{"$f":"CONCATENATE($S$61,\" \", $A$252)","v":"Primärvolumenstrom Baugröße 800"},{"$f":"CONCATENATE(\"Primärvolumenstrom \", $A$252)","v":"Primärvolumenstrom Baugröße 800"},{"$f":"CONCATENATE(\"Primärdruck \", $A$252)","v":"Primärdruck Baugröße 800"},{"$f":"CONCATENATE(\"Primärvolumenstrom \", $A$271)","v":"Primärvolumenstrom Baugröße 630"},{"$f":"CONCATENATE(\"Primärdruck \", $A$271)","v":"Primärdruck Baugröße 630"},"Induktionsverhältnis i",{"$f":"CONCATENATE(\"Sekundärvolumenstrom - \",$A$252)","v":"Sekundärvolumenstrom - Baugröße 800"},{"$f":"CONCATENATE(\"Sekundärvolumenstrom - \",A271)","v":"Sekundärvolumenstrom - Baugröße 630"},"Korrektur Total \nbei Sollwassermenge","Korrektur Sensibel\nbei Sollwassermenge","Zelle","qSK1)  - aus Primärdruck der gemessenen BG","Korrektur Baugröße","qSK1)  - BG korrigiert","qSK2)  - BG und Kondsations berücksichtigt","qtotoal2)  - BG und Kondsations berücksichtigt","Schallleistungspegel","Primärvolumenstrom Minimal","Primärvolumenstrom Maximal","Primärdruck Minimal","Primärdruck Maximal","Korrektur heizen (bei anderem Massenstrom, gleicher WT)","spez. Leistung Eurocoil 4L kühlen bei Nennwassermenge Heizen","spez. Leistung Eurocoil 4L heizen","Korrektur Heizen / Kühlen 4 Leiter","Leistung (messung) zu Leistung Eurocoil",{"$f":"CONCATENATE(\"Primärdruck \", $A$290, \"; S\",AD272)","v":"Primärdruck Baugröße 800; S5"},"qSK1)  - aus Primärdruck der gemessenen BG","Kühlleistung \"mit\" Schieber im Vergleich zu \"ohne Schieber\""]
["[-]",{"$f":"$G$2","v":"Pa"},{"$f":"IF($F$1=2,G275,H275)","v":"[m³/h]"},{"$f":"$T$61","v":"[m³/h]"},"[m³/h]","[Pa]","[m³/h]","[Pa]","[-]","[m³/h]","[m³/h]","[-]","[-]","[-]","[W/K]","[-]","[W/K]","[W/K]","[W/K]","[dB(A)]","[m³/h]","[m³/h]","[m³/h]","[m³/h]","[-]","[-]","[-]","[-]","[-]","[Pa]","[W/K]"]
[{"$f":"Auslegetool!B26","v":5},{"$f":"Auslegetool!C26","v":120},{"$f":"IF($F$1=2,G276,H276)","v":58.086531680690612},{"$f":"VLOOKUP(A276,Matrix_Ergebnisse,7,0)*B276^VLOOKUP(A276,Matrix_Ergebnisse,8,0)","v":80.73043386129882},{"$f":"IF($F$1=2,D276,B276)","v":80.73043386129882},{"$f":"IF($F$1=2,B276,D276)","v":120},{"$f":"IF($F$1=2,E276*$C$212,E276)","v":58.086531680690612},{"$f":"IF($F$1=1,F276/$C$212^2,F276)","v":120},{"$f":"VLOOKUP(A276,Matrix_Ergebnisse,9,0)*H276^VLOOKUP(N276,Matrix_Ergebnisse,9,0)+VLOOKUP(A276,Matrix_Ergebnisse,10,0)*H276^VLOOKUP(N276,Matrix_Ergebnisse,10,0)+VLOOKUP(A276,Matrix_Ergebnisse,11,0)*H276^VLOOKUP(N276,Matrix_Ergebnisse,11,0)","v":2.0317546050552298},{"$f":"E276*I276","v":164.02443076580053},{"$f":"G276*I276","v":118.01757823392964},{"$f":"Auslegung_BG800_kondensierend!AH32","v":1.4203588067994268},{"$f":"Auslegung_BG800_kondensierend!AL32","v":0.93069193474908996},{"$f":"CONCATENATE(\"H\",A276)","v":"H5"},{"$f":"(VLOOKUP(A276,Matrix_Ergebnisse,3,0)*H276^VLOOKUP(N276,Matrix_Ergebnisse,3,0)+VLOOKUP(A276,Matrix_Ergebnisse,4,0)*H276^VLOOKUP(N276,Matrix_Ergebnisse,4,0)+VLOOKUP(A276,Matrix_Ergebnisse,5,0)*H276^VLOOKUP(N276,Matrix_Ergebnisse,5,0)+VLOOKUP(A276,Matrix_Ergebnisse,6,0)*H276^VLOOKUP(N276,Matrix_Ergebnisse,6,0))*$C$352","v":41.134218578828666},{"$f":"$R$241*O276^$R$240+$S$241*O276^$S$240+$T$241*O276^$T$240+$U$241*O276^$U$240+$V$241*O276^$V$240+$W$241*O276^$W$240+$X$241*O276^$X$240","v":0.72785425953927096},{"$f":"IF($A$252=$A$271,O276,O276*P276)","v":29.93971620541986},{"$f":"Q276*M276","v":27.864652401060891},{"$f":"Q276*L276","v":42.525139585443618},{"$f":"VLOOKUP(A276,Matrix_Ergebnisse,17,0)*LN(F276)+VLOOKUP(A276,Matrix_Ergebnisse,18,0)+10*LOG($B$212/$B$213*(D77/D76))","v":26.853492277823904},{"$f":"VLOOKUP(A276,Matrix_Ergebnisse,12,0)*$C$212","v":35.829612208091895},{"$f":"VLOOKUP(A276,Matrix_Ergebnisse,13,0)*$C$212","v":91.968255671508004},{"$f":"$D$228","v":45},{"$f":"$D$229","v":305},{"$f":"(VLOOKUP(A276,Matrix_Ergebnisse,26,0))","v":0.80605372973855705},{"$f":"$R$235*K276^$R$234+$S$235*K276^$S$234+$T$235*K276^$T$234+$U$235*K276^$U$234+$V$235*K276^$V$234+$W$235*K276^$W$234+$X$235*K276^$X$234","v":31.7849043763235},{"$f":"$R$228*K276^$R$227+$S$228*K276^$S$227+$T$228*K276^$T$227+$U$228*K276^$U$227+$V$228*K276^$V$227+$W$228*K276^$W$227+$X$228*K276^$X$227","v":16.980528171768835},{"$f":"1/Z276*AA276","v":0.53423247623225789},{"$f":"1/Z276*Q276*$C$352","v":0.94194765700543936},{"$f":"VLOOKUP($AD$272,Matrix_Ergebnisse,14,0)*E276^VLOOKUP($AD$272,Matrix_Ergebnisse,15,0)","v":120.00162820198784},{"$f":"(VLOOKUP($AD$272,Matrix_Ergebnisse,3,0)*AD276^VLOOKUP($AD$273,Matrix_Ergebnisse,3,0)+VLOOKUP($AD$272,Matrix_Ergebnisse,4,0)*AD276^VLOOKUP($AD$273,Matrix_Ergebnisse,4,0)+VLOOKUP($AD$272,Matrix_Ergebnisse,5,0)*AD276^VLOOKUP($AD$273,Matrix_Ergebnisse,5,0)+VLOOKUP($AD$272,Matrix_Ergebnisse,6,0)*AD276^VLOOKUP($AD$273,Matrix_Ergebnisse,6,0))*$C$352","v":41.134526594315048},{"$f":"1/AE276*O276-1","v":-7.488003676781041E-6}]
[{"$f":"Auslegetool!B27","v":4.5},{"$f":"Auslegetool!C27","v":120},{"$f":"IF($F$1=2,G277,H277)","v":69.753007157474343},{"$f":"VLOOKUP(A277,Matrix_Ergebnisse,7,0)*B277^VLOOKUP(A277,Matrix_Ergebnisse,8,0)","v":96.944857405303324},{"$f":"IF($F$1=2,D277,B277)","v":96.944857405303324},{"$f":"IF($F$1=2,B277,D277)","v":120},{"$f":"IF($F$1=2,E277*$C$212,E277)","v":69.753007157474343},{"$f":"IF($F$1=1,F277/$C$212^2,F277)","v":120},{"$f":"VLOOKUP(A277,Matrix_Ergebnisse,9,0)*H277^VLOOKUP(N277,Matrix_Ergebnisse,9,0)+VLOOKUP(A277,Matrix_Ergebnisse,10,0)*H277^VLOOKUP(N277,Matrix_Ergebnisse,10,0)+VLOOKUP(A277,Matrix_Ergebnisse,11,0)*H277^VLOOKUP(N277,Matrix_Ergebnisse,11,0)","v":1.5977671256887627},{"$f":"E277*I277","v":154.89530616677845},{"$f":"G277*I277","v":111.44906175414548},{"$f":"Auslegung_BG800_kondensierend!AH33","v":1.431542005216897},{"$f":"Auslegung_BG800_kondensierend!AL33","v":0.93382245854282908},"H4,5",37.757955145535455,0.72820895668262342,{"$f":"IF($A$252=$A$271,O277,O277*P277)","v":27.495681122999667},{"$f":"Q277*M277","v":25.676084545589205},39.361222489623323,{"$f":"VLOOKUP(A277,Matrix_Ergebnisse,17,0)*LN(F277)+VLOOKUP(A277,Matrix_Ergebnisse,18,0)+10*LOG($B$212/$B$213)","v":26.599994934706302},42.376630030042996,112.04833567755138,{"$f":"$D$228","v":45},{"$f":"$D$229","v":305},0.80605372973855705,{"$f":"$R$235*K277^$R$234+$S$235*K277^$S$234+$T$235*K277^$T$234+$U$235*K277^$U$234+$V$235*K277^$V$234+$W$235*K277^$W$234+$X$235*K277^$X$234","v":30.498521537665106},{"$f":"$R$228*K277^$R$227+$S$228*K277^$S$227+$T$228*K277^$T$227+$U$228*K277^$U$227+$V$228*K277^$V$227+$W$228*K277^$W$227+$X$228*K277^$X$227","v":16.46182100377445},{"$f":"1/Z277*AA277","v":0.53975800051305467},{"$f":"1/Z277*Q277*$C$352","v":0.90154144321530516},173.99655111742987,49.000728741583814,{"$f":"1/AE277*O277-1","v":-0.22944094679366123}]
[{"$f":"Auslegetool!B28","v":4},{"$f":"Auslegetool!C28","v":120},43.732137109665416,{"$f":"VLOOKUP(A278,Matrix_Ergebnisse,7,0)*B278^VLOOKUP(A278,Matrix_Ergebnisse,8,0)","v":60.780258355806176},{"$f":"IF($F$1=2,D278,B278)","v":60.780258355806176},120,{"$f":"IF($F$1=2,E278*$C$212,E278)","v":43.732137109665416},120,1.6276072028144852,98.926386288835431,71.178741354162071,{"$f":"Auslegung_BG800_kondensierend!AH34","v":1.500638422150776},{"$f":"Auslegung_BG800_kondensierend!AL34","v":0.95423647266969258},"H4",26.303715133112355,0.73104144538279558,19.229105929847769,18.349114215089806,28.855935181936886,{"$f":"VLOOKUP(A278,Matrix_Ergebnisse,17,0)*LN(F278)+VLOOKUP(A278,Matrix_Ergebnisse,18,0)+10*LOG($B$212/$B$213*(D107/D106))","v":25.484378344900541},26.356312056141046,70.786819893433403,45,305,0.80605372973855716,21.535534516038073,12.446089737744376,0.57793270598765267,0.89290126119355684,67.444862186503812,28.164543973614087,-6.606990840132354E-2]
[{"$f":"Auslegetool!B29","v":3.5},{"$f":"Auslegetool!C29","v":120},43.64437414695697,{"$f":"VLOOKUP(A279,Matrix_Ergebnisse,7,0)*B279^VLOOKUP(A279,Matrix_Ergebnisse,8,0)","v":60.65828271271986},{"$f":"IF($F$1=2,D279,B279)","v":60.65828271271986},120,{"$f":"IF($F$1=2,E279*$C$212,E279)","v":43.64437414695697},120,1.3456870105038172,81.627063125975369,58.731667371128616,{"$f":"Auslegung_BG800_kondensierend!AH35","v":1.5218505309956356},{"$f":"Auslegung_BG800_kondensierend!AL35","v":0.96083516452126294},"H3,5",20.198804008772065,0.73341444799015243,14.814094692154843,14.233903110770166,22.544837873475473,26.590703565879842,26.098235881915322,71.172882575979386,45,305,0.80605372973855705,18.345543024652009,10.846120777183287,0.59121285004257995,0.80750374476505016,67.170395260763343,28.078827497634418,-0.28063933543970909]
[{"$f":"Auslegetool!B30","v":3},{"$f":"Auslegetool!C30","v":120},28.753928827221785,39.963087522579428,39.963087522579428,120,28.753928827221785,120,2.1607673299501133,86.350933922726639,62.130550017571608,{"$f":"Auslegung_BG800_kondensierend!AH36","v":1.5160778851913599},{"$f":"Auslegung_BG800_kondensierend!AL36","v":0.95902503721811339},"H3",21.62034877106791,0.73281120877708306,15.843633917108397,15.194441607025043,24.0201830027958,{"$f":"VLOOKUP(A280,Matrix_Ergebnisse,17,0)*LN(F280)+VLOOKUP(A280,Matrix_Ergebnisse,18,0)+10*LOG($B$212/$B$213*(D137/D136))","v":26.921213008725285},17.069668367746367,47.215440006220334,45,305,0.80605372973855705,19.23816993795548,11.302772240031338,0.58751805792773504,0.82355203058322535,28.793385541619394,13.884957918723281,0.55710581894625544]
[{"$f":"Auslegetool!B31","v":2.5},{"$f":"Auslegetool!C31","v":120},36.420801214319269,50.618740670748814,50.618740670748814,120,36.420801214319269,120,1.5765376052182374,79.802348196225324,57.418762726552373,{"$f":"Auslegung_BG800_kondensierend!AH37","v":1.5240756803566906},{"$f":"Auslegung_BG800_kondensierend!AL37","v":0.96153573290491057},"H2,5",19.813206921650636,0.73358356700733929,14.534643007438978,13.975578616669072,22.151895930304178,24.835797468795356,21.600169553880168,59.859901779086933,45,305,0.80605372973855705,17.996297196479439,10.665572934370491,0.59265374526360703,0.8076463090575291,46.523140578089006,21.008337558006481,-5.6888396478586234E-2]
[{"$f":"Auslegetool!B32","v":2},{"$f":"Auslegetool!C32","v":120},14.185027009026168,19.714783300680438,19.714783300680438,120,14.185027009026168,120,3.2339169965202519,63.7559727987841,45.873199940588556,{"$f":"Auslegung_BG800_kondensierend!AH38","v":1.5435105748695772},{"$f":"Auslegung_BG800_kondensierend!AL38","v":0.96772069093466051},"H2",12.480288994803733,0.73730786588889963,9.2018152444354602,8.9047870061981751,14.203099137782216,{"$f":"VLOOKUP(A282,Matrix_Ergebnisse,17,0)*LN(F282)+VLOOKUP(A282,Matrix_Ergebnisse,18,0)+10*LOG($B$212/$B$213*(D167/D166))","v":19.42498669523571},8.1988950705672679,23.891962165052611,45,305,0.80605372973855727,14.815095409939927,8.9727762514869944,0.6056509258433036,0.62111076505532758,6.8608232203697046,3.5849719174690882,2.4812794303879917]
[{"$f":"Auslegetool!B33","v":2},{"$f":"Auslegetool!C33","v":120},14.185027009026168,19.714783300680438,19.714783300680438,120,14.185027009026168,120,3.2339169965202519,63.7559727987841,45.873199940588556,{"$f":"Auslegung_BG800_kondensierend!AH39","v":1.5435105748695772},{"$f":"Auslegung_BG800_kondensierend!AL39","v":0.96772069093466051},"H2",12.480288994803733,0.73730786588889963,9.2018152444354602,8.9047870061981751,14.203099137782216,22.073164925331078,8.1988950705672679,23.891962165052611,45,305,0.80605372973855727,14.815095409939927,8.9727762514869944,0.6056509258433036,0.62111076505532758,6.8608232203697046,3.5849719174690882,2.4812794303879917]
[{"$f":"Auslegetool!B34","v":2},{"$f":"Auslegetool!C34","v":120},14.185027009026168,19.714783300680438,19.714783300680438,120,14.185027009026168,120,3.2339169965202519,63.7559727987841,45.873199940588556,{"$f":"Auslegung_BG800_kondensierend!AH40","v":1.5435105748695772},{"$f":"Auslegung_BG800_kondensierend!AL40","v":0.96772069093466051},"H2",12.480288994803733,0.73730786588889963,9.2018152444354602,8.9047870061981751,14.203099137782216,{"$f":"VLOOKUP(A284,Matrix_Ergebnisse,17,0)*LN(F284)+VLOOKUP(A284,Matrix_Ergebnisse,18,0)+10*LOG($B$212/$B$213)","v":22.073164925331078},{"$f":"VLOOKUP(A284,Matrix_Ergebnisse,12,0)","v":11.395074504856202},23.891962165052611,45,305,0.80605372973855727,14.815095409939927,8.9727762514869944,0.6056509258433036,0.62111076505532758,6.8608232203697046,3.5849719174690882,2.4812794303879917]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,46.025708300255808,1,46.025708300255808,42.386592451112961,63.703945329157882,33.194641606329263]
[]
[{"$f":"A213","v":"Baugröße 800"},null,null,"DpK =",{"$f":"H235","v":28.201307810721179},"[kPa]",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"vprim Auslegung"]
[null,null,null,"DpH =",{"$f":"I235","v":1.6},"[kPa]",null,null,null,null,null,null,null,null,"mit evtl. Korrektur 2L bzw. 4L",null,null,null,null,null,"Grenzwerte Auslegung","Grenzwerte Auslegung","Grenzwerte Auslegung","Grenzwerte Auslegung","Korrektur spez.Leistung \n heizen / kühlen\n (da anderer Massenstrom) bei gleichem Wärmetauscher",null,null,"Korrektur Heizen / Kühlen 4 Leiter",null,5,null,"Abweichung \"mit Schieber\" zu ohne Schieber",{"$f":"E295","v":80.73043386129882}]
[{"$f":"CONCATENATE(\"bei \", ROUND($B$3,0), \" kg/h Kühlwassermassenstrom\")","v":"bei 200 kg/h Kühlwassermassenstrom"},null,null,null,null,null,null,null,null,"für kondensierende Auslegung",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"AD273","v":"H5"}]
["Schieberstellung",{"$f":"CONCATENATE($H$2,\" (\", $A$290,\" = \", $A$252,\")\")","v":"Primärdruck (Baugröße 800 = Baugröße 800)"},{"$f":"IF($F$1=2,G293,H293)","v":"Primärvolumenstrom Baugröße 800"},{"$f":"CONCATENATE($S$61,\" \", $A$252)","v":"Primärvolumenstrom Baugröße 800"},{"$f":"CONCATENATE(\"Primärvolumenstrom \", $A$252)","v":"Primärvolumenstrom Baugröße 800"},{"$f":"CONCATENATE(\"Primärdruck \", $A$252)","v":"Primärdruck Baugröße 800"},{"$f":"CONCATENATE(\"Primärvolumenstrom \", $A$290)","v":"Primärvolumenstrom Baugröße 800"},{"$f":"CONCATENATE(\"Primärdruck \", $A$290)","v":"Primärdruck Baugröße 800"},"Induktionsverhältnis i",{"$f":"CONCATENATE(\"Sekundärvolumenstrom - \",$A$252)","v":"Sekundärvolumenstrom - Baugröße 800"},{"$f":"CONCATENATE(\"Sekundärvolumenstrom - \",A290)","v":"Sekundärvolumenstrom - Baugröße 800"},"Korrektur Total \nbei Sollwassermenge","Korrektur Sensibel\nbei Sollwassermenge","Zelle","qSK1)  - aus Primärdruck der gemessenen BG","Korrektur Baugröße","qSK1)  - BG korrigiert","qSK2)  - BG und Kondsations berücksichtigt","qtotoal2)  - BG und Kondsations berücksichtigt","Schallleistungspegel","Primärvolumenstrom Minimal","Primärvolumenstrom Minimal","Primärdruck Minimal","Primärdruck Maximal","Korrektur heizen (bei anderem Massenstrom, gleicher WT)","spez. Leistung Eurocoil 4L kühlen","spez. Leistung Eurocoil 4L heizen","Korrektur Heizen / Kühlen 4 Leiter","Leistung (messung) zu Leistung Eurocoil",{"$f":"CONCATENATE(\"Primärdruck \", $A$290, \"; S\",AD291)","v":"Primärdruck Baugröße 800; S5"},"qSK1)  - aus Primärdruck der gemessenen BG","Kühlleistung \"mit Schieber\" im Vergleich zu \"ohne Schieber\"","prozentualer Anteil Primrvol von Auslegung","prozentualer Anteil spez. Leistung zu Auslegung"]
["[-]",{"$f":"$G$2","v":"Pa"},{"$f":"IF($F$1=2,G294,H294)","v":"[m³/h]"},{"$f":"$T$61","v":"[m³/h]"},"[m³/h]","[Pa]","[m³/h]","[Pa]","[-]","[m³/h]","[m³/h]","[-]","[-]","[-]","[W/K]","[-]","[W/K]","[W/K]","[W/K]","[dB(A)]","[m³/h]","[m³/h]","[m³/h]","[m³/h]","[-]","[-]","[-]","[-]","[-]","[Pa]","[W/K]"]
[{"$f":"Auslegetool!B45","v":5},{"$f":"Auslegetool!C45","v":120},{"$f":"IF($F$1=2,G295,H295)","v":80.73043386129882},{"$f":"VLOOKUP(A295,Matrix_Ergebnisse,7,0)*B295^VLOOKUP(A295,Matrix_Ergebnisse,8,0)","v":80.73043386129882},{"$f":"IF($F$1=2,D295,B295)","v":80.73043386129882},{"$f":"IF($F$1=2,B295,D295)","v":120},{"$f":"IF($F$1=2,E295*$C$213,E295)","v":80.73043386129882},{"$f":"IF($F$1=1,F295/$C$213^2,F295)","v":120},{"$f":"VLOOKUP(A295,Matrix_Ergebnisse,9,0)*B295^VLOOKUP(N295,Matrix_Ergebnisse,9,0)+VLOOKUP(A295,Matrix_Ergebnisse,10,0)*B295^VLOOKUP(N295,Matrix_Ergebnisse,10,0)+VLOOKUP(A295,Matrix_Ergebnisse,11,0)*B295^VLOOKUP(N295,Matrix_Ergebnisse,11,0)","v":2.0317546050552298},{"$f":"E295*I295","v":164.02443076580053},{"$f":"G295*I295","v":164.02443076580053},{"$f":"Auslegung_BG800_kondensierend!AH51","v":1.4203588067994268},{"$f":"Auslegung_BG800_kondensierend!AL51","v":0.93069193474908996},{"$f":"CONCATENATE(\"H\",A295)","v":"H5"},{"$f":"(VLOOKUP(A295,Matrix_Ergebnisse,3,0)*H295^VLOOKUP(N295,Matrix_Ergebnisse,3,0)+VLOOKUP(A295,Matrix_Ergebnisse,4,0)*H295^VLOOKUP(N295,Matrix_Ergebnisse,4,0)+VLOOKUP(A295,Matrix_Ergebnisse,5,0)*H295^VLOOKUP(N295,Matrix_Ergebnisse,5,0)+VLOOKUP(A295,Matrix_Ergebnisse,6,0)*H295^VLOOKUP(N295,Matrix_Ergebnisse,6,0))*$C$352","v":41.134218578828666},{"$f":"$R$242*O295^$R$240+$S$242*O295^$S$240+$T$242*O295^$T$240+$U$242*O295^$U$240+$V$242*O295^$V$240+$W$242*O295^$W$240+$X$242*O295^$X$240","v":1},{"$f":"IF($A$252=$A$290,O295,O295*P295)","v":41.134218578828666},{"$f":"Q295*M295","v":38.283285473522014},{"$f":"Q295*L295","v":58.425349619251897},{"$f":"VLOOKUP(A295,Matrix_Ergebnisse,17,0)*LN(F295)+VLOOKUP(A295,Matrix_Ergebnisse,18,0)+10*LOG($B$213/$B$213*(D77/D76))","v":28.283110685239627},{"$f":"VLOOKUP(A295,Matrix_Ergebnisse,12,0)*$C$213","v":49.797088153619242},{"$f":"VLOOKUP(A295,Matrix_Ergebnisse,13,0)*$C$213","v":127.82028754345181},{"$f":"$D$228","v":45},{"$f":"$D$229","v":305},{"$f":"(VLOOKUP(A295,Matrix_Ergebnisse,26,0))","v":0.80605372973855705},{"$f":"$R$236*K295^$R$234+$S$236*K295^$S$234+$T$236*K295^$T$234+$U$236*K295^$U$234+$V$236*K295^$V$234+$W$236*K295^$W$234+$X$236*K295^$X$234","v":42.657223386637845},{"$f":"$R$229*K295^$R$227+$S$229*K295^$S$227+$T$229*K295^$T$227+$U$229*K295^$U$227+$V$229*K295^$V$227+$W$229*K295^$W$227+$X$229*K295^$X$227","v":22.911497499711633},{"$f":"1/Z295*AA295","v":0.53710709888559094},{"$f":"1/Z295*Q295*$C$352","v":0.96429667271109232},{"$f":"VLOOKUP($AD$291,Matrix_Ergebnisse,14,0)*E295^VLOOKUP($AD$291,Matrix_Ergebnisse,15,0)","v":120.00162820198784},{"$f":"(VLOOKUP($AD$291,Matrix_Ergebnisse,3,0)*AD295^VLOOKUP($AD$292,Matrix_Ergebnisse,3,0)+VLOOKUP($AD$291,Matrix_Ergebnisse,4,0)*AD295^VLOOKUP($AD$292,Matrix_Ergebnisse,4,0)+VLOOKUP($AD$291,Matrix_Ergebnisse,5,0)*AD295^VLOOKUP($AD$292,Matrix_Ergebnisse,5,0)+VLOOKUP($AD$291,Matrix_Ergebnisse,6,0)*AD295^VLOOKUP($AD$292,Matrix_Ergebnisse,6,0))*$C$352","v":41.134526594315048},{"$f":"1/O295*AE295-1","v":7.4880597473736543E-6},{"$f":"1/$AG$291*E295","v":1},{"$f":"1/O295*AE295","v":1.0000074880597474}]
[{"$f":"Auslegetool!B46","v":4.5},{"$f":"Auslegetool!C46","v":120},96.944857405303324,{"$f":"VLOOKUP(A296,Matrix_Ergebnisse,7,0)*B296^VLOOKUP(A296,Matrix_Ergebnisse,8,0)","v":96.944857405303324},{"$f":"IF($F$1=2,D296,B296)","v":96.944857405303324},{"$f":"IF($F$1=2,B296,D296)","v":120},{"$f":"IF($F$1=2,E296*$C$213,E296)","v":96.944857405303324},{"$f":"IF($F$1=1,F296/$C$213^2,F296)","v":120},1.5977671256887627,154.89530616677845,{"$f":"G296*I296","v":154.89530616677845},{"$f":"Auslegung_BG800_kondensierend!AH52","v":1.431542005216897},{"$f":"Auslegung_BG800_kondensierend!AL52","v":0.93382245854282908},"H4,5",{"$f":"(VLOOKUP(A296,Matrix_Ergebnisse,3,0)*H296^VLOOKUP(N296,Matrix_Ergebnisse,3,0)+VLOOKUP(A296,Matrix_Ergebnisse,4,0)*H296^VLOOKUP(N296,Matrix_Ergebnisse,4,0)+VLOOKUP(A296,Matrix_Ergebnisse,5,0)*H296^VLOOKUP(N296,Matrix_Ergebnisse,5,0)+VLOOKUP(A296,Matrix_Ergebnisse,6,0)*H296^VLOOKUP(N296,Matrix_Ergebnisse,6,0))*$C$352","v":37.757955145535455},1,{"$f":"IF($A$252=$A$290,O296,O296*P296)","v":37.757955145535455},{"$f":"Q296*M296","v":35.259226503553784},54.052098821929476,{"$f":"VLOOKUP(A296,Matrix_Ergebnisse,17,0)*LN(F296)+VLOOKUP(A296,Matrix_Ergebnisse,18,0)+10*LOG($B$213/$B$213)","v":28.029613342122026},58.896333262093655,155.72819534846124,{"$f":"$D$228","v":45},{"$f":"$D$229","v":305},0.80605372973855705,41.022613505223546,22.320492596141335,{"$f":"1/Z296*AA296","v":0.54410215949062324},{"$f":"1/Z296*Q296*$C$352","v":0.92041807967031675},173.99655111742987,49.000728741583814,{"$f":"1/O296*AE296-1","v":0.29775906965072285},{"$f":"1/$AG$291*E296","v":1.2008464809177435},{"$f":"1/O296*AE296","v":1.2977590696507229}]
[{"$f":"Auslegetool!B47","v":4},{"$f":"Auslegetool!C47","v":120},60.780258355806176,60.780258355806176,60.780258355806176,120,60.780258355806176,120,1.6276072028144852,98.926386288835431,98.926386288835431,{"$f":"Auslegung_BG800_kondensierend!AH53","v":1.500638422150776},{"$f":"Auslegung_BG800_kondensierend!AL53","v":0.95423647266969258},"H4",26.303715133112355,1,26.303715133112355,25.099964346729546,39.472365574057214,{"$f":"VLOOKUP(A297,Matrix_Ergebnisse,17,0)*LN(F297)+VLOOKUP(A297,Matrix_Ergebnisse,18,0)+10*LOG($B$213/$B$213*(D107/D106))","v":26.913996752316265},36.630806586501116,98.381681885788808,45,305,0.80605372973855716,29.351391816913299,17.547885518013025,0.59785531219345178,0.89616585466162568,67.444862186503812,28.164543973614087,{"$f":"1/O297*AE297-1","v":7.0743955030110328E-2},0.7528791243737325,{"$f":"1/O297*AE297","v":1.0707439550301103}]
[{"$f":"Auslegetool!B48","v":3.5},{"$f":"Auslegetool!C48","v":120},60.65828271271986,60.65828271271986,60.65828271271986,120,60.65828271271986,120,1.3456870105038172,81.627063125975369,81.627063125975369,{"$f":"Auslegung_BG800_kondensierend!AH54","v":1.5218505309956356},{"$f":"Auslegung_BG800_kondensierend!AL54","v":0.96083516452126294},"H3,5",20.198804008772065,1,20.198804008772065,19.407721172901251,30.73956060622654,28.020321973295566,36.272124446051805,98.918243580174746,45,305,0.80605372973855705,25.09940013834094,15.523668382064885,0.61848762506285915,0.8047524601162519,67.170395260763343,28.078827497634418,0.39012327093426746,0.75136822399512337,{"$f":"1/O298*AE298","v":1.3901232709342675}]
[{"$f":"Auslegetool!B49","v":3},{"$f":"Auslegetool!C49","v":120},39.963087522579428,{"$f":"VLOOKUP(A299,Matrix_Ergebnisse,7,0)*B299^VLOOKUP(A299,Matrix_Ergebnisse,8,0)","v":39.963087522579428},39.963087522579428,120,39.963087522579428,120,2.1607673299501133,86.350933922726639,86.350933922726639,{"$f":"Auslegung_BG800_kondensierend!AH55","v":1.5160778851913599},{"$f":"Auslegung_BG800_kondensierend!AL55","v":0.95902503721811339},"H3",21.62034877106791,1,21.62034877106791,20.734455784841995,32.778132641940253,{"$f":"VLOOKUP(A299,Matrix_Ergebnisse,17,0)*LN(F299)+VLOOKUP(A299,Matrix_Ergebnisse,18,0)+10*LOG($B$213/$B$213*(D137/D136))","v":28.350831416141009},23.723945867037322,65.621458991696059,45,305,0.80605372973855705,26.293572146444326,16.10894038351643,0.61265697539293229,0.82226745953921765,28.793385541619394,13.884957918723281,-0.35778288936282276,0.49501886229472181,{"$f":"1/O299*AE299","v":0.64221711063717724}]
[{"$f":"Auslegetool!B50","v":2.5},{"$f":"Auslegetool!C50","v":120},50.618740670748814,50.618740670748814,50.618740670748814,120,50.618740670748814,120,1.5765376052182374,79.802348196225324,79.802348196225324,{"$f":"Auslegung_BG800_kondensierend!AH56","v":1.5240756803566906},{"$f":"Auslegung_BG800_kondensierend!AL56","v":0.96153573290491057},"H2,5",19.813206921650636,1,19.813206921650636,19.051106438605991,30.196826819162585,26.26541587621108,30.020574634206334,83.195117726866584,45,305,0.80605372973855705,24.63129503794131,15.2906113199261,0.62077983704766226,0.8043916038978447,46.523140578089006,21.008337558006481,6.0319898796891813E-2,0.6270093971960532,{"$f":"1/O300*AE300","v":1.0603198987968918}]
[{"$f":"Auslegetool!B51","v":2},{"$f":"Auslegetool!C51","v":120},19.714783300680438,19.714783300680438,19.714783300680438,120,19.714783300680438,120,3.2339169965202519,63.7559727987841,63.7559727987841,{"$f":"Auslegung_BG800_kondensierend!AH57","v":1.5435105748695772},{"$f":"Auslegung_BG800_kondensierend!AL57","v":0.96772069093466051},"H2",12.480288994803733,1,12.480288994803733,12.077433889115708,19.263458040907967,{"$f":"VLOOKUP(A301,Matrix_Ergebnisse,17,0)*LN(F301)+VLOOKUP(A301,Matrix_Ergebnisse,18,0)+10*LOG($B$213/$B$213*(D167/D166))","v":20.854605102651437},11.395074504856202,33.205777924310411,45,305,0.80605372973855727,20.346128254429384,13.060341639261571,0.64190795791421962,0.61339871835747195,6.8608232203697046,3.5849719174690882,-0.71274928657808168,0.24420509537396978,0.28725071342191832]
[{"$f":"Auslegetool!B52","v":2},{"$f":"Auslegetool!C52","v":120},19.714783300680438,19.714783300680438,19.714783300680438,120,19.714783300680438,120,3.2339169965202519,63.7559727987841,63.7559727987841,{"$f":"Auslegung_BG800_kondensierend!AH58","v":1.5435105748695772},{"$f":"Auslegung_BG800_kondensierend!AL58","v":0.96772069093466051},"H2",12.480288994803733,1,12.480288994803733,12.077433889115708,19.263458040907967,23.502783332746802,11.395074504856202,33.205777924310411,45,305,0.80605372973855727,20.346128254429384,13.060341639261571,0.64190795791421962,0.61339871835747195,6.8608232203697046,3.5849719174690882,-0.71274928657808168,0.24420509537396978,0.28725071342191832]
[{"$f":"Auslegetool!B53","v":2},{"$f":"Auslegetool!C53","v":120},19.714783300680438,19.714783300680438,19.714783300680438,120,19.714783300680438,120,3.2339169965202519,63.7559727987841,63.7559727987841,{"$f":"Auslegung_BG800_kondensierend!AH59","v":1.5435105748695772},{"$f":"Auslegung_BG800_kondensierend!AL59","v":0.96772069093466051},"H2",12.480288994803733,1,12.480288994803733,12.077433889115708,19.263458040907967,23.502783332746802,11.395074504856202,33.205777924310411,45,305,0.80605372973855727,20.346128254429384,13.060341639261571,0.64190795791421962,0.61339871835747195,6.8608232203697046,3.5849719174690882,-0.71274928657808168,0.24420509537396978,0.28725071342191832]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,46.025708300255808,1.2344512357359014,56.816492486870914,52.324181429910418,78.63941403283124,34.142504800111269]
[]
[{"$f":"A214","v":"Baugröße 1000"},null,null,"DpK =",{"$f":"H236","v":33.328818321761396},"[kPa]"]
[null,null,null,"DpH =",{"$f":"I236","v":1.8},"[kPa]",null,null,null,null,null,null,null,null,"mit evtl. Korrektur 2L bzw. 4L",null,null,null,null,null,"Grenzwerte Auslegung","Grenzwerte Auslegung","Grenzwerte Auslegung","Grenzwerte Auslegung","Korrektur heizen / kühlen\n (da anderer Massenstrom) bei gleichem Wärmetauscher",null,null,"Korrektur Heizen / Kühlen 4 Leiter",null,{"$f":"AD291","v":5},null,"Abweichung \"mit Schieber\" zu \"ohne Schieber\""]
[{"$f":"CONCATENATE(\"bei \", ROUND($B$3,0), \" kg/h Kühlwassermassenstrom\")","v":"bei 200 kg/h Kühlwassermassenstrom"},null,null,null,null,null,null,null,null,"für kondensierende Auslegung",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"AD292","v":"H5"}]
["Schieberstellung",{"$f":"CONCATENATE($H$2,\" (\", $A$309,\" = \", $A$252,\")\")","v":"Primärdruck (Baugröße 1000 = Baugröße 800)"},{"$f":"IF($F$1=2,G312,H312)","v":"Primärvolumenstrom Baugröße 1000"},{"$f":"CONCATENATE($S$61,\" \", $A$252)","v":"Primärvolumenstrom Baugröße 800"},{"$f":"CONCATENATE(\"Primärvolumenstrom \", $A$252)","v":"Primärvolumenstrom Baugröße 800"},{"$f":"CONCATENATE(\"Primärdruck \", $A$252)","v":"Primärdruck Baugröße 800"},{"$f":"CONCATENATE(\"Primärvolumenstrom \", $A$309)","v":"Primärvolumenstrom Baugröße 1000"},{"$f":"CONCATENATE(\"Primärdruck \", $A$309)","v":"Primärdruck Baugröße 1000"},"Induktionsverhältnis i",{"$f":"CONCATENATE(\"Sekundärvolumenstrom - \",$A$252)","v":"Sekundärvolumenstrom - Baugröße 800"},{"$f":"CONCATENATE(\"Sekundärvolumenstrom - \",A309)","v":"Sekundärvolumenstrom - Baugröße 1000"},"Korrektur Total \nbei Sollwassermenge","Korrektur Sensibel\nbei Sollwassermenge","Zelle","qSK1)  - aus Primärdruck der gemessenen BG","Korrektur Baugröße","qSK1)  - BG korrigiert","qSK2)  - BG und Kondsations berücksichtigt","qtotoal2)  - BG und Kondsations berücksichtigt","Schallleistungspegel","Primärvolumenstrom Minimal","Primärvolumenstrom Minimal","Primärdruck Minimal","Primärdruck Maximal","Korrektur heizen (bei anderem Massenstrom, gleicher WT)","spez. Leistung Eurocoil 4L kühlen","spez. Leistung Eurocoil 4L heizen","Korrektur Heizen / Kühlen 4 Leiter","Leistung (messung) zu Leistung Eurocoil",{"$f":"CONCATENATE(\"Primärdruck \", $A$290, \"; S\",AD310)","v":"Primärdruck Baugröße 800; S5"},"qSK1)  - aus Primärdruck der gemessenen BG","Kühlleistung \"mit\" Schieber im Vergleich zu \"ohne Schieber\""]
["[-]",{"$f":"$G$2","v":"Pa"},{"$f":"IF($F$1=2,G313,H313)","v":"[m³/h]"},{"$f":"$T$61","v":"[m³/h]"},"[m³/h]","[Pa]","[m³/h]","[Pa]","[-]","[m³/h]","[m³/h]","[-]","[-]","[-]","[W/K]","[-]","[W/K]","[W/K]","[W/K]","[dB(A)]","[m³/h]","[m³/h]","[m³/h]","[m³/h]","[-]","[-]","[-]","[-]","[-]","[Pa]","[W/K]"]
[{"$f":"Auslegetool!B64","v":5},{"$f":"Auslegetool!C64","v":120},96.482713639113214,{"$f":"VLOOKUP(A314,Matrix_Ergebnisse,7,0)*B314^VLOOKUP(A314,Matrix_Ergebnisse,8,0)","v":80.73043386129882},{"$f":"IF($F$1=2,D314,B314)","v":80.73043386129882},{"$f":"IF($F$1=2,B314,D314)","v":120},{"$f":"IF($F$1=2,E314*$C$214,E314)","v":96.482713639113214},{"$f":"IF($F$1=1,F314/$C$214^2,F314)","v":120},{"$f":"VLOOKUP(A314,Matrix_Ergebnisse,9,0)*B314^VLOOKUP(N314,Matrix_Ergebnisse,9,0)+VLOOKUP(A314,Matrix_Ergebnisse,10,0)*B314^VLOOKUP(N314,Matrix_Ergebnisse,10,0)+VLOOKUP(A314,Matrix_Ergebnisse,11,0)*B314^VLOOKUP(N314,Matrix_Ergebnisse,11,0)","v":2.0317546050552298},{"$f":"E314*I314","v":164.02443076580053},{"$f":"G314*I314","v":196.0291977444933},{"$f":"Auslegung_BG800_kondensierend!AH70","v":1.4203588067994268},{"$f":"Auslegung_BG800_kondensierend!AL70","v":0.93069193474908996},{"$f":"CONCATENATE(\"H\",A314)","v":"H5"},{"$f":"(VLOOKUP(A314,Matrix_Ergebnisse,3,0)*H314^VLOOKUP(N314,Matrix_Ergebnisse,3,0)+VLOOKUP(A314,Matrix_Ergebnisse,4,0)*H314^VLOOKUP(N314,Matrix_Ergebnisse,4,0)+VLOOKUP(A314,Matrix_Ergebnisse,5,0)*H314^VLOOKUP(N314,Matrix_Ergebnisse,5,0)+VLOOKUP(A314,Matrix_Ergebnisse,6,0)*H314^VLOOKUP(N314,Matrix_Ergebnisse,6,0))*$C$352","v":41.134218578828666},{"$f":"$R$243*O314^$R$240+$S$243*O314^$S$240+$T$243*O314^$T$240+$U$243*O314^$U$240+$V$243*O314^$V$240+$W$243*O314^$W$240+$X$243*O314^$X$240","v":1.2381056168237654},{"$f":"IF($A$252=$A$309,O314,O314*P314)","v":50.928507066104252},{"$f":"Q314*M314","v":47.398750775235264},{"$f":"Q314*L314","v":72.336753528488018},{"$f":"VLOOKUP(A314,Matrix_Ergebnisse,17,0)*LN(F314)+VLOOKUP(A314,Matrix_Ergebnisse,18,0)+10*LOG($B$214/$B$213*(D77/D76))","v":29.057232918327411},{"$f":"VLOOKUP(A314,Matrix_Ergebnisse,12,0)*$C$214","v":59.513593159203481},{"$f":"VLOOKUP(A314,Matrix_Ergebnisse,13,0)*$C$214","v":152.76083145436922},{"$f":"$D$228","v":45},{"$f":"$D$229","v":305},{"$f":"(VLOOKUP(A314,Matrix_Ergebnisse,26,0))","v":0.80605372973855705},{"$f":"$R$237*K314^$R$234+$S$237*K314^$S$234+$T$237*K314^$T$234+$U$237*K314^$U$234+$V$237*K314^$V$234+$W$237*K314^$W$234+$X$237*K314^$X$234","v":50.375429939655938},{"$f":"$R$230*K314^$R$227+$S$230*K314^$S$227+$T$230*K314^$T$227+$U$230*K314^$U$227+$V$230*K314^$V$227+$W$230*K314^$W$227+$X$230*K314^$X$227","v":27.150348623065099},{"$f":"1/Z314*AA314","v":0.53896013702688272},{"$f":"1/Z314*Q314*$C$352","v":1.0109791048356478},{"$f":"VLOOKUP($AD$310,Matrix_Ergebnisse,14,0)*E314^VLOOKUP($AD$310,Matrix_Ergebnisse,15,0)","v":120.00162820198784},{"$f":"(VLOOKUP($AD$310,Matrix_Ergebnisse,3,0)*AD314^VLOOKUP($AD$311,Matrix_Ergebnisse,3,0)+VLOOKUP($AD$310,Matrix_Ergebnisse,4,0)*AD314^VLOOKUP($AD$311,Matrix_Ergebnisse,4,0)+VLOOKUP($AD$310,Matrix_Ergebnisse,5,0)*AD314^VLOOKUP($AD$311,Matrix_Ergebnisse,5,0)+VLOOKUP($AD$310,Matrix_Ergebnisse,6,0)*AD314^VLOOKUP($AD$311,Matrix_Ergebnisse,6,0))*$C$352","v":41.134526594315048},{"$f":"1/AE314*O314-1","v":-7.488003676781041E-6}]
[{"$f":"Auslegetool!B65","v":4.5},{"$f":"Auslegetool!C65","v":120},115.86092714292349,96.944857405303324,{"$f":"IF($F$1=2,D315,B315)","v":96.944857405303324},{"$f":"IF($F$1=2,B315,D315)","v":120},{"$f":"IF($F$1=2,E315*$C$214,E315)","v":115.86092714292349},{"$f":"IF($F$1=1,F315/$C$214^2,F315)","v":120},1.5977671256887627,154.89530616677845,185.118780540784,{"$f":"Auslegung_BG800_kondensierend!AH71","v":1.431542005216897},{"$f":"Auslegung_BG800_kondensierend!AL71","v":0.93382245854282908},"H4,5",37.757955145535455,1.2403619101060737,46.83352936601581,43.734201534810666,67.044164540010698,{"$f":"VLOOKUP(A315,Matrix_Ergebnisse,17,0)*LN(F315)+VLOOKUP(A315,Matrix_Ergebnisse,18,0)+10*LOG($B$214/$B$213)","v":28.803735575209807},70.388300727868028,186.11418468474636,{"$f":"$D$228","v":45},{"$f":"$D$229","v":305},0.80605372973855705,48.49935893920378,26.483704903409706,{"$f":"1/Z315*AA315","v":0.54606298892750871},{"$f":"1/Z315*Q315*$C$352","v":0.96565254449494553},173.99655111742987,49.000728741583814,{"$f":"1/AE315*O315-1","v":-0.22944094679366123}]
[{"$f":"Auslegetool!B66","v":4},{"$f":"Auslegetool!C66","v":120},72.639820961817136,60.780258355806176,60.780258355806176,120,72.639820961817136,120,1.6276072028144852,98.926386288835431,118.22909580860819,{"$f":"Auslegung_BG800_kondensierend!AH72","v":1.500638422150776},{"$f":"Auslegung_BG800_kondensierend!AL72","v":0.95423647266969258},"H4",26.303715133112355,1.2461468530768973,32.77829183735912,31.278241583019344,49.188364143612255,{"$f":"VLOOKUP(A316,Matrix_Ergebnisse,17,0)*LN(F316)+VLOOKUP(A316,Matrix_Ergebnisse,18,0)+10*LOG($B$214/$B$213*(D107/D106))","v":27.688118985404049},43.778281042403769,117.57810761960125,45,305,0.80605372973855716,34.851136435232874,21.113736311742006,0.60582633656666074,0.94052289796271304,67.444862186503812,28.164543973614087,-6.606990840132354E-2]
[{"$f":"Auslegetool!B67","v":3.5},{"$f":"Auslegetool!C67","v":120},72.494045193250557,60.65828271271986,60.65828271271986,120,72.494045193250557,120,1.3456870105038172,81.627063125975369,97.55429495543396,{"$f":"Auslegung_BG800_kondensierend!AH73","v":1.5218505309956356},{"$f":"Auslegung_BG800_kondensierend!AL73","v":0.96083516452126294},"H3,5",20.198804008772065,1.2480430298483789,25.208976554421469,24.221671135080211,38.364294355202837,28.794444206383346,43.349612142842396,118.21936427874542,45,305,0.80605372973855705,29.810048735420956,18.800113598623028,0.63066363176670426,0.84565365116185165,67.170395260763343,28.078827497634418,-0.28063933543970909]
[{"$f":"Auslegetool!B68","v":3},{"$f":"Auslegetool!C68","v":120},47.760763136741268,39.963087522579428,39.963087522579428,120,47.760763136741268,120,2.1607673299501133,86.350933922726639,103.19989663935623,{"$f":"Auslegung_BG800_kondensierend!AH74","v":1.5160778851913599},{"$f":"Auslegung_BG800_kondensierend!AL74","v":0.95902503721811339},"H3",21.62034877106791,1.2476683400961834,26.975024663498857,25.869724031871517,40.896238344822123,{"$f":"VLOOKUP(A318,Matrix_Ergebnisse,17,0)*LN(F318)+VLOOKUP(A318,Matrix_Ergebnisse,18,0)+10*LOG($B$214/$B$213*(D137/D136))","v":29.124953649228789},28.353008475239726,78.425646112026996,45,305,0.80605372973855705,31.2279723407784,19.472331794937521,0.62355415146535087,0.86380967579742862,28.793385541619394,13.884957918723281,0.55710581894625544]
[{"$f":"Auslegetool!B69","v":2.5},{"$f":"Auslegetool!C69","v":120},60.495568118699801,50.618740670748814,50.618740670748814,120,60.495568118699801,120,1.5765376052182374,79.802348196225324,95.373538088171728,{"$f":"Auslegung_BG800_kondensierend!AH75","v":1.5240756803566906},{"$f":"Auslegung_BG800_kondensierend!AL75","v":0.96153573290491057},"H2,5",19.813206921650636,1.2481382877201643,24.729622161434332,23.77841536945628,37.689815720651922,27.03953810929886,35.878247733563668,99.428311429669819,45,305,0.80605372973855705,29.253870443926143,18.53166430526759,0.63347734928918586,0.84534530939542185,46.523140578089006,21.008337558006481,-5.6888396478586234E-2]
[{"$f":"Auslegetool!B70","v":2},{"$f":"Auslegetool!C70","v":120},23.561570286179059,19.714783300680438,19.714783300680438,120,23.561570286179059,120,3.2339169965202519,63.7559727987841,76.196162613180988,{"$f":"Auslegung_BG800_kondensierend!AH76","v":1.5435105748695772},{"$f":"Auslegung_BG800_kondensierend!AL76","v":0.96772069093466051},"H2",12.480288994803733,1.2495365857511807,15.59457769975509,15.091195506441245,24.070395590197268,{"$f":"VLOOKUP(A320,Matrix_Ergebnisse,17,0)*LN(F320)+VLOOKUP(A320,Matrix_Ergebnisse,18,0)+10*LOG($B$214/$B$213*(D167/D166))","v":21.628727335739217},13.618503676535461,39.68495410466366,45,305,0.80605372973855727,24.155625793026289,15.940039494852634,0.65988932066725881,0.64558781599677006,6.8608232203697046,3.5849719174690882,2.4812794303879917]
[{"$f":"Auslegetool!B71","v":2},{"$f":"Auslegetool!C71","v":120},23.561570286179059,19.714783300680438,19.714783300680438,120,23.561570286179059,120,3.2339169965202519,63.7559727987841,76.196162613180988,{"$f":"Auslegung_BG800_kondensierend!AH77","v":1.5435105748695772},{"$f":"Auslegung_BG800_kondensierend!AL77","v":0.96772069093466051},"H2",12.480288994803733,1.2495365857511807,15.59457769975509,15.091195506441245,24.070395590197268,24.276905565834582,13.618503676535461,39.68495410466366,45,305,0.80605372973855727,24.155625793026289,15.940039494852634,0.65988932066725881,0.64558781599677006,6.8608232203697046,3.5849719174690882,2.4812794303879917]
[{"$f":"Auslegetool!B72","v":2},{"$f":"Auslegetool!C72","v":120},23.561570286179059,19.714783300680438,19.714783300680438,120,23.561570286179059,120,3.2339169965202519,63.7559727987841,76.196162613180988,{"$f":"Auslegung_BG800_kondensierend!AH78","v":1.5435105748695772},{"$f":"Auslegung_BG800_kondensierend!AL78","v":0.96772069093466051},"H2",12.480288994803733,1.2495365857511807,15.59457769975509,15.091195506441245,24.070395590197268,24.276905565834582,13.618503676535461,39.68495410466366,45,305,0.80605372973855727,24.155625793026289,15.940039494852634,0.65988932066725881,0.64558781599677006,6.8608232203697046,3.5849719174690882,2.4812794303879917]
[]
[]
[]
[]
[]
[{"$f":"A215","v":"Baugröße 1200"},null,null,"DpK =",{"$f":"H237","v":37.174451205041549},"[kPa]"]
[null,null,null,"DpH =",{"$f":"I237","v":2.1090909090909089},"[kPa]",null,null,null,null,null,null,null,null,"mit evtl. Korrektur 2L bzw. 4L",null,null,null,null,null,"Grenzwerte Auslegung","Grenzwerte Auslegung","Grenzwerte Auslegung","Grenzwerte Auslegung","Korrektur heizen / kühlen\n (da anderer Massenstrom) bei gleichem Wärmetauscher",null,null,"Korrektur Heizen / Kühlen 4 Leiter"]
[{"$f":"CONCATENATE(\"bei \", ROUND($B$3,0), \" kg/h Kühlwassermassenstrom\")","v":"bei 200 kg/h Kühlwassermassenstrom"},null,null,null,null,null,null,null,null,"für kondensierende Auslegung"]
["Schieberstellung",{"$f":"CONCATENATE($H$2,\" (\", $A$328,\" = \", $A$252,\")\")","v":"Primärdruck (Baugröße 1200 = Baugröße 800)"},{"$f":"IF($F$1=2,G331,H331)","v":"Primärvolumenstrom Baugröße 1200"},{"$f":"CONCATENATE($S$61,\" \", $A$252)","v":"Primärvolumenstrom Baugröße 800"},{"$f":"CONCATENATE(\"Primärvolumenstrom \", $A$252)","v":"Primärvolumenstrom Baugröße 800"},{"$f":"CONCATENATE(\"Primärdruck \", $A$252)","v":"Primärdruck Baugröße 800"},{"$f":"CONCATENATE(\"Primärvolumenstrom \", $A$328)","v":"Primärvolumenstrom Baugröße 1200"},{"$f":"CONCATENATE(\"Primärdruck \", $A$328)","v":"Primärdruck Baugröße 1200"},"Induktionsverhältnis i",{"$f":"CONCATENATE(\"Sekundärvolumenstrom - \",$A$252)","v":"Sekundärvolumenstrom - Baugröße 800"},{"$f":"CONCATENATE(\"Sekundärvolumenstrom - \",A328)","v":"Sekundärvolumenstrom - Baugröße 1200"},"Korrektur Total \nbei Sollwassermenge","Korrektur Sensibel\nbei Sollwassermenge","Zelle","qSK1)  - aus Primärdruck der gemessenen BG","Korrektur Baugröße","qSK1)  - BG korrigiert","qSK2)  - BG und Kondsations berücksichtigt","qtotoal2)  - BG und Kondsations berücksichtigt","Schallleistungspegel","Primärvolumenstrom Minimal","Primärvolumenstrom Minimal","Primärdruck Minimal","Primärdruck Maximal","Korrektur heizen (bei anderem Massenstrom, gleicher WT)","spez. Leistung Eurocoil 4L kühlen","spez. Leistung Eurocoil 4L heizen","Korrektur Heizen / Kühlen 4 Leiter","Leistung (messung) zu Leistung Eurocoil"]
["[-]",{"$f":"$T$61","v":"[m³/h]"},{"$f":"IF($F$1=2,G332,H332)","v":"[m³/h]"},{"$f":"$T$61","v":"[m³/h]"},"[m³/h]","[Pa]","[m³/h]","[Pa]","[-]","[m³/h]","[m³/h]","[-]","[-]","[-]","[W/K]","[-]","[W/K]","[W/K]","[W/K]","[dB(A)]","[m³/h]","[m³/h]","[m³/h]","[m³/h]","[-]","[-]","[-]","[-]","[-]"]
[{"$f":"Auslegetool!B83","v":5},{"$f":"Auslegetool!C83","v":120},118.14209833360803,{"$f":"VLOOKUP(A333,Matrix_Ergebnisse,7,0)*B333^VLOOKUP(A333,Matrix_Ergebnisse,8,0)","v":80.73043386129882},{"$f":"IF($F$1=2,D333,B333)","v":80.73043386129882},{"$f":"IF($F$1=2,B333,D333)","v":120},{"$f":"IF($F$1=2,E333*$C$215,E333)","v":118.14209833360803},{"$f":"IF($F$1=1,F333/$C$215^2,F333)","v":120},{"$f":"VLOOKUP(A333,Matrix_Ergebnisse,9,0)*B333^VLOOKUP(N333,Matrix_Ergebnisse,9,0)+VLOOKUP(A333,Matrix_Ergebnisse,10,0)*B333^VLOOKUP(N333,Matrix_Ergebnisse,10,0)+VLOOKUP(A333,Matrix_Ergebnisse,11,0)*B333^VLOOKUP(N333,Matrix_Ergebnisse,11,0)","v":2.0317546050552298},{"$f":"E333*I333","v":164.02443076580053},{"$f":"G333*I333","v":240.0357523401959},{"$f":"Auslegung_BG800_kondensierend!AH89","v":1.4203588067994268},{"$f":"Auslegung_BG800_kondensierend!AL89","v":0.93069193474908996},{"$f":"CONCATENATE(\"H\",A333)","v":"H5"},{"$f":"(VLOOKUP(A333,Matrix_Ergebnisse,3,0)*H333^VLOOKUP(N333,Matrix_Ergebnisse,3,0)+VLOOKUP(A333,Matrix_Ergebnisse,4,0)*H333^VLOOKUP(N333,Matrix_Ergebnisse,4,0)+VLOOKUP(A333,Matrix_Ergebnisse,5,0)*H333^VLOOKUP(N333,Matrix_Ergebnisse,5,0)+VLOOKUP(A333,Matrix_Ergebnisse,6,0)*H333^VLOOKUP(N333,Matrix_Ergebnisse,6,0))*$C$352","v":41.134218578828666},{"$f":"$R$244*O333^$R$240+$S$244*O333^$S$240+$T$244*O333^$T$240+$U$244*O333^$U$240+$V$244*O333^$V$240+$W$244*O333^$W$240+$X$244*O333^$X$240","v":1.4502083962971335},{"$f":"IF($A$252=$A$328,O333,O333*P333)","v":59.653189158138872},{"$f":"Q333*M333","v":55.518742031541706},{"$f":"Q333*L333","v":84.728932574434637},{"$f":"VLOOKUP(A333,Matrix_Ergebnisse,17,0)*LN(F333)+VLOOKUP(A333,Matrix_Ergebnisse,18,0)+10*LOG($B$215/$B$213*(D77/D76))","v":29.936784621878711},{"$f":"VLOOKUP(A333,Matrix_Ergebnisse,12,0)*$C$215","v":72.873787541881811},{"$f":"VLOOKUP(A333,Matrix_Ergebnisse,13,0)*$C$215","v":187.0540793318807},{"$f":"$D$228","v":45},{"$f":"$D$229","v":305},{"$f":"(VLOOKUP(A333,Matrix_Ergebnisse,26,0))","v":0.80605372973855705},{"$f":"$R$238*K333^$R$234+$S$238*K333^$S$234+$T$238*K333^$T$234+$U$238*K333^$U$234+$V$238*K333^$V$234+$W$238*K333^$W$234+$X$238*K333^$X$234","v":59.203585583916677},{"$f":"$R$231*K333^$R$227+$S$231*K333^$S$227+$T$231*K333^$T$227+$U$231*K333^$U$227+$V$231*K333^$V$227+$W$231*K333^$W$227+$X$231*K333^$X$227","v":31.570546851792706},{"$f":"1/Z333*AA333","v":0.5332539666376086},{"$f":"1/Z333*Q333*$C$352","v":1.0075941950101133}]
[{"$f":"Auslegetool!B84","v":4.5},{"$f":"Auslegetool!C84","v":120},141.8705230321512,96.944857405303324,{"$f":"IF($F$1=2,D334,B334)","v":96.944857405303324},{"$f":"IF($F$1=2,B334,D334)","v":120},{"$f":"IF($F$1=2,E334*$C$215,E334)","v":141.8705230321512},{"$f":"IF($F$1=1,F334/$C$215^2,F334)","v":120},1.5977671256887627,154.89530616677845,226.67605780504161,{"$f":"Auslegung_BG800_kondensierend!AH90","v":1.431542005216897},{"$f":"Auslegung_BG800_kondensierend!AL90","v":0.93382245854282908},"H4,5",37.757955145535455,1.4548047067032923,54.930450861216777,51.295288672087516,78.635247773334498,{"$f":"VLOOKUP(A334,Matrix_Ergebnisse,17,0)*LN(F334)+VLOOKUP(A334,Matrix_Ergebnisse,18,0)+10*LOG($B$215/$B$213)","v":29.683287278761107},86.189755993307784,227.89492002213839,{"$f":"$D$228","v":45},{"$f":"$D$229","v":305},0.80605372973855705,57.160512761292175,30.838081304293937,{"$f":"1/Z334*AA334","v":0.53949973180046062},{"$f":"1/Z334*Q334*$C$352","v":0.96098597104283601}]
[{"$f":"Auslegetool!B85","v":4},{"$f":"Auslegetool!C85","v":120},88.946719545082203,60.780258355806176,60.780258355806176,120,88.946719545082203,120,1.6276072028144852,98.926386288835431,144.77032139829575,{"$f":"Auslegung_BG800_kondensierend!AH91","v":1.500638422150776},{"$f":"Auslegung_BG800_kondensierend!AL91","v":0.95423647266969258},"H4",26.303715133112355,1.4643107962126862,38.516814049919439,36.754148777469581,57.799811062145949,{"$f":"VLOOKUP(A335,Matrix_Ergebnisse,17,0)*LN(F335)+VLOOKUP(A335,Matrix_Ergebnisse,18,0)+10*LOG($B$215/$B$213*(D107/D106))","v":28.567670688955349},53.606058419269921,143.97319300359337,45,305,0.80605372973855716,41.670979134392731,25.06786488727117,0.60156649562816866,0.92430787204925469]
[{"$f":"Auslegetool!B86","v":3.5},{"$f":"Auslegetool!C86","v":120},88.768218603980287,60.65828271271986,60.65828271271986,120,88.768218603980287,120,1.3456870105038172,81.627063125975369,119.45423872093957,{"$f":"Auslegung_BG800_kondensierend!AH92","v":1.5218505309956356},{"$f":"Auslegung_BG800_kondensierend!AL92","v":0.96083516452126294},"H3,5",20.198804008772065,1.4651874509233609,29.595034157313304,28.435949513554526,45.039218447141224,29.673995909934646,53.081157725929472,144.75840523928011,45,305,0.80605372973855705,35.746756642948696,22.549890009635259,0.63082338447852959,0.82790823382716972]
[{"$f":"Auslegetool!B87","v":3},{"$f":"Auslegetool!C87","v":120},58.482567106213793,39.963087522579428,39.963087522579428,120,58.482567106213793,120,2.1607673299501133,86.350933922726639,126.36722037472191,{"$f":"Auslegung_BG800_kondensierend!AH93","v":1.5160778851913599},{"$f":"Auslegung_BG800_kondensierend!AL93","v":0.95902503721811339},"H3",21.62034877106791,1.4652490821578974,31.679196192740879,30.381142307783236,48.028128768452774,{"$f":"VLOOKUP(A337,Matrix_Ergebnisse,17,0)*LN(F337)+VLOOKUP(A337,Matrix_Ergebnisse,18,0)+10*LOG($B$215/$B$213*(D137/D136))","v":30.00450535278009},34.717969561518032,96.031403402482042,45,305,0.80605372973855705,37.421003377699819,23.28654156450277,0.62228533343870318,0.84656191265088754]
[{"$f":"Auslegetool!B88","v":2.5},{"$f":"Auslegetool!C88","v":120},74.07620585963241,50.618740670748814,50.618740670748814,120,74.07620585963241,120,1.5765376052182374,79.802348196225324,116.78392418959804,{"$f":"Auslegung_BG800_kondensierend!AH94","v":1.5240756803566906},{"$f":"Auslegung_BG800_kondensierend!AL94","v":0.96153573290491057},"H2,5",19.813206921650636,1.465143107977831,29.029183568195087,27.912597297875649,44.242672696896193,27.91908981285016,43.932548245180001,121.74895277102426,45,305,0.80605372973855705,35.088538698515308,22.254436415645088,0.63423662657649327,0.82731241154318547]
[{"$f":"Auslegetool!B89","v":2},{"$f":"Auslegetool!C89","v":120},28.850902391239664,19.714783300680438,19.714783300680438,120,28.850902391239664,120,3.2339169965202519,63.7559727987841,93.30142360797673,{"$f":"Auslegung_BG800_kondensierend!AH95","v":1.5435105748695772},{"$f":"Auslegung_BG800_kondensierend!AL95","v":0.96772069093466051},"H2",12.480288994803733,1.4621120453287422,18.247580868486278,17.658561565937632,28.165334036296354,{"$f":"VLOOKUP(A339,Matrix_Ergebnisse,17,0)*LN(F339)+VLOOKUP(A339,Matrix_Ergebnisse,18,0)+10*LOG($B$215/$B$213*(D167/D166))","v":22.508279039290517},16.675718787594441,48.593821352649378,45,305,0.80605372973855727,29.021729257124626,19.362156406244601,0.66716067242930854,0.62875580937364817]
[{"$f":"Auslegetool!B90","v":2},{"$f":"Auslegetool!C90","v":120},28.850902391239664,19.714783300680438,19.714783300680438,120,28.850902391239664,120,3.2339169965202519,63.7559727987841,93.30142360797673,{"$f":"Auslegung_BG800_kondensierend!AH96","v":1.5435105748695772},{"$f":"Auslegung_BG800_kondensierend!AL96","v":0.96772069093466051},"H2",12.480288994803733,1.4621120453287422,18.247580868486278,17.658561565937632,28.165334036296354,25.156457269385882,16.675718787594441,48.593821352649378,45,305,0.80605372973855727,29.021729257124626,19.362156406244601,0.66716067242930854,0.62875580937364817]
[{"$f":"Auslegetool!B91","v":2},{"$f":"Auslegetool!C91","v":120},28.850902391239664,19.714783300680438,19.714783300680438,120,28.850902391239664,120,3.2339169965202519,63.7559727987841,93.30142360797673,{"$f":"Auslegung_BG800_kondensierend!AH97","v":1.5435105748695772},{"$f":"Auslegung_BG800_kondensierend!AL97","v":0.96772069093466051},"H2",12.480288994803733,1.4621120453287422,18.247580868486278,17.658561565937632,28.165334036296354,25.156457269385882,16.675718787594441,48.593821352649378,45,305,0.80605372973855727,29.021729257124626,19.362156406244601,0.66716067242930854,0.62875580937364817]
[]
[]
[]
[]
[]
[]
[]
[]
["Abfrage "]
["2L",{"$f":"Auslegetool!AM11","v":false},{"$f":"Auslegetool!AN11","v":2}]
[null,"Korrektur",{"$f":"IF(C351=1,D360,1)","v":1}]
[]
[null,1,5,11]
[{"$f":"CONCATENATE($A$16,\" mit \",$H$17)","v":" mit "},{"$f":"CONCATENATE($A$16,\" mit \",$H$17)","v":" mit "},{"$f":"CONCATENATE($A$16,\" mit \",$H$17)","v":" mit "},{"$f":"CONCATENATE($A$16,\" mit \",$H$17)","v":" mit "}]
["Messung","Messung","Primärdruck [Pa]","spez. Kühlleistung [W/K]"]
[null,"Kontrolle","[Pa]","[W/K]"]
["V4",{"$f":"VLOOKUP($A358,Matrix_Rohdaten,B$354,0)","v":"V4"},150,45.27565994029851]
["V49","V49",150,50.487755106060604]
[null,null,"2 Leiter",{"$f":"1/D358*D359","v":1.1151191428823981}]

{"sheet":"BG;WT2,5;k","index":5,"n_rows":441,"n_cols":115,"rows_kept":441,"cut":false,"hidden":true,"merged":[]}
["TT",null,"Master auswählen ->","BG","WT","Verhältnis","DpK =","Verhältnis",{"$f":"CONCATENATE(\"Polynom 6 Ordnung - \",A3)","v":"Polynom 6 Ordnung - BG;WT2,5;k"},6,5,4,3,2,1,0]
["2017-08-14",null,null,"BG 800",{"$f":"VLOOKUP(D2,D3:F6,2,0)","v":820},{"$f":"VLOOKUP(D2,D3:F6,3,0)","v":1},{"$f":"VLOOKUP(D2,D3:G6,4,0)","v":22},{"$f":"VLOOKUP(E2,E3:H6,4,0)","v":1},{"$f":"D2","v":"BG 800"},{"$f":"VLOOKUP($I2,$I$3:$P$6,2,0)","v":4.6007795611198745E-16},{"$f":"VLOOKUP($I2,$I$3:$P$6,3,0)","v":-1.3695909307464427E-12},{"$f":"VLOOKUP($I2,$I$3:$P$6,4,0)","v":1.4148434158245012E-9},{"$f":"VLOOKUP($I2,$I$3:$P$6,5,0)","v":-4.2313510530365898E-7},{"$f":"VLOOKUP($I2,$I$3:$P$6,6,0)","v":-2.9140622930393968E-4},{"$f":"VLOOKUP($I2,$I$3:$P$6,7,0)","v":0.34015835446073489},{"$f":"VLOOKUP($I2,$I$3:$P$6,8,0)","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"  Datentabelle aus Eurocoil entnehmen"]
[{"$f":"MID(CELL(\"dateiname\",A1),FIND(\"]\",CELL(\"dateiname\",A1))+1,255)","v":"BG;WT2,5;k"},null,null,"BG 630",590,{"$f":"E3/$E$2","v":0.71951219512195119},{"$f":"BI18","v":18},{"$f":"G3/$G$2","v":0.81818181818181823},{"$f":"D3","v":"BG 630"},{"$f":"LINEST(AS18:AS117,AU18:AU117^{1,2,3,4,5,6},0,0)","v":4.0754116872129361E-17},2.4538746707244088E-14,-3.7851684969490067E-10,6.885048902602693E-7,-6.1199856110644721E-4,0.3529570250383019,0]
[null,null,null,"BG 800",820,{"$f":"E4/$E$2","v":1},{"$f":"CA18","v":22},{"$f":"G4/$G$2","v":1},{"$f":"D4","v":"BG 800"},{"$f":"LINEST(BK18:BK117,BM18:BM117^{1,2,3,4,5,6},0,0)","v":4.6007795611198745E-16},-1.3695909307464427E-12,1.4148434158245012E-9,-4.2313510530365898E-7,-2.9140622930393968E-4,0.34015835446073489,0]
["WT 4L",2.5,"mm","BG 1000",1020,{"$f":"E5/$E$2","v":1.2439024390243902},{"$f":"CS18","v":26},{"$f":"G5/$G$2","v":1.1818181818181819},{"$f":"D5","v":"BG 1000"},{"$f":"LINEST(CC18:CC117,CE18:CE117^{1,2,3,4,5,6},0,0)","v":3.8643260613551264E-16},-1.2131806326824018E-12,1.358964763365231E-9,-5.059710939947184E-7,-2.277576478546036E-4,0.34189407435782632,0]
["Länge",820,"mm","BG 1200",1200,{"$f":"E6/$E$2","v":1.4634146341463414},{"$f":"DK18","v":29},{"$f":"G6/$G$2","v":1.3181818181818181},{"$f":"D6","v":"BG 1200"},{"$f":"LINEST(CU18:CU116,CW18:CW116^{1,2,3,4,5,6},0,0)","v":5.6907660943630829E-16},-1.7892144299697382E-12,2.0715636603802355E-9,-9.4302767112261555E-7,-9.6974330483458386E-5,0.33631557592527878,0]
["Rohrreihen",3,null,null,null,null,"Wassermenge =",{"$f":"DF18","v":200}]
[null,null,null,null,null,null,null,null,{"$f":"CONCATENATE(\"Korrekturfaktoren - \",A3)","v":"Korrekturfaktoren - BG;WT2,5;k"},6,5,4,3,2,1,0]
[null,null,null,null,null,null,null,null,{"$f":"D3","v":"BG 630"},{"$f":"LINEST(G18:G117,C18:C117^{0,1,2,3,4,5,6},0,0)","v":3.4816233818189494E-13},-1.2563474610047514E-10,1.6251742736909859E-8,-9.3568170018377565E-7,3.4348469144301678E-5,-1.1160363694072517E-3,0.74734760780225895]
["Grenzen",null,null,null,null,null,null,null,{"$f":"D4","v":"BG 800"},{"$f":"LINEST(J18:J117,C18:C117^{0,1,2,3,4,5,6},0,0)","v":1.0475346449154691E-26},-4.8955168558711517E-24,8.4629729763327543E-22,-6.8854819969857664E-20,2.7225990865238E-18,-4.5667947962183834E-17,1.0000000000000002]
["Maximum",{"$f":"MAX(B18:B117)","v":1000},"m³/h",null,null,null,null,null,{"$f":"D5","v":"BG 1000"},{"$f":"LINEST(M18:M97,C18:C97^{0,1,2,3,4,5,6},0,0)","v":7.8693165984620388E-15},-2.935344341039698E-11,7.661484403257628E-9,-6.6987564862412183E-7,1.525204034465662E-5,-2.7499345363208601E-4,1.25171812029343]
[null,null,null,null,null,null,null,null,{"$f":"D6","v":"BG 1200"},{"$f":"LINEST(P18:P84,C18:C84^{0,1,2,3,4,5,6},0,0)","v":-4.7324727316282315E-13},8.3072357948498334E-11,-6.7343997792567237E-10,-2.8421661850020901E-7,-2.6365020864954163E-5,1.4753152096046846E-3,1.4483517003839317,null,null,null,null,null,null,null,null,null,null,null,null,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,null,null,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,null,null,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,null,null,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,null,null,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15]
[null,{"$f":"CONCATENATE(\"Master - \",AA13)","v":"Master - BG 800"},null,null,{"$f":"AS13","v":"BG630"},null,null,{"$f":"BK13","v":"BG 800"},null,null,{"$f":"CC13","v":"BG1000"},null,null,{"$f":"CU13","v":"BG1200"},null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"D2","v":"BG 800"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"BG630",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"BG 800",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"BG1000",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"BG1200"]
[null,"Volumen-nstrom","spez. \nLeistung","Korrektur-faktor","Volumen-nstrom","spez. \nLeistung","Korrektur-faktor","Volumen-nstrom","spez. \nLeistung","Korrektur-faktor","Volumen-nstrom","spez. \nLeistung","Korrektur-faktor","Volumen-nstrom","spez. \nLeistung","Korrektur-faktor",null,null,null,null,null,null,null,null,null,null,{"$f":"IF($AA$13=$AS$13,AS14,IF($AA$13=$BK$13,BK14,IF($AA$13=$CC$13,CC14,IF($AA$13=$CU$13,CU14,\"-\"))))","v":"q sensibel"},{"$f":"IF($AA$13=$AS$13,AT14,IF($AA$13=$BK$13,BL14,IF($AA$13=$CC$13,CD14,IF($AA$13=$CU$13,CV14,\"-\"))))","v":"S"},{"$f":"IF($AA$13=$AS$13,AU14,IF($AA$13=$BK$13,BM14,IF($AA$13=$CC$13,CE14,IF($AA$13=$CU$13,CW14,\"-\"))))","v":"QA"},{"$f":"IF($AA$13=$AS$13,AV14,IF($AA$13=$BK$13,BN14,IF($AA$13=$CC$13,CF14,IF($AA$13=$CU$13,CX14,\"-\"))))","v":"VA"},{"$f":"IF($AA$13=$AS$13,AW14,IF($AA$13=$BK$13,BO14,IF($AA$13=$CC$13,CG14,IF($AA$13=$CU$13,CY14,\"-\"))))","v":"DPA"},{"$f":"IF($AA$13=$AS$13,AX14,IF($AA$13=$BK$13,BP14,IF($AA$13=$CC$13,CH14,IF($AA$13=$CU$13,CZ14,\"-\"))))","v":"TAI"},{"$f":"IF($AA$13=$AS$13,AY14,IF($AA$13=$BK$13,BQ14,IF($AA$13=$CC$13,CI14,IF($AA$13=$CU$13,DA14,\"-\"))))","v":"UR"},{"$f":"IF($AA$13=$AS$13,AZ14,IF($AA$13=$BK$13,BR14,IF($AA$13=$CC$13,CJ14,IF($AA$13=$CU$13,DB14,\"-\"))))","v":"TAO"},{"$f":"IF($AA$13=$AS$13,BA14,IF($AA$13=$BK$13,BS14,IF($AA$13=$CC$13,CK14,IF($AA$13=$CU$13,DC14,\"-\"))))","v":"UR"},{"$f":"IF($AA$13=$AS$13,BB14,IF($AA$13=$BK$13,BT14,IF($AA$13=$CC$13,CL14,IF($AA$13=$CU$13,DD14,\"-\"))))","v":"PT"},{"$f":"IF($AA$13=$AS$13,BC14,IF($AA$13=$BK$13,BU14,IF($AA$13=$CC$13,CM14,IF($AA$13=$CU$13,DE14,\"-\"))))","v":"PS"},{"$f":"IF($AA$13=$AS$13,BD14,IF($AA$13=$BK$13,BV14,IF($AA$13=$CC$13,CN14,IF($AA$13=$CU$13,DF14,\"-\"))))","v":"QW"},{"$f":"IF($AA$13=$AS$13,BE14,IF($AA$13=$BK$13,BW14,IF($AA$13=$CC$13,CO14,IF($AA$13=$CU$13,DG14,\"-\"))))","v":"VW"},{"$f":"IF($AA$13=$AS$13,BF14,IF($AA$13=$BK$13,BX14,IF($AA$13=$CC$13,CP14,IF($AA$13=$CU$13,DH14,\"-\"))))","v":"TWI"},{"$f":"IF($AA$13=$AS$13,BG14,IF($AA$13=$BK$13,BY14,IF($AA$13=$CC$13,CQ14,IF($AA$13=$CU$13,DI14,\"-\"))))","v":"TWO"},null,{"$f":"IF($AA$13=$AS$13,BI14,IF($AA$13=$BK$13,CA14,IF($AA$13=$CC$13,CS14,IF($AA$13=$CU$13,DK14,\"-\"))))","v":"DPW"},null,"q sensibel","S","QA","VA","DPA","TAI","UR","TAO","UR","PT","PS","QW","VW","TWI","TWO",null,"DPW",null,"q sensibel","S","QA","VA","DPA","TAI","UR","TAO","UR","PT","PS","QW","VW","TWI","TWO",null,"DPW",null,"q sensibel","S","QA","VA","DPA","TAI","UR","TAO","UR","PT","PS","QW","VW","TWI","TWO",null,"DPW",null,"q sensibel","S","QA","VA","DPA","TAI","UR","TAO","UR","PT","PS","QW","VW","TWI","TWO",null,"DPW"]
[null,"[m³/h]","[W/K]","[-]","[m³/h]","[W/K]","[-]","[m³/h]","[W/K]","[-]","[m³/h]","[W/K]","[-]","[m³/h]","[W/K]","[-]",null,null,null,null,null,null,null,null,null,null,"W/K",0,"m3/h","m/s","Pa","°C"," % ","°C"," % ","kW","kW","l/h","m/s","°C","°C",null,"kPa",null,"W/K",null,"m3/h","m/s","Pa","°C"," % ","°C"," % ","kW","kW","l/h","m/s","°C","°C",null,"kPa",null,"W/K",null,"m3/h","m/s","Pa","°C"," % ","°C"," % ","kW","kW","l/h","m/s","°C","°C",null,"kPa",null,"W/K",null,"m3/h","m/s","Pa","°C"," % ","°C"," % ","kW","kW","l/h","m/s","°C","°C",null,"kPa",null,"W/K",null,"m3/h","m/s","Pa","°C"," % ","°C"," % ","kW","kW","l/h","m/s","°C","°C",null,"kPa"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,"S","QA","VA","DPA","TAI","RH","TAO","RH","QTOT","QSEN","QW","VW","TWI","TWO",null,"DPW",null,null,"S","QA","VA","DPA","TAI","RH","TAO","RH","QTOT","QSEN","QW","VW","TWI","TWO","GLI","DPW",null,null,"S","QA","VA","DPA","TAI","RH","TAO","RH","QTOT","QSEN","QW","VW","TWI","TWO","GLI","DPW",null,null,"S","QA","VA","DPA","TAI","RH","TAO","RH","QTOT","QSEN","QW","VW","TWI","TWO","GLI","DPW",null,null,"S","QA","VA","DPA","TAI","RH","TAO","RH","QTOT","QSEN","QW","VW","TWI","TWO","GLI","DPW"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,"m3/h","m/s","Pa","°C","%","°C","%","kW","kW","l/h","m/s","°C","°C",null,"kPa",null,null,null,"m3/h","m/s","Pa","°C","%","°C","%","kW","kW","l/h","m/s","°C","°C","%","kPa",null,null,null,"m3/h","m/s","Pa","°C","%","°C","%","kW","kW","l/h","m/s","°C","°C","%","kPa",null,null,null,"m3/h","m/s","Pa","°C","%","°C","%","kW","kW","l/h","m/s","°C","°C","%","kPa",null,null,null,"m3/h","m/s","Pa","°C","%","°C","%","kW","kW","l/h","m/s","°C","°C","%","kPa"]
[null,{"$f":"AC18","v":10},{"$f":"$J$4*B18^6+$K$4*B18^5+$L$4*B18^4+$M$4*B18^3+$N$4*B18^2+$O$4*B18","v":3.3720337985067945},{"$f":"1/C18*C18","v":1},{"$f":"IF($B18*$F$3>$B$11,\"\",$B18*$F$3)","v":7.1951219512195124},{"$f":"IF(E18>$B$11,\"\",$J$3*E18^6+$K$3*E18^5+$L$3*E18^4+$M$3*E18^3+$N$3*E18^2+$O$3*E18)","v":2.5081412550027307},{"$f":"IF(E18>$B$11,\"\",1/$C18*F18)","v":0.7438066771790327},{"$f":"IF($B18*$F$4>$B$11,\"\",$B18*$F$4)","v":10},{"$f":"IF(H18>$B$11,\"\",$J$4*H18^6+$K$4*H18^5+$L$4*H18^4+$M$4*H18^3+$N$4*H18^2+$O$4*H18)","v":3.3720337985067945},{"$f":"IF(H18>$B$11,\"\",1/$C18*I18)","v":1},{"$f":"IF($B18*$F$5>$B$11,\"\",$B18*$F$5)","v":12.439024390243903},{"$f":"IF(K18>$B$11,\"\",$J$5*K18^6+$K$5*K18^5+$L$5*K18^4+$M$5*K18^3+$N$5*K18^2+$O$5*K18)","v":4.2166462840098404},{"$f":"IF(K18>$B$11,\"\",1/$C18*L18)","v":1.2504756879593133},{"$f":"IF($B18*$F$6>$B$11,\"\",$B18*$F$6)","v":14.634146341463413},{"$f":"IF(N18>$B$11,\"\",$J$6*N18^6+$K$6*N18^5+$L$6*N18^4+$M$6*N18^3+$N$6*N18^2+$O$6*N18)","v":4.8980618471144588},{"$f":"IF(N18>$B$11,\"\",1/$C18*O18)","v":1.4525541971979701},null,null,null,null,null,null,null,null,null,null,3,0,10,0.02,0,26,45,16,83,0.03,0.03,200,0.8,16,16.3,null,22,null,{"$f":"BC18/(AX18-BF18)*1000","v":3},null,10,0.03,0,26,45,16,83,0.03,0.03,200,0.8,16,16.2,0,18,null,{"$f":"BU18/(BP18-BX18)*1000","v":3},null,10,0.02,0,26,45,16,83,0.03,0.03,200,0.8,16,16.3,0,22,null,{"$f":"CM18/(CH18-CP18)*1000","v":3},null,10,0.02,0,26,45,16,100,0.04,0.03,200,0.8,16,16.2,0,26,null,{"$f":"DE18/(CZ18-DH18)*1000","v":3},null,10,0.01,0,26,45,16,100,0.04,0.03,200,0.8,16,16.2,0,29]
[null,20,6.6834415383512358,{"$f":"1/C19*C19","v":0.99999999999999989},14.390243902439025,{"$f":"IF(E19>$B$11,\"\",$J$3*E19^6+$K$3*E19^5+$L$3*E19^4+$M$3*E19^3+$N$3*E19^2+$O$3*E19)","v":4.9544410270323116},{"$f":"IF(E19>$B$11,\"\",1/$C19*F19)","v":0.74130087000873834},20,{"$f":"IF(H19>$B$11,\"\",$J$4*H19^6+$K$4*H19^5+$L$4*H19^4+$M$4*H19^3+$N$4*H19^2+$O$4*H19)","v":6.6834415383512358},{"$f":"IF(H19>$B$11,\"\",1/$C19*I19)","v":0.99999999999999989},24.878048780487806,8.3574127349530016,1.2504654506209272,29.268292682926827,{"$f":"IF(N19>$B$11,\"\",$J$6*N19^6+$K$6*N19^5+$L$6*N19^4+$M$6*N19^3+$N$6*N19^2+$O$6*N19)","v":9.738149623680922},1.4570561540489309,null,null,null,null,null,null,null,null,null,null,6,0,20,0.04,0,26,45,16,83,0.06,0.06,200,0.8,16,16.399999999999999,null,22,null,6,null,20,0.05,0,26,45,16,83,0.06,0.06,200,0.8,16,16.3,0,18,null,6,null,20,0.04,0,26,45,16,83,0.06,0.06,200,0.8,16,16.399999999999999,0,22,null,6,null,20,0.03,0,26,45,16,83,0.06,0.06,200,0.8,16,16.399999999999999,0,26,null,6,null,20,0.03,0,26,45,16,83,0.06,0.06,200,0.8,16,16.399999999999999,0,29]
[null,30,9.9321734571093323,1,21.585365853658537,7.3404016359384219,0.7390529039426158,30,9.9321734571093323,1,37.31707317073171,12.417574198995283,1.2502373476076307,43.90243902439024,14.505773742121606,1.4604833277190246,null,null,null,null,null,null,null,null,null,null,10,0,30,0.06,0,26,45,16,83,0.1,0.1,200,0.8,16,16.399999999999999,null,22,null,10,null,30,0.08,0,26,45,16,83,0.1,0.1,200,0.8,16,16.399999999999999,0,18,null,10,null,30,0.06,0,26,45,16,83,0.1,0.1,200,0.8,16,16.399999999999999,0,22,null,10,null,30,0.05,0,26,45,16,83,0.1,0.1,200,0.8,16,16.5,0,26,null,10,null,30,0.04,0,26,45,16,83,0.1,0.1,200,0.8,16,16.5,0,29]
[null,40,13.116487202316168,0.99999999999999989,28.780487804878049,9.6675011767554189,0.73704956423456791,40,13.116487202316168,0.99999999999999989,49.756097560975611,16.393101890406701,1.2498088579320179,58.536585365853654,19.188445355825714,1.4629256339637438,null,null,null,null,null,null,null,null,null,null,13.000000000000002,0,40,0.08,0,26,45,16,83,0.13,0.13,200,0.8,16,16.600000000000001,null,22,null,13.000000000000002,null,40,0.11,0,26,45,16,83,0.13,0.13,200,0.8,16,16.600000000000001,0,18,null,13.000000000000002,null,40,0.08,0,26,45,16,83,0.13,0.13,200,0.8,16,16.600000000000001,0,22,null,13.000000000000002,null,40,0.06,0,26,45,16,83,0.13,0.13,200,0.8,16,16.600000000000001,0,26,null,13.000000000000002,null,40,0.05,0,26,45,16,83,0.13,0.13,200,0.8,16,16.600000000000001,0,29]
[null,50,16.234932224515045,1,35.975609756097562,11.937193586664391,0.73527831355150408,50,16.234932224515045,1,62.195121951219512,20.280622613351209,1.2491966293968937,73.170731707317074,23.775542314782385,1.4644682211164934,null,null,null,null,null,null,null,null,null,null,16,0,50,0.1,0,26,45,16,83,0.16,0.16,200,0.8,16,16.7,null,22,null,16,null,50,0.13,0,26,45,16,82,0.16,0.16,200,0.8,16,16.7,0,18,null,16,null,50,0.1,0,26,45,16,83,0.16,0.16,200,0.8,16,16.7,0,22,null,16,null,50,0.08,0,26,45,16,83,0.16,0.16,200,0.8,16,16.7,0,26,null,16,null,50,7.0000000000000007E-2,0,26,45,16,83,0.16,0.16,200,0.8,16,16.7,0,29]
[null,60,19.286334501562777,0.99999999999999989,43.170731707317074,14.150908716026477,0.73372722612893726,60,19.286334501562777,0.99999999999999989,74.634146341463421,24.077379014357156,1.2484165413809534,87.804878048780481,28.25817914567347,1.4651917990628909,null,null,null,null,null,null,null,null,null,null,19,0,60,0.12,0,26,45,16,83,0.19,0.19,200,0.8,16,16.8,null,22,null,19,null,60,0.16,0,26,45,16,82,0.19,0.19,200,0.8,16,16.8,0,18,null,19,null,60,0.12,0,26,45,16,83,0.19,0.19,200,0.8,16,16.8,0,22,null,19,null,60,0.09,0,26,45,16,83,0.19,0.19,200,0.8,16,16.8,0,26,null,19,null,60,0.08,0,26,45,16,83,0.19,0.19,200,0.8,16,16.8,0,29]
[null,70,22.269781594191084,1,50.365853658536587,16.310052403487525,0.73238492863090709,70,22.269781594191084,1,87.073170731707322,27.781190865468549,1.2474837594597279,102.4390243902439,32.629081056426116,1.4651729258511086,null,null,null,null,null,null,null,null,null,null,22,0,70,0.14000000000000001,0,26,45,16,82,0.22,0.22,200,0.8,16,17,null,22,null,22,null,70,0.19,0,26,45,16,81,0.22,0.22,200,0.8,16,16.899999999999999,0,18,null,22,null,70,0.14000000000000001,0,26,45,16,82,0.22,0.22,200,0.8,16,17,0,22,null,22,null,70,0.11,0,26,45,16,83,0.22,0.22,200,0.8,16,17,0,26,null,23,null,70,0.09,0,26,45,16,83,0.23,0.23,200,0.8,16,17,0,29]
[null,80,25.184608032824134,1,57.560975609756099,18.416006555154024,0.73124054704967756,80,25.184608032824134,1,99.512195121951223,31.390417378077085,1.2464127826474276,117.07317073170731,36.882461965225112,1.4644842563026863,null,null,null,null,null,null,null,null,null,null,25,0,80,0.15,0,26,45,16,82,0.25,0.25,200,0.8,16,17.100000000000001,null,22,null,25,null,80,0.22,0,26,45,16,80,0.25,0.25,200,0.8,16,17.100000000000001,0,18,null,25,null,80,0.15,0,26,45,16,82,0.25,0.25,200,0.8,16,17.100000000000001,0,22,null,26.000000000000004,null,80,0.12,0,26,45,16,82,0.26,0.26,200,0.8,16,17.100000000000001,0,26,null,26.000000000000004,null,80,0.11,0,26,45,16,83,0.26,0.26,200,0.8,16,17.100000000000001,0,29]
[null,90,28.030381035652216,1,64.756097560975604,20.470129227840324,0.73028365906992476,90,28.030381035652216,1,111.95121951219512,34.903920547434957,1.2452174839521517,131.70731707317074,41.01390655398508,1.4631947564972074,null,null,null,null,null,null,null,null,null,null,28.000000000000004,0,90,0.17,0,26,45,16,81,0.28000000000000003,0.28000000000000003,200,0.8,16,17.2,null,22,null,27.000000000000004,null,90,0.24,1,26,45,16,80,0.27,0.27,200,0.8,16,17.2,0,18,null,28.000000000000004,null,90,0.17,0,26,45,16,81,0.28000000000000003,0.28000000000000003,200,0.8,16,17.2,0,22,null,28.999999999999996,null,90,0.14000000000000001,0,26,45,16,82,0.28999999999999998,0.28999999999999998,200,0.8,16,17.2,0,26,null,28.999999999999996,null,90,0.12,0,26,45,16,82,0.28999999999999998,0.28999999999999998,200,0.8,16,17.2,0,29]
[null,100,30.80688655796153,1,71.951219512195124,22.473754716387212,0.72950425139859654,100,30.80688655796153,1,124.39024390243902,38.321029527848452,1.243911144858779,146.34146341463415,45.020256346282416,1.4613698875924765,null,null,null,null,null,null,null,null,null,null,31,0,100,0.19,0,26,45,16,81,0.31,0.31,200,0.8,16,17.3,null,22,null,30,null,100,0.27,1,26,45,16,79,0.3,0.3,200,0.8,16,17.3,0,18,null,31,null,100,0.19,0,26,45,16,81,0.31,0.31,200,0.8,16,17.3,0,22,null,32,null,100,0.16,0,26,45,16,82,0.32,0.32,200,0.8,16,17.399999999999999,0,26,null,32,null,100,0.13,0,26,45,16,82,0.32,0.32,200,0.8,16,17.399999999999999,0,29]
[null,110,33.514115672720102,1,79.146341463414629,24.428193645051678,0.7288926816271567,110,33.514115672720102,1,136.82926829268294,41.641506038552286,1.2425064842885809,160.97560975609755,48.899499809747105,1.4590717620978564,null,null,null,null,null,null,null,null,null,null,34,0,110,0.21,0,26,45,16,80,0.34,0.34,200,0.8,16,17.5,null,22,null,32,null,110,0.3,1,26,45,16,78,0.32,0.32,200,0.8,16,17.399999999999999,0,18,null,34,null,110,0.21,0,26,45,16,80,0.34,0.34,200,0.8,16,17.5,0,22,null,34,null,110,0.17,0,26,45,16,81,0.34,0.34,200,0.8,16,17.5,0,26,null,34.999999999999993,null,110,0.15,0,26,45,16,82,0.35,0.35,200,0.8,16,17.5,0,29]
[null,120,36.152251282419854,1,86.341463414634148,26.334733062968112,0.72843964424904817,120,36.152251282419854,1,149.26829268292684,44.865510800264794,1.241015682530455,175.60975609756096,52.650666482914282,1.4563592754323793,null,null,null,null,null,null,null,null,null,null,36,0,120,0.23,0,26,45,16,80,0.36,0.36,200,0.8,16,17.600000000000001,null,22,null,34.999999999999993,null,120,0.32,1,26,45,17,78,0.35,0.35,200,0.8,16,17.5,0,18,null,36,null,120,0.23,0,26,45,16,80,0.36,0.36,200,0.8,16,17.600000000000001,0,22,null,37,null,120,0.19,0,26,45,16,81,0.37,0.37,200,0.8,16,17.600000000000001,0,26,null,38,null,120,0.16,0,26,45,16,81,0.38,0.38,200,0.8,16,17.600000000000001,0,29]
[null,130,38.721655162174748,1,93.536585365853654,28.194636543680687,0.7281361405031731,130,38.721655162174748,1,161.70731707317074,47.993571002423806,1.2394504005940927,190.2439024390244,56.273725126535609,1.4532882153629272,null,null,null,null,null,null,null,null,null,null,39,0,130,0.25,1,26,45,16,79,0.39,0.39,200,0.8,16,17.7,null,22,null,37,null,130,0.35,1,26,45,17,77,0.37,0.37,200,0.8,16,17.600000000000001,0,18,null,39,null,130,0.25,1,26,45,16,79,0.39,0.39,200,0.8,16,17.7,0,22,null,40,null,130,0.2,0,26,45,16,80,0.4,0.4,200,0.8,16,17.7,0,26,null,40.999999999999993,null,130,0.17,0,26,45,16,81,0.41,0.41,200,0.8,16,17.7,0,29]
[null,140,41.222855334075142,1,100.73170731707317,30.009144288747134,0.72797345175508343,140,41.222855334075142,1,174.14634146341464,51.026548801103388,1.2378217953991275,204.8780487804878,59.769485899350407,1.4499113517239666,null,null,null,null,null,null,null,null,null,null,40.999999999999993,0,140,0.27,1,26,45,16,79,0.41,0.41,200,0.8,16,17.8,null,22,null,39,null,140,0.38,1,26,45,17,76,0.39,0.39,200,0.8,16,17.7,0,18,null,40.999999999999993,null,140,0.27,1,26,45,16,79,0.41,0.41,200,0.8,16,17.8,0,22,null,43,null,140,0.22,0,26,45,16,80,0.43,0.43,200,0.8,16,17.8,0,26,null,43,null,140,0.19,0,26,45,16,81,0.43,0.43,200,0.8,16,17.899999999999999,0,29]
[null,150,43.656533772798177,1,107.92682926829268,31.779473235413693,0.72794311616226093,150,43.656533772798177,1,186.58536585365854,53.965610847611288,1.2361405311851983,219.51219512195121,63.139506558316697,1.4462785086629599,null,null,null,null,null,null,null,null,null,null,44,0,150,0.28999999999999998,1,26,45,17,78,0.44,0.44,200,0.8,16,17.899999999999999,null,22,null,40.999999999999993,null,150,0.4,1,26,45,17,76,0.41,0.41,200,0.8,16,17.8,0,18,null,44,null,150,0.28999999999999998,1,26,45,17,78,0.44,0.44,200,0.8,16,17.899999999999999,0,22,null,45,null,150,0.23,0,26,45,16,79,0.45,0.45,200,0.8,16,17.899999999999999,0,26,null,46,null,150,0.2,0,26,45,16,80,0.46,0.46,200,0.8,16,18,0,29]
[null,160,46.023514442474379,1,115.1219512195122,33.506817168361536,0.72803690839912516,160,46.023514442474379,1,199.02439024390245,56.812198847767206,1.2344167875049568,234.14634146341461,66.386002683301982,1.442436621529176,null,null,null,null,null,null,null,null,null,null,46,0,160,0.31,1,26,45,17,77,0.46,0.46,200,0.8,16,18,null,22,null,44,null,160,0.43,2,26,45,17,75,0.44,0.44,200,0.8,16,17.899999999999999,0,18,null,46,null,160,0.31,1,26,45,17,77,0.46,0.46,200,0.8,16,18,0,22,null,48,null,160,0.25,1,26,45,16,79,0.48,0.48,200,0.8,16,18.100000000000001,0,26,null,49,null,160,0.21,0,26,45,16,80,0.49,0.49,200,0.8,16,18.100000000000001,0,29]
[null,170,48.324751664810329,1,122.3170731707317,35.19234683552429,0.72824682224184212,170,48.324751664810329,1,211.46341463414635,59.568001151861814,1.2326602641444866,248.78048780487805,69.511761926233746,1.4384297804235096,null,null,null,null,null,null,null,null,null,null,48,0,170,0.33,1,26,45,17,77,0.48,0.48,200,0.8,16,18.100000000000001,null,22,null,46,null,170,0.46,2,26,45,17,74,0.46,0.46,200,0.8,16,18,0,18,null,48,null,170,0.33,1,26,45,17,77,0.48,0.48,200,0.8,16,18.100000000000001,0,22,null,50,null,170,0.26,1,26,45,16,78,0.5,0.5,200,0.8,16,18.2,0,26,null,51.000000000000007,null,170,0.22,0,26,45,16,79,0.51,0.51,200,0.8,16,18.2,0,29]
[null,180,50.561318818467498,1,129.51219512195121,36.83721006797704,0.72856505583320086,180,50.561318818467498,1,223.90243902439025,62.234925375296584,1.2308801833026022,263.41463414634148,72.520062284709908,1.4342992623487896,null,null,null,null,null,null,null,null,null,null,51.000000000000007,0,180,0.35,1,26,45,17,76,0.51,0.51,200,0.8,16,18.2,null,22,null,47,null,180,0.48,2,26,45,17,74,0.47,0.47,200,0.8,16,18,0,18,null,51.000000000000007,null,180,0.35,1,26,45,17,76,0.51,0.51,200,0.8,16,18.2,0,22,null,53.000000000000007,null,180,0.28000000000000003,1,26,45,17,78,0.53,0.53,200,0.8,16,18.3,0,26,null,54.000000000000007,null,180,0.24,1,26,45,16,79,0.54,0.54,200,0.8,16,18.3,0,29]
[null,190,52.734397369697191,1,136.70731707317071,38.442531903896516,0.72898399946420511,190,52.734397369697191,1,236.34146341463415,64.815072049904387,1.2290852893513697,278.04878048780489,75.414594400068992,1.4300835538400321,null,null,null,null,null,null,null,null,null,null,53.000000000000007,0,190,0.37,1,26,45,17,76,0.53,0.53,200,0.8,16,18.3,null,22,null,49,null,190,0.51,2,26,45,18,73,0.49,0.49,200,0.8,16,18.100000000000001,0,18,null,53.000000000000007,null,190,0.37,1,26,45,17,76,0.53,0.53,200,0.8,16,18.3,0,22,null,55.000000000000007,null,190,0.3,1,26,45,17,77,0.55000000000000004,0.55000000000000004,200,0.8,16,18.399999999999999,0,26,null,56.000000000000007,null,190,0.25,1,26,45,16,78,0.56000000000000005,0.56000000000000005,200,0.8,16,18.399999999999999,0,29]
[null,200,54.84526623423163,1,143.90243902439025,40.009414716592588,0.7294962257220432,200,54.84526623423163,1,248.78048780487805,67.310709305950795,1.2272838464942828,292.6829268292683,78.19938787992011,1.4258183659087067,null,null,null,null,null,null,null,null,null,null,55.000000000000007,0,200,0.39,1,26,45,17,75,0.55000000000000004,0.55000000000000004,200,0.8,16,18.399999999999999,null,22,null,51.000000000000007,null,200,0.54,2,26,45,18,73,0.51,0.51,200,0.8,16,18.2,0,18,null,55.000000000000007,null,200,0.39,1,26,45,17,75,0.55000000000000004,0.55000000000000004,200,0.8,16,18.399999999999999,0,22,null,56.999999999999993,null,200,0.31,1,26,45,17,77,0.56999999999999995,0.56999999999999995,200,0.8,16,18.5,0,26,null,59,null,200,0.26,1,26,45,17,78,0.59,0.59,200,0.8,16,18.5,0,29]
[null,210,56.895291470431133,0.99999999999999989,151.09756097560975,41.538938346611111,0.73009448186409553,210,56.895291470431133,0.99999999999999989,261.21951219512192,69.724248584816323,1.2254836346352578,307.3170731707317,80.878741645132692,1.4215366431010537,null,null,null,null,null,null,null,null,null,null,56.999999999999993,0,210,0.41,1,26,45,17,75,0.56999999999999995,0.56999999999999995,200,0.8,16,18.399999999999999,null,22,null,53.000000000000007,null,210,0.56000000000000005,2,26,45,18,72,0.53,0.53,200,0.8,16,18.3,0,18,null,56.999999999999993,null,210,0.41,1,26,45,17,75,0.56999999999999995,0.56999999999999995,200,0.8,16,18.399999999999999,0,22,null,59,null,210,0.33,1,26,45,17,76,0.59,0.59,200,0.8,16,18.600000000000001,0,26,null,61,null,210,0.28000000000000003,1,26,45,17,78,0.61,0.61,200,0.8,16,18.600000000000001,0,29]
[null,220,58.885916303687502,1,158.29268292682926,43.032160237908059,0.73077168428494566,220,58.885916303687502,1,273.65853658536588,72.058221382359264,1.2236919437703799,321.95121951219511,83.457158301286171,1.4172685684447777,null,null,null,null,null,null,null,null,null,null,59,0,220,0.43,1,26,45,17,74,0.59,0.59,200,0.8,16,18.5,null,22,null,55.000000000000007,null,220,0.59,3,26,45,18,71,0.55000000000000004,0.55000000000000004,200,0.8,16,18.3,0,18,null,59,null,220,0.43,1,26,45,17,74,0.59,0.59,200,0.8,16,18.5,0,22,null,61,null,220,0.34,1,26,45,17,76,0.61,0.61,200,0.8,16,18.600000000000001,0,26,null,63,null,220,0.28999999999999998,1,26,45,17,77,0.63,0.63,200,0.8,16,18.7,0,29]
[null,230,60.818651482083439,1,165.48780487804876,44.490115578094873,0.7315209149482903,230,60.818651482083439,1,286.09756097560978,74.315257022959472,1.2219155672146396,336.58536585365852,85.939282534579291,1.4130415660382758,null,null,null,null,null,null,null,null,null,null,61,0,230,0.45,2,26,45,17,74,0.61,0.61,200,0.8,16,18.600000000000001,null,22,null,56.000000000000007,null,230,0.62,3,26,45,18,71,0.56000000000000005,0.56000000000000005,200,0.8,16,18.399999999999999,0,18,null,61,null,230,0.45,2,26,45,17,74,0.61,0.61,200,0.8,16,18.600000000000001,0,22,null,64,null,230,0.36,1,26,45,17,75,0.64,0.64,200,0.8,16,18.7,0,26,null,65,null,230,0.3,1,26,45,17,77,0.65,0.65,200,0.8,16,18.8,0,29]
[null,240,62.69506596330816,1,172.6829268292683,45.913817442755281,0.73233541965847859,240,62.69506596330816,1,298.53658536585368,76.498061464242767,1.2201607939771961,351.21951219512192,88.329843532199305,1.4088803030192794,null,null,null,null,null,null,null,null,null,null,63,0,240,0.46,2,26,45,18,73,0.63,0.63,200,0.8,16,18.7,null,22,null,57.999999999999993,null,240,0.65,3,26,45,18,70,0.57999999999999996,0.57999999999999996,200,0.8,16,18.5,0,18,null,63,null,240,0.46,2,26,45,18,73,0.63,0.63,200,0.8,16,18.7,0,22,null,66,null,240,0.37,1,26,45,17,75,0.66,0.66,200,0.8,16,18.8,0,26,null,68,null,240,0.32,1,26,45,17,76,0.68,0.68,200,0.8,16,18.899999999999999,0,29]
[null,250,64.516777932829115,1,179.8780487804878,47.304256943833167,0.73320860804740495,250,64.516777932829115,1,310.97560975609758,78.60939713248618,1.2184334006005295,365.85365853658539,90.633601427151035,1.4048066926329326,null,null,null,null,null,null,null,null,null,null,64,0,250,0.48,2,26,45,18,73,0.64,0.64,200,0.8,16,18.8,null,22,null,59,null,250,0.67,3,26,45,18,70,0.59,0.59,200,0.8,16,18.600000000000001,0,18,null,64,null,250,0.48,2,26,45,18,73,0.64,0.64,200,0.8,16,18.8,0,22,null,68,null,250,0.39,1,26,45,17,75,0.68,0.68,200,0.8,16,18.899999999999999,0,26,null,69.999999999999986,null,250,0.33,1,26,45,17,76,0.7,0.7,200,0.8,16,19,0,29]
[null,260,66.285446153319782,1,187.07317073170731,48.662403382091995,0.73413405515193675,260,66.285446153319782,1,323.41463414634148,80.65206378870414,1.2167386427807099,380.48780487804879,92.855297767545494,1.4008399001006802,null,null,null,null,null,null,null,null,null,null,66,0,260,0.5,2,26,45,18,72,0.66,0.66,200,0.8,16,18.8,null,22,null,61,null,260,0.7,4,26,45,18,70,0.61,0.61,200,0.8,16,18.600000000000001,0,18,null,66,null,260,0.5,2,26,45,18,72,0.66,0.66,200,0.8,16,18.8,0,22,null,68.999999999999986,null,260,0.4,1,26,45,17,74,0.69,0.69,200,0.8,16,19,0,26,null,72,null,260,0.34,1,26,45,17,75,0.72,0.72,200,0.8,16,19.100000000000001,0,29]
[null,270,68.002761645343796,1,194.26829268292681,49.989204403645402,0.73510550445517386,270,68.002761645343796,1,335.85365853658539,82.628880425415048,1.2150812470874515,395.1219512195122,94.999610010348661,1.3969963529687528,null,"Beispiel: BG1200 - kühlen",null,null,null,null,null,null,null,null,68,0,270,0.52,2,26,45,18,72,0.68,0.68,200,0.8,16,18.899999999999999,null,22,null,62,null,270,0.73,4,26,45,18,69,0.62,0.62,200,0.8,16,18.7,0,18,null,68,null,270,0.52,2,26,45,18,72,0.68,0.68,200,0.8,16,18.899999999999999,0,22,null,71,null,270,0.42,1,26,45,17,74,0.71,0.71,200,0.8,16,19.100000000000001,0,26,null,74,null,270,0.36,1,26,45,17,75,0.74,0.74,200,0.8,16,19.2,0,29]
[null,280,69.67043969929486,1,201.46341463414635,51.285586160559035,0.73611687226194011,280,69.67043969929486,1,348.29268292682929,84.542668194089117,1.2134654031033019,409.7560975609756,97.071110039589783,1.3932897575867065,null,null,null,null,null,null,null,null,null,null,69.999999999999986,0,280,0.54,2,26,45,18,71,0.7,0.7,200,0.8,16,19,null,22,null,64,null,280,0.75,4,26,45,19,69,0.64,0.64,200,0.8,16,18.7,0,18,null,69.999999999999986,null,280,0.54,2,26,45,18,71,0.7,0.7,200,0.8,16,19,0,22,null,73,null,280,0.44,2,26,45,18,73,0.73,0.73,200,0.8,16,19.100000000000001,0,26,null,76,null,280,0.37,1,26,45,17,75,0.76,0.76,200,0.8,16,19.3,0,29]
[null,290,71.290212218593069,1,208.65853658536585,52.552453475523798,0.73716225327517948,290,71.290212218593069,1,360.73170731707319,86.396234363276506,1.2118947563006925,424.39024390243901,99.074226709029602,1.3897311233307037,null,null,null,null,null,null,null,null,null,null,{"$f":"IF($AA$13=$AS$13,AS46,IF($AA$13=$BK$13,BK46,IF($AA$13=$CC$13,CC46,IF($AA$13=$CU$13,CU46,\"-\"))))","v":71},{"$f":"IF($AA$13=$AS$13,AT46,IF($AA$13=$BK$13,BL46,IF($AA$13=$CC$13,CD46,IF($AA$13=$CU$13,CV46,\"-\"))))","v":0},{"$f":"IF($AA$13=$AS$13,AU46,IF($AA$13=$BK$13,BM46,IF($AA$13=$CC$13,CE46,IF($AA$13=$CU$13,CW46,\"-\"))))","v":290},{"$f":"IF($AA$13=$AS$13,AV46,IF($AA$13=$BK$13,BN46,IF($AA$13=$CC$13,CF46,IF($AA$13=$CU$13,CX46,\"-\"))))","v":0.56000000000000005},{"$f":"IF($AA$13=$AS$13,AW46,IF($AA$13=$BK$13,BO46,IF($AA$13=$CC$13,CG46,IF($AA$13=$CU$13,CY46,\"-\"))))","v":2},{"$f":"IF($AA$13=$AS$13,AX46,IF($AA$13=$BK$13,BP46,IF($AA$13=$CC$13,CH46,IF($AA$13=$CU$13,CZ46,\"-\"))))","v":26},{"$f":"IF($AA$13=$AS$13,AY46,IF($AA$13=$BK$13,BQ46,IF($AA$13=$CC$13,CI46,IF($AA$13=$CU$13,DA46,\"-\"))))","v":45},{"$f":"IF($AA$13=$AS$13,AZ46,IF($AA$13=$BK$13,BR46,IF($AA$13=$CC$13,CJ46,IF($AA$13=$CU$13,DB46,\"-\"))))","v":18},{"$f":"IF($AA$13=$AS$13,BA46,IF($AA$13=$BK$13,BS46,IF($AA$13=$CC$13,CK46,IF($AA$13=$CU$13,DC46,\"-\"))))","v":71},{"$f":"IF($AA$13=$AS$13,BB46,IF($AA$13=$BK$13,BT46,IF($AA$13=$CC$13,CL46,IF($AA$13=$CU$13,DD46,\"-\"))))","v":0.71},{"$f":"IF($AA$13=$AS$13,BC46,IF($AA$13=$BK$13,BU46,IF($AA$13=$CC$13,CM46,IF($AA$13=$CU$13,DE46,\"-\"))))","v":0.71},{"$f":"IF($AA$13=$AS$13,BD46,IF($AA$13=$BK$13,BV46,IF($AA$13=$CC$13,CN46,IF($AA$13=$CU$13,DF46,\"-\"))))","v":200},{"$f":"IF($AA$13=$AS$13,BE46,IF($AA$13=$BK$13,BW46,IF($AA$13=$CC$13,CO46,IF($AA$13=$CU$13,DG46,\"-\"))))","v":0.8},{"$f":"IF($AA$13=$AS$13,BF46,IF($AA$13=$BK$13,BX46,IF($AA$13=$CC$13,CP46,IF($AA$13=$CU$13,DH46,\"-\"))))","v":16},{"$f":"IF($AA$13=$AS$13,BG46,IF($AA$13=$BK$13,BY46,IF($AA$13=$CC$13,CQ46,IF($AA$13=$CU$13,DI46,\"-\"))))","v":19.100000000000001},null,{"$f":"IF($AA$13=$AS$13,BI46,IF($AA$13=$BK$13,CA46,IF($AA$13=$CC$13,CS46,IF($AA$13=$CU$13,DK46,\"-\"))))","v":22},null,65,null,290,0.78,5,26,45,19,68,0.65,0.65,200,0.8,16,18.8,0,18,null,71,null,290,0.56000000000000005,2,26,45,18,71,0.71,0.71,200,0.8,16,19.100000000000001,0,22,null,75,null,290,0.45,2,26,45,18,73,0.75,0.75,200,0.8,16,19.2,0,26,null,78,null,290,0.38,1,26,45,17,74,0.78,0.78,200,0.8,16,19.3,0,29]
[null,300,72.863820394137349,1,215.85365853658536,53.7906900106004,0.73823592723568499,300,72.863820394137349,1,373.17073170731709,88.192357307416628,1.2103724019734849,439.02439024390242,101.01321240928829,1.3863287961416837,null,null,null,null,null,null,null,null,null,null,73,0,300,0.57999999999999996,3,26,45,18,71,0.73,0.73,200,0.8,16,19.100000000000001,null,22,null,66,null,300,0.81,5,26,45,19,68,0.66,0.66,200,0.8,16,18.899999999999999,0,18,null,73,null,300,0.57999999999999996,3,26,45,18,71,0.73,0.73,200,0.8,16,19.100000000000001,0,22,null,77,null,300,0.47,2,26,45,18,73,0.77,0.77,200,0.8,16,19.3,0,26,null,79,null,300,0.4,1,26,45,17,74,0.79,0.79,200,0.8,16,19.399999999999999,0,29]
[null,310,74.393007710013805,1,223.04878048780486,55.00115844003507,0.73933236648303358,310,74.393007710013805,1,385.60975609756099,89.933772526328056,1.2089008805356092,453.65853658536582,102.89211365943329,1.3830885028941142,null,null,null,null,null,null,null,null,null,null,74,0,310,0.6,3,26,45,18,70,0.74,0.74,200,0.8,16,19.2,null,22,null,68,null,310,0.83,5,26,45,19,67,0.68,0.68,200,0.8,16,18.899999999999999,0,18,null,74,null,310,0.6,3,26,45,18,70,0.74,0.74,200,0.8,16,19.2,0,22,null,78,null,310,0.48,2,26,45,18,72,0.78,0.78,200,0.8,16,19.399999999999999,0,26,null,81,null,310,0.41,1,26,45,17,73,0.81,0.81,200,0.8,16,19.5,0,29]
[null,320,75.879513280460429,1,230.2439024390244,56.184700627146739,0.74044624429101003,320,75.879513280460429,1,398.04878048780489,91.623159695379144,1.2074821744932414,468.29268292682923,104.71474572302688,1.3800134080458282,null,null,null,null,null,null,null,null,null,null,76,0,320,0.62,3,26,45,18,70,0.76,0.76,200,0.8,16,19.3,null,22,null,68.999999999999986,null,320,0.86,5,26,45,19,67,0.69,0.69,200,0.8,16,19,0,18,null,76,null,320,0.62,3,26,45,18,70,0.76,0.76,200,0.8,16,19.3,0,22,null,80,null,320,0.5,2,26,45,18,72,0.8,0.8,200,0.8,16,19.399999999999999,0,26,null,82.999999999999986,null,320,0.42,1,26,45,18,73,0.83,0.83,200,0.8,16,19.600000000000001,0,29]
[null,{"$f":"AC50","v":330},{"$f":"$J$4*B50^6+$K$4*B50^5+$L$4*B50^4+$M$4*B50^3+$N$4*B50^2+$O$4*B50","v":77.325065518087811},1,{"$f":"IF($B50*$F$3>$B$11,\"\",$B50*$F$3)","v":237.4390243902439},57.342137805285375,0.74157244382640652,{"$f":"IF($B50*$F$4>$B$11,\"\",$B50*$F$4)","v":330},77.325065518087811,1,{"$f":"IF($B50*$F$5>$B$11,\"\",$B50*$F$5)","v":410.48780487804879},{"$f":"IF(K50>$B$11,\"\",$J$5*K50^6+$K$5*K50^5+$L$5*K50^4+$M$5*K50^3+$N$5*K50^2+$O$5*K50)","v":93.263130746339584},{"$f":"IF(K50>$B$11,\"\",1/$C50*L50)","v":1.2061177073884735},{"$f":"IF($B50*$F$6>$B$11,\"\",$B50*$F$6)","v":482.92682926829269},106.4846712486337,{"$f":"IF(N50>$B$11,\"\",1/$C50*O50)","v":1.3771041839431084},null,null,null,null,null,null,null,null,null,null,77,0,330,0.64,3,26,45,18,70,0.77,0.77,200,0.8,16,19.3,null,22,null,{"$f":"BC50/(AX50-BF50)*1000","v":69.999999999999986},null,330,0.89,6,26,45,19,67,0.7,0.7,200,0.8,16,19,0,18,null,{"$f":"BU50/(BP50-BX50)*1000","v":77},null,330,0.64,3,26,45,18,70,0.77,0.77,200,0.8,16,19.3,0,22,null,{"$f":"CM50/(CH50-CP50)*1000","v":81.999999999999986},null,330,0.51,2,26,45,18,71,0.82,0.82,200,0.8,16,19.5,0,26,null,{"$f":"DE50/(CZ50-DH50)*1000","v":84.999999999999986},null,330,0.44,2,26,45,18,73,0.85,0.85,200,0.8,16,19.600000000000001,0,29]
[null,340,78.731376133356065,1,244.63414634146341,58.474270762861678,0.74270606757612512,340,78.731376133356065,1,422.92682926829269,94.85621897891258,1.2048083450014144,497.5609756097561,108.20518293478767,1.3743590960674756,null,null,null,null,null,null,null,null,null,null,79,0,340,0.66,3,26,45,18,69,0.79,0.79,200,0.8,16,19.399999999999999,null,22,null,71,null,340,0.91,6,26,45,19,66,0.71,0.71,200,0.8,16,19.100000000000001,0,18,null,79,null,340,0.66,3,26,45,18,69,0.79,0.79,200,0.8,16,19.399999999999999,0,22,null,82.999999999999986,null,340,0.53,2,26,45,18,71,0.83,0.83,200,0.8,16,19.600000000000001,0,26,null,86,null,340,0.45,2,26,45,18,72,0.86,0.86,200,0.8,16,19.7,0,29]
[null,350,80.100134465307747,1,251.82926829268291,59.58188003244814,0.74384244708420189,350,80.100134465307747,1,435.36585365853659,96.404869202948035,1.2035543990840869,512.19512195121945,109.87929021941923,1.3717741044118865,null,null,null,null,null,null,null,null,null,null,80,0,350,0.68,3,26,45,19,69,0.8,0.8,200,0.8,16,19.399999999999999,null,22,null,72,null,350,0.94,6,26,45,19,66,0.72,0.72,200,0.8,16,19.100000000000001,0,18,null,80,null,350,0.68,3,26,45,19,69,0.8,0.8,200,0.8,16,19.399999999999999,0,22,null,84.999999999999986,null,350,0.54,2,26,45,18,71,0.85,0.85,200,0.8,16,19.600000000000001,0,26,null,88,null,350,0.46,2,26,45,18,72,0.88,0.88,200,0.8,16,19.8,0,29]
[null,360,81.433002143557061,1,259.02439024390242,60.665726083951299,0.7449771528379191,360,81.433002143557061,1,447.80487804878049,97.911428911336202,1.2023556338832941,526.82926829268297,111.50970999374219,1.3693429820647327,null,null,null,null,null,null,null,null,null,null,81,0,360,0.7,4,26,45,19,68,0.81,0.81,200,0.8,16,19.5,null,22,null,74,null,360,0.97,7,26,45,19,66,0.74,0.74,200,0.8,16,19.2,0,18,null,81,null,360,0.7,4,26,45,19,68,0.81,0.81,200,0.8,16,19.5,0,22,null,86,null,360,0.56000000000000005,2,26,45,18,70,0.86,0.86,200,0.8,16,19.7,0,26,null,90,null,360,0.48,2,26,45,18,72,0.9,0.9,200,0.8,16,19.899999999999999,0,29]
[null,370,82.7316080815351,1,266.21951219512192,61.726549521855333,0.74610600414078143,370,82.7316080815351,1,460.2439024390244,99.378140483582385,1.2012112756909246,541.46341463414637,113.09886134060004,1.3670574519612488,null,null,null,null,null,null,null,null,null,null,82.999999999999986,0,370,0.72,4,26,45,19,68,0.83,0.83,200,0.8,16,19.600000000000001,null,22,null,75,null,370,1,7,26,45,19,65,0.75,0.75,200,0.8,16,19.2,0,18,null,82.999999999999986,null,370,0.72,4,26,45,19,68,0.83,0.83,200,0.8,16,19.600000000000001,0,22,null,88,null,370,0.57999999999999996,3,26,45,18,70,0.88,0.88,200,0.8,16,19.8,0,26,null,91,null,370,0.49,2,26,45,18,71,0.91,0.91,200,0.8,16,19.899999999999999,0,29]
[null,380,83.997543800991224,1,273.41463414634143,62.76507128653688,0.74722507880993794,380,83.997543800991224,1,472.6829268292683,100.80713442006218,1.2001200256390425,556.09756097560978,114.64886429727264,1.3649073426349367,null,null,null,null,null,null,null,null,null,null,83.999999999999986,0,380,0.74,4,26,45,19,68,0.84,0.84,200,0.8,16,19.600000000000001,null,22,null,76,null,380,1.02,7,26,45,19,65,0.76,0.76,200,0.8,16,19.3,0,18,null,83.999999999999986,null,380,0.74,4,26,45,19,68,0.84,0.84,200,0.8,16,19.600000000000001,0,22,null,89,null,380,0.59,3,26,45,18,70,0.89,0.89,200,0.8,16,19.8,0,26,null,93,null,380,0.5,2,26,45,18,71,0.93,0.93,200,0.8,16,20,0,29]
[null,390,85.232359087750581,1,280.60975609756099,63.781992859651389,0.74833072253678834,390,85.232359087750581,1,485.1219512195122,102.20042360695784,1.1990800759338112,570.73170731707319,116.16154264274215,1.3628807636680402,null,null,null,null,null,null,null,null,null,null,84.999999999999986,0,390,0.75,4,26,45,19,67,0.85,0.85,200,0.8,16,19.7,null,22,null,77,null,390,1.05,8,26,45,19,65,0.77,0.77,200,0.8,16,19.3,0,18,null,84.999999999999986,null,390,0.75,4,26,45,19,67,0.85,0.85,200,0.8,16,19.7,0,22,null,90,null,390,0.61,3,26,45,18,69,0.9,0.9,200,0.8,16,19.899999999999999,0,26,null,94,null,390,0.52,2,26,45,18,71,0.94,0.94,200,0.8,16,20.100000000000001,0,29]
[null,400,86.437557978727796,0.99999999999999989,287.80487804878049,64.777996473590477,0.74941955775210911,400,86.437557978727796,0.99999999999999989,497.5609756097561,103.559898611875,1.1980891296970813,585.36585365853659,117.63843070941945,1.3609643014020614,null,null,null,null,null,null,null,null,null,null,86,0,400,0.77,4,26,45,19,67,0.86,0.86,200,0.8,16,19.7,null,22,null,78,null,400,1.08,8,26,45,20,64,0.78,0.78,200,0.8,16,19.399999999999999,0,18,null,86,null,400,0.77,4,26,45,19,67,0.86,0.86,200,0.8,16,19.7,0,22,null,92,null,400,0.62,3,26,45,18,69,0.92,0.92,200,0.8,16,20,0,26,null,96,null,400,0.53,2,26,45,18,70,0.96,0.96,200,0.8,16,20.100000000000001,0,29]
[null,410,87.614595080196608,1,295,65.753745325010712,0.75048849184116051,410,87.614595080196608,1,510,104.88732401014039,1.197144424557729,600,119.08078421932933,1.359143235328893,null,null,null,null,null,null,null,null,null,null,88,0,410,0.79,5,26,45,19,67,0.88,0.88,200,0.8,16,19.8,null,22,null,79,null,410,1.1000000000000001,9,26,45,20,64,0.79,0.79,200,0.8,16,19.399999999999999,0,18,null,88,null,410,0.79,5,26,45,19,67,0.88,0.88,200,0.8,16,19.8,0,22,null,93,null,410,0.64,3,26,45,19,69,0.93,0.93,200,0.8,16,20,0,26,null,97,null,410,0.54,2,26,45,18,70,0.97,0.97,200,0.8,16,20.2,0,29]
[null,420,88.764872217315983,0.99999999999999989,302.19512195121951,66.709883792433786,0.75153472455988302,420,88.764872217315983,0.99999999999999989,522.43902439024384,106.1843357417805,1.1962427601069241,614.63414634146341,120.4895951447569,1.357401775443013,null,null,null,null,null,null,null,null,null,null,89,0,420,0.81,5,26,45,19,67,0.89,0.89,200,0.8,16,19.8,null,22,null,80,null,420,1.1299999999999999,9,26,45,20,64,0.8,0.8,200,0.8,16,19.399999999999999,0,18,null,89,null,420,0.81,5,26,45,19,67,0.89,0.89,200,0.8,16,19.8,0,22,null,94,null,420,0.65,3,26,45,19,68,0.94,0.94,200,0.8,16,20.100000000000001,0,26,null,98,null,420,0.56000000000000005,2,26,45,18,70,0.98,0.98,200,0.8,16,20.2,0,29]
[null,430,89.889735414911968,1,309.39024390243901,67.647037657917821,0.75255575451049483,430,89.889735414911968,1,534.8780487804878,107.45243949918061,1.1953805293029613,629.26829268292681,121.86561059335203,1.3557233206978105,null,null,null,null,null,null,null,null,null,null,90,0,430,0.83,5,26,45,19,66,0.9,0.9,200,0.8,16,19.899999999999999,null,22,null,81,null,430,1.1599999999999999,9,26,45,20,64,0.81,0.81,200,0.8,16,19.5,0,18,null,90,null,430,0.83,5,26,45,19,66,0.9,0.9,200,0.8,16,19.899999999999999,0,22,null,96,null,430,0.67,3,26,45,19,68,0.96,0.96,200,0.8,16,20.100000000000001,0,26,null,100,null,430,0.56999999999999995,3,26,45,18,69,1,1,200,0.8,16,20.3,0,29]
[null,440,90.990472209515929,1,316.58536585365852,68.565814332800116,0.75354938454346643,440,90.990472209515929,1,547.31707317073176,108.69301014542505,1.1945537538825715,643.90243902439022,123.20935571769553,1.354090738577463,null,null,null,null,null,null,null,null,null,null,91,0,440,0.85,5,26,45,19,66,0.91,0.91,200,0.8,16,19.899999999999999,null,22,null,81.999999999999986,null,440,1.18,10,26,45,20,63,0.82,0.82,200,0.8,16,19.5,0,18,null,91,null,440,0.85,5,26,45,19,66,0.91,0.91,200,0.8,16,19.899999999999999,0,22,null,97,null,440,0.68,4,26,45,19,68,0.97,0.97,200,0.8,16,20.2,0,26,null,101,null,440,0.57999999999999996,3,26,45,18,69,1.01,1.01,200,0.8,16,20.399999999999999,0,29]
[null,450,92.068309292658824,1,323.78048780487802,69.466803087511011,0.7545137259629251,450,92.068309292658824,1,559.7560975609756,109.90729216331773,1.193758123807334,658.53658536585363,124.52116064932343,1.3524866656724006,null,null,null,null,null,null,null,null,null,null,92,0,450,0.87,6,26,45,19,66,0.92,0.92,200,0.8,16,20,null,22,null,82.999999999999986,null,450,1.21,10,26,45,20,63,0.83,0.83,200,0.8,16,19.600000000000001,0,18,null,92,null,450,0.87,6,26,45,19,66,0.92,0.92,200,0.8,16,20,0,22,null,98,null,450,0.7,4,26,45,19,67,0.98,0.98,200,0.8,16,20.2,0,26,null,102.00000000000001,null,450,0.6,3,26,45,19,69,1.02,1.02,200,0.8,16,20.399999999999999,0,29]
[null,460,93.124410485421635,1,330.97560975609753,70.350575285459314,0.75544720142386834,460,93.124410485421635,1,572.19512195121956,111.09640113508409,1.1929890407464745,673.17073170731703,125.80119145721224,1.3508938290342902,null,null,null,null,null,null,null,null,null,null,93,0,460,0.89,6,26,45,19,65,0.93,0.93,200,0.8,16,20,null,22,null,83.999999999999986,null,460,1.24,11,26,45,20,63,0.84,0.84,200,0.8,16,19.600000000000001,0,18,null,93,null,460,0.89,6,26,45,19,65,0.93,0.93,200,0.8,16,20,0,22,null,99,null,460,0.72,4,26,45,19,67,0.99,0.99,200,0.8,16,20.3,0,26,null,104.00000000000001,null,460,0.61,3,26,45,19,68,1.04,1.04,200,0.8,16,20.5,0,29]
[null,470,94.159875044241886,1,338.17073170731709,71.217684620988763,0.75634854642199212,470,94.159875044241886,1,584.63414634146341,112.26132625275315,1.19224166557152,687.80487804878044,127.04948513072321,1.3492953879880134,null,null,null,null,null,null,null,null,null,null,94,0,470,0.91,6,26,45,19,65,0.94,0.94,200,0.8,16,20.100000000000001,null,22,null,84.999999999999986,null,470,1.26,11,26,45,20,63,0.85,0.85,200,0.8,16,19.600000000000001,0,18,null,94,null,470,0.91,6,26,45,19,65,0.94,0.94,200,0.8,16,20.100000000000001,0,22,null,100,null,470,0.73,4,26,45,19,67,1,1,200,0.8,16,20.3,0,26,null,105.00000000000001,null,470,0.62,3,26,45,19,68,1.05,1.05,200,0.8,16,20.5,0,29]
[null,480,95.175736297976329,1,345.36585365853659,72.068667361405957,0.75721680929027202,480,95.175736297976329,1,597.07317073170736,113.40293385922079,1.1915109698146042,702.43902439024384,128.26598858700694,1.3476752959959419,null,null,null,null,null,null,null,null,null,null,95,0,480,0.93,6,26,45,19,65,0.95,0.95,200,0.8,16,20.100000000000001,null,22,null,86,null,480,1.29,12,26,45,20,62,0.86,0.86,200,0.8,16,19.7,0,18,null,95,null,480,0.93,6,26,45,19,65,0.95,0.95,200,0.8,16,20.100000000000001,0,22,null,102.00000000000001,null,480,0.75,4,26,45,19,66,1.02,1.02,200,0.8,16,20.399999999999999,0,26,null,106.00000000000001,null,480,0.63,3,26,45,19,68,1.06,1.06,200,0.8,16,20.6,0,29]
[null,490,96.172960616219768,1,352.5609756097561,72.904042593079495,0.75805134963042897,490,96.172960616219768,1,609.51219512195121,114.5219720199938,1.190791791021139,717.07317073170725,129.45060170286774,1.3460186821059101,null,null,null,null,null,null,null,null,null,null,96,0,490,0.95,6,26,45,20,65,0.96,0.96,200,0.8,16,20.100000000000001,null,22,null,86,null,490,1.32,12,26,45,20,62,0.86,0.86,200,0.8,16,19.7,0,18,null,96,null,490,0.95,6,26,45,20,65,0.96,0.96,200,0.8,16,20.100000000000001,0,22,null,103.00000000000001,null,490,0.76,4,26,45,19,66,1.03,1.03,200,0.8,16,20.399999999999999,0,26,null,107.00000000000001,null,490,0.65,3,26,45,19,68,1.07,1.07,200,0.8,16,20.6,0,29]
[null,500,97.15244670887995,1,359.7560975609756,73.724312471610489,0.75885183512184184,500,97.15244670887995,1,621.95121951219517,115.61907612561434,1.1900788919096414,731.70731707317077,130.60322437108749,1.3443122514705548,null,null,null,null,null,null,null,null,null,null,97,0,500,0.97,7,26,45,20,64,0.97,0.97,200,0.8,16,20.2,null,22,null,87,null,500,1.35,12,26,45,20,62,0.87,0.87,200,0.8,16,19.8,0,18,null,97,null,500,0.97,7,26,45,20,64,0.97,0.97,200,0.8,16,20.2,0,22,null,104.00000000000001,null,500,0.78,5,26,45,19,66,1.04,1.04,200,0.8,16,20.5,0,26,null,109.00000000000001,null,500,0.66,3,26,45,19,67,1.0900000000000001,1.0900000000000001,200,0.8,16,20.7,0,29]
[null,510,98.115025257008597,1,366.95121951219511,74.529962476074303,0.75961823666503558,510,98.115025257008597,1,634.39024390243901,116.69477552476562,1.1893670232371452,746.34146341463418,131.72380758120926,1.3425447044034666,null,null,null,null,null,null,null,null,null,null,98,0,510,0.99,7,26,45,20,64,0.98,0.98,200,0.8,16,20.2,null,22,null,88,null,510,1.37,13,26,45,20,62,0.88,0.88,200,0.8,16,19.8,0,18,null,98,null,510,0.99,7,26,45,20,64,0.98,0.98,200,0.8,16,20.2,0,22,null,105.00000000000001,null,510,0.79,5,26,45,19,66,1.05,1.05,200,0.8,16,20.5,0,26,null,110.00000000000001,null,510,0.67,3,26,45,19,67,1.1000000000000001,1.1000000000000001,200,0.8,16,20.7,0,29]
[null,520,99.061458874888714,1,374.14634146341461,75.321461667333608,0.76035082183134495,520,99.061458874888714,1,646.82926829268297,117.74950118805799,1.1886509902581956,760.97560975609758,132.81240852478092,1.3407071734378404,null,null,null,null,null,null,null,null,null,null,99,0,520,1.01,7,26,45,20,64,0.99,0.99,200,0.8,16,20.3,null,22,null,89,null,520,1.4,13,26,45,20,61,0.89,0.89,200,0.8,16,19.8,0,18,null,99,null,520,1.01,7,26,45,20,64,0.99,0.99,200,0.8,16,20.3,0,22,null,106.00000000000001,null,520,0.81,5,26,45,19,65,1.06,1.06,200,0.8,16,20.6,0,26,null,111.00000000000001,null,520,0.69,4,26,45,19,67,1.1100000000000001,1.1100000000000001,200,0.8,16,20.8,0,29]
[null,530,99.992442403377808,0.99999999999999989,381.34146341463412,76.099262950422826,0.76105014660440118,530,99.992442403377808,0.99999999999999989,659.26829268292681,118.78359440249615,1.1879257226592512,775.60975609756099,133.86924972505926,1.3387936778763698,null,null,null,null,null,null,null,null,null,null,100,0,530,1.03,8,26,45,20,64,1,1,200,0.8,16,20.3,null,22,null,90,null,530,1.43,14,26,45,20,61,0.9,0.9,200,0.8,16,19.899999999999999,0,18,null,100,null,530,1.03,8,26,45,20,64,1,1,200,0.8,16,20.3,0,22,null,107.00000000000001,null,530,0.82,5,26,45,19,65,1.07,1.07,200,0.8,16,20.6,0,26,null,112.00000000000001,null,530,0.7,4,26,45,19,67,1.1200000000000001,1.1200000000000001,200,0.8,16,20.8,0,29]
[null,540,100.90860353450729,1,388.53658536585363,76.863803341003688,0.76171704541247454,540,100.90860353450729,1,671.70731707317077,119.79731649662698,1.1871863478485298,790.2439024390244,134.89478219117254,1.3368015953668722,null,null,null,null,null,null,null,null,null,null,101,0,540,1.05,8,26,45,20,63,1.01,1.01,200,0.8,16,20.399999999999999,null,22,null,91,null,540,1.45,14,26,45,20,61,0.91,0.91,200,0.8,16,19.899999999999999,0,18,null,101,null,540,1.05,8,26,45,20,63,1.01,1.01,200,0.8,16,20.399999999999999,0,22,null,108.00000000000001,null,540,0.84,5,26,45,19,65,1.08,1.08,200,0.8,16,20.7,0,26,null,112.99999999999999,null,540,0.71,4,26,45,19,66,1.1299999999999999,1.1299999999999999,200,0.8,16,20.9,0,29]
[null,550,101.81050376733825,1,395.73170731707313,77.615504235892232,0.76235261946314037,550,101.81050376733825,1,684.14634146341461,120.79085959636782,1.1864282674841127,804.8780487804878,135.88975259674314,1.3347321501058895,null,null,null,null,null,null,null,null,null,null,102.00000000000001,0,550,1.06,8,26,45,20,63,1.02,1.02,200,0.8,16,20.399999999999999,null,22,null,91,null,550,1.48,15,26,45,20,61,0.91,0.91,200,0.8,16,19.899999999999999,0,18,null,102.00000000000001,null,550,1.06,8,26,45,20,63,1.02,1.02,200,0.8,16,20.399999999999999,0,22,null,109.00000000000001,null,550,0.86,5,26,45,19,65,1.0900000000000001,1.0900000000000001,200,0.8,16,20.7,0,26,null,113.99999999999999,null,550,0.73,4,26,45,19,66,1.1399999999999999,1.1399999999999999,200,0.8,16,20.9,0,29]
[null,560,102.69863969507277,1,402.92682926829269,78.354771687657177,0.76295822340299657,560,102.69863969507277,1,696.58536585365857,121.76435841151617,1.1856472371304265,819.51219512195121,136.85527448297159,1.3325909173608808,null,null,null,null,null,null,null,null,null,null,103.00000000000001,0,560,1.08,8,26,45,20,63,1.03,1.03,200,0.8,16,20.399999999999999,null,22,null,92,null,560,1.51,15,26,45,20,61,0.92,0.92,200,0.8,16,20,0,18,null,103.00000000000001,null,560,1.08,8,26,45,20,63,1.03,1.03,200,0.8,16,20.399999999999999,0,22,null,110.00000000000001,null,560,0.87,6,26,45,20,65,1.1000000000000001,1.1000000000000001,200,0.8,16,20.7,0,26,null,114.99999999999999,null,560,0.74,4,26,45,19,66,1.1499999999999999,1.1499999999999999,200,0.8,16,21,0,29]
[null,570,103.57344462342223,1,410.1219512195122,79.081996683289248,0.76353545033497461,570,103.57344462342223,1,709.02439024390242,122.71790305293997,1.184839448944893,834.14634146341461,137.79290348617849,1.3303883441086002,null,null,null,null,null,null,null,null,null,null,104.00000000000001,0,570,1.1000000000000001,9,26,45,20,63,1.04,1.04,200,0.8,16,20.5,null,22,null,93,null,570,1.53,16,26,45,21,60,0.93,0.93,200,0.8,16,20,0,18,null,104.00000000000001,null,570,1.1000000000000001,9,26,45,20,63,1.04,1.04,200,0.8,16,20.5,0,22,null,111.00000000000001,null,570,0.89,6,26,45,20,64,1.1100000000000001,1.1100000000000001,200,0.8,16,20.8,0,26,null,115.99999999999999,null,570,0.75,4,26,45,19,65,1.1599999999999999,1.1599999999999999,200,0.8,16,21,0,29]
[null,580,104.43529052023098,1,417.3170731707317,79.797555426942324,0.76408611523404646,580,104.43529052023098,1,721.46341463414637,123.65155288044784,1.1840016173124384,848.78048780487802,138.70471658980631,1.3281402857105733,null,null,null,null,null,null,null,null,null,null,105.00000000000001,0,580,1.1200000000000001,9,26,45,20,63,1.05,1.05,200,0.8,16,20.5,null,22,null,93,null,580,1.56,16,26,45,21,60,0.93,0.93,200,0.8,16,20,0,18,null,105.00000000000001,null,580,1.1200000000000001,9,26,45,20,63,1.05,1.05,200,0.8,16,20.5,0,22,null,112.00000000000001,null,580,0.9,6,26,45,20,64,1.1200000000000001,1.1200000000000001,200,0.8,16,20.8,0,26,null,117,null,580,0.77,4,26,45,19,65,1.17,1.17,200,0.8,16,21,0,29]
[null,590,105.28449029635635,1,424.51219512195121,80.501809626745342,0.76461223680855228,590,105.28449029635635,1,733.90243902439022,124.56535138134163,1.1831310673653188,863.41463414634143,139.59339540088251,1.3258685586827932,null,null,null,null,null,null,null,null,null,null,105.00000000000001,0,590,1.1399999999999999,9,26,45,20,62,1.05,1.05,200,0.8,16,20.5,null,22,null,94,null,590,1.59,17,26,45,21,60,0.94,0.94,200,0.8,16,20.100000000000001,0,18,null,105.00000000000001,null,590,1.1399999999999999,9,26,45,20,62,1.05,1.05,200,0.8,16,20.5,0,22,null,112.99999999999999,null,590,0.92,6,26,45,20,64,1.1299999999999999,1.1299999999999999,200,0.8,16,20.9,0,26,null,118,null,590,0.78,5,26,45,19,65,1.18,1.18,200,0.8,16,21.1,0,29]
[null,600,106.1213004178052,1,431.70731707317071,81.195106785685894,0.76511601785896366,600,106.1213004178052,1,746.34146341463418,125.45934207964828,1.182225826348793,878.04878048780483,140.46231345094219,1.3236015097622682,null,null,null,null,null,null,null,null,null,null,106.00000000000001,0,600,1.1599999999999999,9,26,45,20,62,1.06,1.06,200,0.8,16,20.6,null,22,null,95,null,600,1.61,17,26,45,21,60,0.95,0.95,200,0.8,16,20.100000000000001,0,18,null,106.00000000000001,null,600,1.1599999999999999,9,26,45,20,62,1.06,1.06,200,0.8,16,20.6,0,22,null,113.99999999999999,null,600,0.93,6,26,45,20,64,1.1399999999999999,1.1399999999999999,200,0.8,16,20.9,0,26,null,119,null,600,0.79,5,26,45,19,65,1.19,1.19,200,0.8,16,21.1,0,29]
[null,610,106.94592384912585,0.99999999999999989,438.90243902439022,81.877780496564981,0.76559982418847683,610,106.94592384912585,0.99999999999999989,758.78048780487802,126.33358547603342,1.181284717819248,892.68292682926824,141.31562752140752,1.3213746016236092,null,null,null,null,null,null,null,null,null,null,{"$f":"IF($AA$13=$AS$13,AS78,IF($AA$13=$BK$13,BK78,IF($AA$13=$CC$13,CC78,IF($AA$13=$CU$13,CU78,\"-\"))))","v":107.00000000000001},{"$f":"IF($AA$13=$AS$13,AT78,IF($AA$13=$BK$13,BL78,IF($AA$13=$CC$13,CD78,IF($AA$13=$CU$13,CV78,\"-\"))))","v":0},{"$f":"IF($AA$13=$AS$13,AU78,IF($AA$13=$BK$13,BM78,IF($AA$13=$CC$13,CE78,IF($AA$13=$CU$13,CW78,\"-\"))))","v":610},{"$f":"IF($AA$13=$AS$13,AV78,IF($AA$13=$BK$13,BN78,IF($AA$13=$CC$13,CF78,IF($AA$13=$CU$13,CX78,\"-\"))))","v":1.18},{"$f":"IF($AA$13=$AS$13,AW78,IF($AA$13=$BK$13,BO78,IF($AA$13=$CC$13,CG78,IF($AA$13=$CU$13,CY78,\"-\"))))","v":10},{"$f":"IF($AA$13=$AS$13,AX78,IF($AA$13=$BK$13,BP78,IF($AA$13=$CC$13,CH78,IF($AA$13=$CU$13,CZ78,\"-\"))))","v":26},{"$f":"IF($AA$13=$AS$13,AY78,IF($AA$13=$BK$13,BQ78,IF($AA$13=$CC$13,CI78,IF($AA$13=$CU$13,DA78,\"-\"))))","v":45},{"$f":"IF($AA$13=$AS$13,AZ78,IF($AA$13=$BK$13,BR78,IF($AA$13=$CC$13,CJ78,IF($AA$13=$CU$13,DB78,\"-\"))))","v":20},{"$f":"IF($AA$13=$AS$13,BA78,IF($AA$13=$BK$13,BS78,IF($AA$13=$CC$13,CK78,IF($AA$13=$CU$13,DC78,\"-\"))))","v":62},{"$f":"IF($AA$13=$AS$13,BB78,IF($AA$13=$BK$13,BT78,IF($AA$13=$CC$13,CL78,IF($AA$13=$CU$13,DD78,\"-\"))))","v":1.07},{"$f":"IF($AA$13=$AS$13,BC78,IF($AA$13=$BK$13,BU78,IF($AA$13=$CC$13,CM78,IF($AA$13=$CU$13,DE78,\"-\"))))","v":1.07},{"$f":"IF($AA$13=$AS$13,BD78,IF($AA$13=$BK$13,BV78,IF($AA$13=$CC$13,CN78,IF($AA$13=$CU$13,DF78,\"-\"))))","v":200},{"$f":"IF($AA$13=$AS$13,BE78,IF($AA$13=$BK$13,BW78,IF($AA$13=$CC$13,CO78,IF($AA$13=$CU$13,DG78,\"-\"))))","v":0.8},{"$f":"IF($AA$13=$AS$13,BF78,IF($AA$13=$BK$13,BX78,IF($AA$13=$CC$13,CP78,IF($AA$13=$CU$13,DH78,\"-\"))))","v":16},{"$f":"IF($AA$13=$AS$13,BG78,IF($AA$13=$BK$13,BY78,IF($AA$13=$CC$13,CQ78,IF($AA$13=$CU$13,DI78,\"-\"))))","v":20.6},null,{"$f":"IF($AA$13=$AS$13,BI78,IF($AA$13=$BK$13,CA78,IF($AA$13=$CC$13,CS78,IF($AA$13=$CU$13,DK78,\"-\"))))","v":22},null,96,null,610,1.64,18,26,45,21,60,0.96,0.96,200,0.8,16,20.100000000000001,0,18,null,107.00000000000001,null,610,1.18,10,26,45,20,62,1.07,1.07,200,0.8,16,20.6,0,22,null,114.99999999999999,null,610,0.95,7,26,45,20,63,1.1499999999999999,1.1499999999999999,200,0.8,16,20.9,0,26,null,120,null,610,0.81,5,26,45,19,65,1.2,1.2,200,0.8,16,21.2,0,29]
[null,620,107.75851332805694,1,446.09756097560972,82.550150741022918,0.76606616212038492,620,107.75851332805694,1,771.21951219512198,127.18817701839546,1.1803074586894813,907.31707317073165,142.1583729934321,1.3192310157495326,null,null,null,null,null,null,null,null,null,null,108.00000000000001,0,620,1.2,10,26,45,20,62,1.08,1.08,200,0.8,16,20.6,null,22,null,96,null,620,1.67,18,26,45,21,60,0.96,0.96,200,0.8,16,20.100000000000001,0,18,null,108.00000000000001,null,620,1.2,10,26,45,20,62,1.08,1.08,200,0.8,16,20.6,0,22,null,115.99999999999999,null,620,0.96,7,26,45,20,63,1.1599999999999999,1.1599999999999999,200,0.8,16,21,0,26,null,121,null,620,0.82,5,26,45,20,64,1.21,1.21,200,0.8,16,21.2,0,29]
[null,630,108.55917497143167,1,453.29268292682923,83.212524192636991,0.7665176546757575,630,108.55917497143167,1,783.65853658536582,128.02326610313986,1.1792947591654999,921.95121951219505,142.99656322220048,1.3172222731043353,null,null,null,null,null,null,null,null,null,null,109.00000000000001,0,630,1.22,10,26,45,20,62,1.0900000000000001,1.0900000000000001,200,0.8,16,20.7,null,22,null,97,null,630,1.69,19,26,45,21,59,0.97,0.97,200,0.8,16,20.2,0,18,null,109.00000000000001,null,630,1.22,10,26,45,20,62,1.0900000000000001,1.0900000000000001,200,0.8,16,20.7,0,22,null,115.99999999999999,null,630,0.98,7,26,45,20,63,1.1599999999999999,1.1599999999999999,200,0.8,16,21,0,26,null,122,null,630,0.83,5,26,45,20,64,1.22,1.22,200,0.8,16,21.3,0,29]
[null,640,109.34797221233886,1,460.48780487804879,83.865194524089731,0.76695701646149372,640,109.34797221233886,1,796.09756097560978,128.8390761071355,1.1782484256493351,936.58536585365846,143.83729293569036,1.3154088733934446,null,null,null,null,null,null,null,null,null,null,109.00000000000001,0,640,1.24,11,26,45,20,61,1.0900000000000001,1.0900000000000001,200,0.8,16,20.7,null,22,null,98,null,640,1.72,20,26,45,21,59,0.98,0.98,200,0.8,16,20.2,0,18,null,109.00000000000001,null,640,1.24,11,26,45,20,61,1.0900000000000001,1.0900000000000001,200,0.8,16,20.7,0,22,null,117,null,640,1,7,26,45,20,63,1.17,1.17,200,0.8,16,21,0,26,null,123,null,640,0.85,5,26,45,20,64,1.23,1.23,200,0.8,16,21.3,0,29]
[null,{"$f":"AC82","v":650},{"$f":"$J$4*B82^6+$K$4*B82^5+$L$4*B82^4+$M$4*B82^3+$N$4*B82^2+$O$4*B82","v":110.12493006853957},1,{"$f":"IF($B82*$F$3>$B$11,\"\",$B82*$F$3)","v":467.6829268292683},84.5084427184091,0.76738702731354946,{"$f":"IF($B82*$F$4>$B$11,\"\",$B82*$F$4)","v":650},110.12493006853957,1,{"$f":"IF($B82*$F$5>$B$11,\"\",$B82*$F$5)","v":808.53658536585363},{"$f":"IF(K82>$B$11,\"\",$J$5*K82^6+$K$5*K82^5+$L$5*K82^4+$M$5*K82^3+$N$5*K82^2+$O$5*K82)","v":129.63592545035053},{"$f":"IF(K82>$B$11,\"\",1/$C82*L82)","v":1.1771714667121032},{"$f":"IF($B82*$F$6>$B$11,\"\",$B82*$F$6)","v":951.21951219512198},144.68884565789367,{"$f":"IF(N82>$B$11,\"\",1/$C82*O82)","v":1.3138609538080268},null,null,null,null,null,null,null,null,null,null,110.00000000000001,0,650,1.26,11,26,45,20,61,1.1000000000000001,1.1000000000000001,200,0.8,16,20.7,null,22,null,{"$f":"BC82/(AX82-BF82)*1000","v":98},null,650,1.75,20,26,45,21,59,0.98,0.98,200,0.8,16,20.2,0,18,null,{"$f":"BU82/(BP82-BX82)*1000","v":110.00000000000001},null,650,1.26,11,26,45,20,61,1.1000000000000001,1.1000000000000001,200,0.8,16,20.7,0,22,null,{"$f":"CM82/(CH82-CP82)*1000","v":118},null,650,1.01,7,26,45,20,63,1.18,1.18,200,0.8,16,21.1,0,26,null,{"$f":"DE82/(CZ82-DH82)*1000","v":124},null,650,0.86,5,26,45,20,64,1.24,1.24,200,0.8,16,21.3,0,29]
[null,660,110.89003974214012,{"$f":"1/C83*C83","v":1},474.8780487804878,{"$f":"IF(E83>$B$11,\"\",$J$3*E83^6+$K$3*E83^5+$L$3*E83^4+$M$3*E83^3+$N$3*E83^2+$O$3*E83)","v":85.142537384279734},{"$f":"IF(E83>$B$11,\"\",1/$C83*F83)","v":0.76781050473304235},660,{"$f":"IF(H83>$B$11,\"\",$J$4*H83^6+$K$4*H83^5+$L$4*H83^4+$M$4*H83^3+$N$4*H83^2+$O$4*H83)","v":110.89003974214012},{"$f":"IF(H83>$B$11,\"\",1/$C83*I83)","v":1},820.97560975609758,130.41424968916959,1.1760682022698379,965.85365853658539,{"$f":"IF(N83>$B$11,\"\",$J$6*N83^6+$K$6*N83^5+$L$6*N83^4+$M$6*N83^3+$N$6*N83^2+$O$6*N83)","v":145.56080515649623},{"$f":"IF(N83>$B$11,\"\",1/$C83*O83)","v":1.3126589682443826},null,null,null,null,null,null,null,null,null,null,111.00000000000001,0,660,1.28,11,26,45,20,61,1.1100000000000001,1.1100000000000001,200,0.8,16,20.8,null,22,null,99,null,660,1.78,21,26,45,21,59,0.99,0.99,200,0.8,16,20.3,0,18,null,111.00000000000001,null,660,1.28,11,26,45,20,61,1.1100000000000001,1.1100000000000001,200,0.8,16,20.8,0,22,null,119,null,660,1.03,8,26,45,20,63,1.19,1.19,200,0.8,16,21.1,0,26,null,125,null,660,0.87,6,26,45,20,64,1.25,1.25,200,0.8,16,21.4,0,29]
[null,670,111.64326355052137,1,482.07317073170731,85.76773507542535,0.76823027514430653,670,111.64326355052137,1,833.41463414634143,131.17462464039184,1.174944376120213,980.48780487804879,146.46417091501948,{"$f":"IF(N84>$B$11,\"\",1/$C84*O84)","v":1.3118943880455518},null,null,null,null,null,null,null,null,null,null,112.00000000000001,0,670,1.3,12,26,45,20,61,1.1200000000000001,1.1200000000000001,200,0.8,16,20.8,null,22,null,100,null,670,1.8,21,26,45,21,59,1,1,200,0.8,16,20.3,0,18,null,112.00000000000001,null,670,1.3,12,26,45,20,61,1.1200000000000001,1.1200000000000001,200,0.8,16,20.8,0,22,null,120,null,670,1.04,8,26,45,20,62,1.2,1.2,200,0.8,16,21.2,0,26,null,126,null,670,0.89,6,26,45,20,63,1.26,1.26,200,0.8,16,21.4,0,29]
[null,680,112.38454018852377,1,489.26829268292681,86.384280614062774,0.76864914399395268,680,112.38454018852377,1,845.85365853658539,131.91779053590992,1.1738072720199713,995.1219512195122,147.41147762942191,{"$f":"IF(N85>$B$11,\"\",1/$C85*O85)","v":1.3116704253284379},null,null,null,null,null,null,null,null,null,null,112.00000000000001,0,680,1.32,12,26,45,20,61,1.1200000000000001,1.1200000000000001,200,0.8,16,20.8,null,22,null,100,null,680,1.83,22,26,45,21,59,1,1,200,0.8,16,20.3,0,18,null,112.00000000000001,null,680,1.32,12,26,45,20,61,1.1200000000000001,1.1200000000000001,200,0.8,16,20.8,0,22,null,120,null,680,1.06,8,26,45,20,62,1.2,1.2,200,0.8,16,21.2,0,26,null,126,null,680,0.9,6,26,45,20,63,1.26,1.26,200,0.8,16,21.4,0,29]
[null,690,113.11379032188876,1,496.46341463414632,86.992407418426893,0.76906986469883076,690,113.11379032188876,1,858.29268292682923,132.6446772080686,1.1726658334991751,"","","",null,null,null,null,null,null,null,null,null,null,112.99999999999999,0,690,1.34,12,26,45,21,61,1.1299999999999999,1.1299999999999999,200,0.8,16,20.9,null,22,null,101,null,690,1.86,23,26,45,21,58,1.01,1.01,200,0.8,16,20.3,0,18,null,112.99999999999999,null,690,1.34,12,26,45,21,61,1.1299999999999999,1.1299999999999999,200,0.8,16,20.9,0,22,null,121,null,690,1.07,8,26,45,20,62,1.21,1.21,200,0.8,16,21.2,0,26,null,127,null,690,0.91,6,26,45,20,63,1.27,1.27,200,0.8,16,21.5,0,29]
[null,700,113.83092251195632,1,503.65853658536582,87.592337834367271,0.76949510643882324,700,113.83092251195632,1,870.73170731707319,133.3564303057062,1.1715307876179164,"","","",null,null,null,null,null,null,null,null,null,null,113.99999999999999,0,700,1.36,13,26,45,21,60,1.1399999999999999,1.1399999999999999,200,0.8,16,20.9,null,22,null,101,null,700,1.88,23,26,45,21,58,1.01,1.01,200,0.8,16,20.399999999999999,0,18,null,113.99999999999999,null,700,1.36,13,26,45,21,60,1.1399999999999999,1.1399999999999999,200,0.8,16,20.9,0,22,null,122,null,700,1.0900000000000001,8,26,45,20,62,1.22,1.22,200,0.8,16,21.3,0,26,null,128,null,700,0.93,6,26,45,20,63,1.28,1.28,200,0.8,16,21.5,0,29]
[null,710,114.53583947161866,1,510.85365853658533,88.18428347101576,0.7699274207779071,710,114.53583947161866,1,883.17073170731703,134.05443854087457,1.1704147728719665,"","","",null,null,null,null,null,null,null,null,null,null,114.99999999999999,0,710,1.37,13,26,45,21,60,1.1499999999999999,1.1499999999999999,200,0.8,16,20.9,null,22,null,102.00000000000001,null,710,1.91,24,26,45,21,58,1.02,1.02,200,0.8,16,20.399999999999999,0,18,null,114.99999999999999,null,710,1.37,13,26,45,21,60,1.1499999999999999,1.1499999999999999,200,0.8,16,20.9,0,22,null,123,null,710,1.1000000000000001,9,26,45,20,62,1.23,1.23,200,0.8,16,21.3,0,26,null,129,null,710,0.94,6,26,45,20,63,1.29,1.29,200,0.8,16,21.5,0,29]
[null,720,115.22844465252982,1,518.04878048780483,88.768445540525505,0.77036920708429102,720,115.22844465252982,1,895.60975609756099,134.74036196624186,1.1693324714444426,"","","",null,null,null,null,null,null,null,null,null,null,114.99999999999999,0,720,1.39,13,26,45,21,60,1.1499999999999999,1.1499999999999999,200,0.8,16,21,null,22,null,103.00000000000001,null,720,1.94,24,26,45,21,58,1.03,1.03,200,0.8,16,20.399999999999999,0,18,null,114.99999999999999,null,720,1.39,13,26,45,21,60,1.1499999999999999,1.1499999999999999,200,0.8,16,21,0,22,null,123,null,720,1.1200000000000001,9,26,45,20,61,1.23,1.23,200,0.8,16,21.3,0,26,null,130,null,720,0.95,7,26,45,20,63,1.3,1.3,200,0.8,16,21.6,0,29]
[null,730,115.90864916357157,0.99999999999999989,525.2439024390244,89.34501520188158,0.77082267670807636,730,115.90864916357157,0.99999999999999989,908.04878048780483,135.41616128317409,1.1683007459786137,"","","",null,null,null,null,null,null,null,null,null,null,115.99999999999999,0,730,1.41,14,26,45,21,60,1.1599999999999999,1.1599999999999999,200,0.8,16,21,null,22,null,103.00000000000001,null,730,1.96,25,26,45,21,58,1.03,1.03,200,0.8,16,20.399999999999999,0,18,null,115.99999999999999,null,730,1.41,14,26,45,21,60,1.1599999999999999,1.1599999999999999,200,0.8,16,21,0,22,null,124,null,730,1.1399999999999999,9,26,45,20,61,1.24,1.24,200,0.8,16,21.3,0,26,null,130,null,730,0.97,7,26,45,20,62,1.3,1.3,200,0.8,16,21.6,0,29]
[null,740,116.57637902057576,0.99999999999999989,532.43902439024384,89.914173908782118,0.77128981586323109,740,116.57637902057576,0.99999999999999989,920.48780487804879,136.08412818049936,1.1673387810105207,"","","",null,null,null,null,null,null,null,null,null,null,115.99999999999999,0,740,1.43,14,26,45,21,60,1.1599999999999999,1.1599999999999999,200,0.8,16,21,null,22,null,104.00000000000001,null,740,1.99,26,26,45,21,58,1.04,1.04,200,0.8,16,20.5,0,18,null,115.99999999999999,null,740,1.43,14,26,45,21,60,1.1599999999999999,1.1599999999999999,200,0.8,16,21,0,22,null,125,null,740,1.1499999999999999,9,26,45,20,61,1.25,1.25,200,0.8,16,21.4,0,26,null,131,null,740,0.98,7,26,45,20,62,1.31,1.31,200,0.8,16,21.6,0,29]
[null,750,117.23158272730177,1,539.63414634146341,90.476093761591699,0.77177234715027832,750,117.23158272730177,1,932.92682926829264,136.74691670395177,{"$f":"IF(K92>$B$11,\"\",1/$C92*L92)","v":1.1664682291464545},"","","",null,null,null,null,null,null,null,null,null,null,117,0,750,1.45,14,26,45,21,60,1.17,1.17,200,0.8,16,21,null,22,null,104.00000000000001,null,750,2.02,26,26,45,21,58,1.04,1.04,200,0.8,16,20.5,0,18,null,117,null,750,1.45,14,26,45,21,60,1.17,1.17,200,0.8,16,21,0,22,null,126,null,750,1.17,10,26,45,20,61,1.26,1.26,200,0.8,16,21.4,0,26,null,132,null,750,0.99,7,26,45,20,62,1.32,1.32,200,0.8,16,21.7,0,29]
[null,760,117.87423918767155,1,546.82926829268285,91.030937863365367,0.77227168964740422,760,117.87423918767155,1,945.36585365853659,137.40757565629562,1.1657133619969702,"","","",null,null,null,null,null,null,null,null,null,null,118,0,760,1.47,15,26,45,21,60,1.18,1.18,200,0.8,16,21.1,null,22,null,105.00000000000001,null,760,2.04,27,26,45,21,58,1.05,1.05,200,0.8,16,20.5,0,18,null,118,null,760,1.47,15,26,45,21,60,1.18,1.18,200,0.8,16,21.1,0,22,null,126,null,760,1.18,10,26,45,20,61,1.26,1.26,200,0.8,16,21.4,0,26,null,133,null,760,1.01,7,26,45,20,62,1.33,1.33,200,0.8,16,21.7,0,29]
[null,770,118.50436594925949,1,554.02439024390242,91.578860679944199,0.77278891749149481,770,118.50436594925949,1,957.80487804878044,138.0695820281334,1.1651012257831177,"","","",null,null,null,null,null,null,null,null,null,null,118,0,770,1.49,15,26,45,21,59,1.18,1.18,200,0.8,16,21.1,null,22,null,105.00000000000001,null,770,2.0699999999999998,28,26,45,21,58,1.05,1.05,200,0.8,16,20.5,0,18,null,118,null,770,1.49,15,26,45,21,59,1.18,1.18,200,0.8,16,21.1,0,22,null,127,null,770,1.2,10,26,45,20,61,1.27,1.27,200,0.8,16,21.5,0,26,null,133,null,770,1.02,7,26,45,20,62,1.33,1.33,200,0.8,16,21.7,0,29]
[null,780,119.12202777803904,1,561.21951219512198,92.120008404122089,0.77332471686739579,780,119.12202777803904,1,970.2439024390244,138.73687545938847,1.1646618014083669,"","","",null,null,null,null,null,null,null,null,null,null,119,0,780,1.51,15,26,45,21,59,1.19,1.19,200,0.8,16,21.1,null,22,null,106.00000000000001,null,780,2.1,28,26,45,21,57,1.06,1.06,200,0.8,16,20.6,0,18,null,119,null,780,1.51,15,26,45,21,59,1.19,1.19,200,0.8,16,21.1,0,22,null,128,null,780,1.21,10,26,45,21,61,1.28,1.28,200,0.8,16,21.5,0,26,null,134,null,780,1.03,8,26,45,20,62,1.34,1.34,200,0.8,16,21.8,0,29]
[null,790,119.72734556438573,0.99999999999999989,568.41463414634143,92.654519323884017,0.77387934132438629,790,119.72734556438573,0.99999999999999989,982.68292682926824,139.41389373147624,1.1644281686384141,"","","",null,null,null,null,null,null,null,null,null,null,120,0,790,1.53,16,26,45,21,59,1.2,1.2,200,0.8,16,21.2,null,22,null,106.00000000000001,null,790,2.13,29,26,45,21,57,1.06,1.06,200,0.8,16,20.6,0,18,null,120,null,790,1.53,16,26,45,21,59,1.2,1.2,200,0.8,16,21.2,0,22,null,128,null,790,1.23,11,26,45,21,60,1.28,1.28,200,0.8,16,21.5,0,26,null,135,null,790,1.04,8,26,45,20,61,1.35,1.35,200,0.8,16,21.8,0,29]
[null,800,120.32050556033536,1,575.60975609756099,93.182524194715313,0.7744525653442208,800,120.32050556033536,1,995.1219512195122,140.10560929015008,1.1644366738460334,"","","",null,null,null,null,null,null,null,null,null,null,120,0,800,1.55,16,26,45,21,59,1.2,1.2,200,0.8,16,21.2,null,22,null,107.00000000000001,null,800,2.15,30,26,45,21,57,1.07,1.07,200,0.8,16,20.6,0,18,null,120,null,800,1.55,16,26,45,21,59,1.2,1.2,200,0.8,16,21.2,0,22,null,129,null,800,1.24,11,26,45,21,60,1.29,1.29,200,0.8,16,21.6,0,26,null,136,null,800,1.06,8,26,45,20,61,1.36,1.36,200,0.8,16,21.8,0,29]
[null,810,120.90176894809926,1,582.80487804878044,93.70414661598231,0.77504363609607452,810,120.90176894809926,1,"",{"$f":"IF(K98>$B$11,\"\",$J$5*K98^6+$K$5*K98^5+$L$5*K98^4+$M$5*K98^3+$N$5*K98^2+$O$5*K98)","v":""},{"$f":"IF(K98>$B$11,\"\",1/$C98*L98)","v":""},"","","",null,null,null,null,null,null,null,null,null,null,121,0,810,1.57,16,26,45,21,59,1.21,1.21,200,0.8,16,21.2,null,22,null,107.00000000000001,null,810,2.1800000000000002,30,26,45,21,57,1.07,1.07,200,0.8,16,20.6,0,18,null,121,null,810,1.57,16,26,45,21,59,1.21,1.21,200,0.8,16,21.2,0,22,null,130,null,810,1.26,11,26,45,21,60,1.3,1.3,200,0.8,16,21.6,0,26,null,136,null,810,1.07,8,26,45,20,61,1.36,1.36,200,0.8,16,21.9,0,29]
[null,820,121.4714817398353,1,590,94.219503411384807,0.77565122333143077,820,121.4714817398353,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,121,0,820,1.59,17,26,45,21,59,1.21,1.21,200,0.8,16,21.2,null,22,null,108.00000000000001,null,820,2.21,31,26,45,21,57,1.08,1.08,200,0.8,16,20.6,0,18,null,121,null,820,1.59,17,26,45,21,59,1.21,1.21,200,0.8,16,21.2,0,22,null,130,null,820,1.28,11,26,45,21,60,1.3,1.3,200,0.8,16,21.6,0,26,null,137,null,820,1.08,8,26,45,20,61,1.37,1.37,200,0.8,16,21.9,0,29]
[null,830,122.03008500867529,0.99999999999999989,597.19512195121945,94.728705013478717,0.77627336739742758,830,122.03008500867529,0.99999999999999989,"","","","","","",null,null,null,null,null,null,null,null,null,null,122,0,830,1.61,17,26,45,21,59,1.22,1.22,200,0.8,16,21.3,null,22,null,108.00000000000001,null,830,2.23,32,26,45,22,57,1.08,1.08,200,0.8,16,20.7,0,18,null,122,null,830,1.61,17,26,45,21,59,1.22,1.22,200,0.8,16,21.3,0,22,null,131,null,830,1.29,12,26,45,21,60,1.31,1.31,200,0.8,16,21.6,0,26,null,137,null,830,1.1000000000000001,9,26,45,20,61,1.37,1.37,200,0.8,16,21.9,0,29]
[null,840,122.57812545100751,1,604.39024390243901,95.231855852271366,0.7769074253818149,840,122.57812545100751,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,123,0,840,1.63,18,26,45,21,58,1.23,1.23,200,0.8,16,21.3,null,22,null,109.00000000000001,null,840,2.2599999999999998,32,26,45,22,57,1.0900000000000001,1.0900000000000001,200,0.8,16,20.7,0,18,null,123,null,840,1.63,18,26,45,21,58,1.23,1.23,200,0.8,16,21.3,0,22,null,132,null,840,1.31,12,26,45,21,60,1.32,1.32,200,0.8,16,21.7,0,26,null,137.99999999999997,null,840,1.1100000000000001,9,26,45,20,61,1.38,1.38,200,0.8,16,21.9,0,29]
[null,850,123.11626628001707,0.99999999999999989,611.58536585365846,95.729054747886835,0.77755001544767077,850,123.11626628001707,0.99999999999999989,"","","","","","",null,null,null,null,null,null,null,null,null,null,123,0,850,1.65,18,26,45,21,58,1.23,1.23,200,0.8,16,21.3,null,22,null,109.00000000000001,null,850,2.29,33,26,45,22,57,1.0900000000000001,1.0900000000000001,200,0.8,16,20.7,0,18,null,123,null,850,1.65,18,26,45,21,58,1.23,1.23,200,0.8,16,21.3,0,22,null,132,null,850,1.32,12,26,45,21,60,1.32,1.32,200,0.8,16,21.7,0,26,null,138.99999999999997,null,850,1.1200000000000001,9,26,45,21,60,1.39,1.39,200,0.8,16,22,0,29]
[null,860,123.64529845048105,0.99999999999999989,618.78048780487802,96.220395307303676,0.77819695947306211,860,123.64529845048105,0.99999999999999989,"","","","","","",null,null,null,null,null,null,null,null,null,null,124,0,860,1.66,18,26,45,21,58,1.24,1.24,200,0.8,16,21.3,null,22,null,110.00000000000001,null,860,2.31,34,26,45,22,57,1.1000000000000001,1.1000000000000001,200,0.8,16,20.7,0,18,null,124,null,860,1.66,18,26,45,21,58,1.24,1.24,200,0.8,16,21.3,0,22,null,133,null,860,1.34,12,26,45,21,59,1.33,1.33,200,0.8,16,21.7,0,26,null,138.99999999999997,null,860,1.1399999999999999,9,26,45,21,60,1.39,1.39,200,0.8,16,22,0,29]
[null,870,124.16615221481962,0.99999999999999989,625.97560975609758,96.705966325162905,0.77884322418119301,870,124.16615221481962,0.99999999999999989,"","","","","","",null,null,null,null,null,null,null,null,null,null,124,0,870,1.68,19,26,45,21,58,1.24,1.24,200,0.8,16,21.3,null,22,null,110.00000000000001,null,870,2.34,35,26,45,22,56,1.1000000000000001,1.1000000000000001,200,0.8,16,20.8,0,18,null,124,null,870,1.68,19,26,45,21,58,1.24,1.24,200,0.8,16,21.3,0,22,null,133,null,870,1.35,13,26,45,21,59,1.33,1.33,200,0.8,16,21.7,0,26,null,139.99999999999997,null,870,1.1499999999999999,9,26,45,21,60,1.4,1.4,200,0.8,16,22,0,29]
[null,880,124.6799090104052,1,633.17073170731703,97.185852188648312,0.7794828610320661,880,124.6799090104052,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,125,0,880,1.7,19,26,45,21,58,1.25,1.25,200,0.8,16,21.4,null,22,null,111.00000000000001,null,880,2.37,35,26,45,22,56,1.1100000000000001,1.1100000000000001,200,0.8,16,20.8,0,18,null,125,null,880,1.7,19,26,45,21,58,1.25,1.25,200,0.8,16,21.4,0,22,null,134,null,880,1.37,13,26,45,21,59,1.34,1.34,200,0.8,16,21.8,0,26,null,141,null,880,1.1599999999999999,9,26,45,21,60,1.41,1.41,200,0.8,16,22.1,0,29]
[null,890,125.18781367812502,0.99999999999999989,640.36585365853659,97.660133286437258,0.78010894524873486,890,125.18781367812502,0.99999999999999989,"","","","","","",null,null,null,null,null,null,null,null,null,null,125,0,890,1.72,20,26,45,21,58,1.25,1.25,200,0.8,16,21.4,null,22,null,111.00000000000001,null,890,2.39,36,26,45,22,56,1.1100000000000001,1.1100000000000001,200,0.8,16,20.8,0,18,null,125,null,890,1.72,20,26,45,21,58,1.25,1.25,200,0.8,16,21.4,0,22,null,134,null,890,1.38,13,26,45,21,59,1.34,1.34,200,0.8,16,21.8,0,26,null,141,null,890,1.18,10,26,45,21,60,1.41,1.41,200,0.8,16,22.1,0,29]
[null,900,125.69128701220194,1,647.56097560975604,98.128886421723138,0.78071351447134862,900,125.69128701220194,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,126,0,900,1.74,20,26,45,21,58,1.26,1.26,200,0.8,16,21.4,null,22,null,112.00000000000001,null,900,2.42,37,26,45,22,56,1.1200000000000001,1.1200000000000001,200,0.8,16,20.8,0,18,null,126,null,900,1.74,20,26,45,21,58,1.26,1.26,200,0.8,16,21.4,0,22,null,135,null,900,1.4,13,26,45,21,59,1.35,1.35,200,0.8,16,21.8,0,26,null,142,null,900,1.19,10,26,45,21,60,1.42,1.42,200,0.8,16,22.1,0,29]
[null,910,126.1919386412705,1,654.7560975609756,98.592185229309251,0.78128750767178667,910,126.1919386412705,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,126,0,910,1.76,20,26,45,21,58,1.26,1.26,200,0.8,16,21.4,null,22,null,112.00000000000001,null,910,2.4500000000000002,38,26,45,22,56,1.1200000000000001,1.1200000000000001,200,0.8,16,20.8,0,18,null,126,null,910,1.76,20,26,45,21,58,1.26,1.26,200,0.8,16,21.4,0,22,null,136,null,910,1.42,14,26,45,21,59,1.36,1.36,200,0.8,16,21.8,0,26,null,142,null,910,1.2,10,26,45,21,60,1.42,1.42,200,0.8,16,22.1,0,29]
[null,920,126.6915802407089,1,661.95121951219505,99.050100596773603,0.7818207051217011,920,126.6915802407089,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,127,0,920,1.78,21,26,45,21,58,1.27,1.27,200,0.8,16,21.5,null,22,null,112.99999999999999,null,920,2.48,38,26,45,22,56,1.1299999999999999,1.1299999999999999,200,0.8,16,20.8,0,18,null,127,null,920,1.78,21,26,45,21,58,1.27,1.27,200,0.8,16,21.5,0,22,null,136,null,920,1.43,14,26,45,21,59,1.36,1.36,200,0.8,16,21.9,0,26,null,143,null,920,1.22,10,26,45,21,60,1.43,1.43,200,0.8,16,22.2,0,29]
[null,930,127.19223907622865,1,669.14634146341461,99.502701089705198,0.78230167038785592,930,127.19223907622865,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,{"$f":"IF($AA$13=$AS$13,AS110,IF($AA$13=$BK$13,BK110,IF($AA$13=$CC$13,CC110,IF($AA$13=$CU$13,CU110,\"-\"))))","v":127},{"$f":"IF($AA$13=$AS$13,AT110,IF($AA$13=$BK$13,BL110,IF($AA$13=$CC$13,CD110,IF($AA$13=$CU$13,CV110,\"-\"))))","v":0},{"$f":"IF($AA$13=$AS$13,AU110,IF($AA$13=$BK$13,BM110,IF($AA$13=$CC$13,CE110,IF($AA$13=$CU$13,CW110,\"-\"))))","v":930},{"$f":"IF($AA$13=$AS$13,AV110,IF($AA$13=$BK$13,BN110,IF($AA$13=$CC$13,CF110,IF($AA$13=$CU$13,CX110,\"-\"))))","v":1.8},{"$f":"IF($AA$13=$AS$13,AW110,IF($AA$13=$BK$13,BO110,IF($AA$13=$CC$13,CG110,IF($AA$13=$CU$13,CY110,\"-\"))))","v":21},{"$f":"IF($AA$13=$AS$13,AX110,IF($AA$13=$BK$13,BP110,IF($AA$13=$CC$13,CH110,IF($AA$13=$CU$13,CZ110,\"-\"))))","v":26},{"$f":"IF($AA$13=$AS$13,AY110,IF($AA$13=$BK$13,BQ110,IF($AA$13=$CC$13,CI110,IF($AA$13=$CU$13,DA110,\"-\"))))","v":45},{"$f":"IF($AA$13=$AS$13,AZ110,IF($AA$13=$BK$13,BR110,IF($AA$13=$CC$13,CJ110,IF($AA$13=$CU$13,DB110,\"-\"))))","v":21},{"$f":"IF($AA$13=$AS$13,BA110,IF($AA$13=$BK$13,BS110,IF($AA$13=$CC$13,CK110,IF($AA$13=$CU$13,DC110,\"-\"))))","v":58},{"$f":"IF($AA$13=$AS$13,BB110,IF($AA$13=$BK$13,BT110,IF($AA$13=$CC$13,CL110,IF($AA$13=$CU$13,DD110,\"-\"))))","v":1.27},{"$f":"IF($AA$13=$AS$13,BC110,IF($AA$13=$BK$13,BU110,IF($AA$13=$CC$13,CM110,IF($AA$13=$CU$13,DE110,\"-\"))))","v":1.27},{"$f":"IF($AA$13=$AS$13,BD110,IF($AA$13=$BK$13,BV110,IF($AA$13=$CC$13,CN110,IF($AA$13=$CU$13,DF110,\"-\"))))","v":200},{"$f":"IF($AA$13=$AS$13,BE110,IF($AA$13=$BK$13,BW110,IF($AA$13=$CC$13,CO110,IF($AA$13=$CU$13,DG110,\"-\"))))","v":0.8},{"$f":"IF($AA$13=$AS$13,BF110,IF($AA$13=$BK$13,BX110,IF($AA$13=$CC$13,CP110,IF($AA$13=$CU$13,DH110,\"-\"))))","v":16},{"$f":"IF($AA$13=$AS$13,BG110,IF($AA$13=$BK$13,BY110,IF($AA$13=$CC$13,CQ110,IF($AA$13=$CU$13,DI110,\"-\"))))","v":21.5},null,{"$f":"IF($AA$13=$AS$13,BI110,IF($AA$13=$BK$13,CA110,IF($AA$13=$CC$13,CS110,IF($AA$13=$CU$13,DK110,\"-\"))))","v":22},null,112.99999999999999,null,930,2.5,39,26,45,22,56,1.1299999999999999,1.1299999999999999,200,0.8,16,20.9,0,18,null,127,null,930,1.8,21,26,45,21,58,1.27,1.27,200,0.8,16,21.5,0,22,null,137,null,930,1.45,14,26,45,21,59,1.37,1.37,200,0.8,16,21.9,0,26,null,144,null,930,1.23,11,26,45,21,59,1.44,1.44,200,0.8,16,22.2,0,29]
[null,940,127.69617187871694,1,676.34146341463418,99.950053381011998,0.78271769553078219,940,127.69617187871694,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,128,0,940,1.82,22,26,45,21,58,1.28,1.28,200,0.8,16,21.5,null,22,null,113.99999999999999,null,940,2.5299999999999998,40,26,45,22,56,1.1399999999999999,1.1399999999999999,200,0.8,16,20.9,0,18,null,128,null,940,1.82,22,26,45,21,58,1.28,1.28,200,0.8,16,21.5,0,22,null,137,null,940,1.46,14,26,45,21,58,1.37,1.37,200,0.8,16,21.9,0,26,null,144,null,940,1.24,11,26,45,21,59,1.44,1.44,200,0.8,16,22.2,0,29]
[null,950,128.20587905033977,1,683.53658536585363,100.39222268429924,0.78305475090483523,950,128.20587905033977,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,128,0,950,1.84,22,26,45,21,57,1.28,1.28,200,0.8,16,21.5,null,22,null,113.99999999999999,null,950,2.56,41,26,45,22,56,1.1399999999999999,1.1399999999999999,200,0.8,16,20.9,0,18,null,128,null,950,1.84,22,26,45,21,57,1.28,1.28,200,0.8,16,21.5,0,22,null,137.99999999999997,null,950,1.48,15,26,45,21,58,1.38,1.38,200,0.8,16,21.9,0,26,null,145,null,950,1.26,11,26,45,21,59,1.45,1.45,200,0.8,16,22.2,0,29]
[null,960,128.724119201897,1,690.73170731707319,100.82927319132011,0.78329744119806111,960,128.724119201897,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,129,0,960,1.86,23,26,45,21,57,1.29,1.29,200,0.8,16,21.5,null,22,null,113.99999999999999,null,960,2.58,41,26,45,22,56,1.1399999999999999,1.1399999999999999,200,0.8,16,20.9,0,18,null,129,null,960,1.86,23,26,45,21,57,1.29,1.29,200,0.8,16,21.5,0,22,null,137.99999999999997,null,960,1.49,15,26,45,21,58,1.38,1.38,200,0.8,16,22,0,26,null,145,null,960,1.27,11,26,45,21,59,1.45,1.45,200,0.8,16,22.3,0,29]
[null,970,{"$f":"$J$4*B114^6+$K$4*B114^5+$L$4*B114^4+$M$4*B114^3+$N$4*B114^2+$O$4*B114","v":129.25392402143666},1,697.92682926829264,101.26126851349707,0.7834289696048452,970,129.25392402143666,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,129,0,970,1.88,23,26,45,21,57,1.29,1.29,200,0.8,16,21.6,null,22,null,114.99999999999999,null,970,2.61,42,26,45,22,56,1.1499999999999999,1.1499999999999999,200,0.8,16,20.9,0,18,null,129,null,970,1.88,23,26,45,21,57,1.29,1.29,200,0.8,16,21.6,0,22,null,138.99999999999997,null,970,1.51,15,26,45,21,58,1.39,1.39,200,0.8,16,22,0,26,null,146,null,970,1.28,11,26,45,21,59,1.46,1.46,200,0.8,16,22.3,0,29]
[null,980,{"$f":"$J$4*B115^6+$K$4*B115^5+$L$4*B115^4+$M$4*B115^3+$N$4*B115^2+$O$4*B115","v":129.79861347412299},1,705.1219512195122,101.68827212751472,0.7834311122883264,980,129.79861347412299,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,130,0,980,1.9,23,26,45,21,57,1.3,1.3,200,0.8,16,21.6,null,22,null,114.99999999999999,null,980,2.64,43,26,45,22,55,1.1499999999999999,1.1499999999999999,200,0.8,16,21,0,18,null,130,null,980,1.9,23,26,45,21,57,1.3,1.3,200,0.8,16,21.6,0,22,null,138.99999999999997,null,980,1.53,16,26,45,21,58,1.39,1.39,200,0.8,16,22,0,26,null,146,null,980,1.3,12,26,45,21,59,1.46,1.46,200,0.8,16,22.3,0,29]
[null,990,{"$f":"$J$4*B116^6+$K$4*B116^5+$L$4*B116^4+$M$4*B116^3+$N$4*B116^2+$O$4*B116","v":130.36181133336174},1,712.31707317073165,102.11034782498379,0.7832842055551591,990,130.36181133336174,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,130,0,990,1.92,24,26,45,22,57,1.3,1.3,200,0.8,16,21.6,null,22,null,115.99999999999999,null,990,2.66,44,26,45,22,55,1.1599999999999999,1.1599999999999999,200,0.8,16,21,0,18,null,130,null,990,1.92,24,26,45,22,57,1.3,1.3,200,0.8,16,21.6,0,22,null,139.99999999999997,null,990,1.54,16,26,45,21,58,1.4,1.4,200,0.8,16,22,0,26,null,147,null,990,1.31,12,26,45,21,59,1.47,1.47,200,0.8,16,22.3,0,29]
[null,1000,{"$f":"$J$4*B117^6+$K$4*B117^5+$L$4*B117^4+$M$4*B117^3+$N$4*B117^2+$O$4*B117","v":130.9474610431825},1,719.51219512195121,102.52756016617658,0.78296714842272586,1000,130.9474610431825,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,131,0,1000,1.94,24,26,45,22,57,1.31,1.31,200,0.8,16,21.6,null,22,null,115.99999999999999,null,1000,2.69,45,26,45,22,55,1.1599999999999999,1.1599999999999999,200,0.8,16,21,0,18,null,131,null,1000,1.94,24,26,45,22,57,1.31,1.31,200,0.8,16,21.6,0,22,null,139.99999999999997,null,1000,1.56,16,26,45,21,58,1.4,1.4,200,0.8,16,22,0,26,null,147,null,1000,1.32,12,26,45,21,59,1.47,1.47,200,0.8,16,22.3,0,29]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"q sensibel"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"W/K"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"DW18/(DT18-DP18)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"DW50/(DT50-DP50)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"DW82/(DT82-DP82)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"DW114/(DT114-DP114)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"DW115/(DT115-DP115)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"DW116/(DT116-DP116)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"DW117/(DT117-DP117)*1000","v":{"$error":"#DIV/0!"}}]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"q sensibel"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"W/K"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"EM18/(EJ18-EF18)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"EM50/(EJ50-EF50)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"EM82/(EJ82-EF82)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"EM114/(EJ114-EF114)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"EM115/(EJ115-EF115)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"EM116/(EJ116-EF116)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"BU441/(BP441-BX441)*1000","v":{"$error":"#DIV/0!"}}]

{"sheet":"BG;WT2,5;k 100kg_h","index":6,"n_rows":441,"n_cols":115,"rows_kept":441,"cut":false,"hidden":true,"merged":[]}
["TT",null,"Master auswählen ->","BG","WT","Verhältnis","DpK =","Verhältnis",{"$f":"CONCATENATE(\"Polynom 6 Ordnung - \",A3)","v":"Polynom 6 Ordnung - BG;WT2,5;k 100kg_h"},6,5,4,3,2,1,0]
["2017-08-14",null,null,"BG 800",{"$f":"VLOOKUP(D2,D3:F6,2,0)","v":820},{"$f":"VLOOKUP(D2,D3:F6,3,0)","v":1},{"$f":"VLOOKUP(D2,D3:G6,4,0)","v":7},{"$f":"VLOOKUP(E2,E3:H6,4,0)","v":1},{"$f":"D2","v":"BG 800"},{"$f":"VLOOKUP($I2,$I$3:$P$6,2,0)","v":1.0830659638580856E-16},{"$f":"VLOOKUP($I2,$I$3:$P$6,3,0)","v":-1.2111372094670782E-13},{"$f":"VLOOKUP($I2,$I$3:$P$6,4,0)","v":-3.6536770359835539E-10},{"$f":"VLOOKUP($I2,$I$3:$P$6,5,0)","v":8.7368153028134265E-7},{"$f":"VLOOKUP($I2,$I$3:$P$6,6,0)","v":-7.7215094251533052E-4},{"$f":"VLOOKUP($I2,$I$3:$P$6,7,0)","v":0.3648995012270973},{"$f":"VLOOKUP($I2,$I$3:$P$6,8,0)","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"  Datentabelle aus Eurocoil entnehmen"]
[{"$f":"MID(CELL(\"dateiname\",A1),FIND(\"]\",CELL(\"dateiname\",A1))+1,255)","v":"BG;WT2,5;k 100kg_h"},null,null,"BG 630",590,{"$f":"E3/$E$2","v":0.71951219512195119},{"$f":"BI18","v":5},{"$f":"G3/$G$2","v":0.7142857142857143},{"$f":"D3","v":"BG 630"},{"$f":"LINEST(AS18:AS117,AU18:AU117^{1,2,3,4,5,6},0,0)","v":-2.1585851685865881E-16},9.6767155892923754E-13,-1.76717709481768E-9,1.7202353252286216E-6,-9.8993263846897822E-4,0.36491528136314816,0]
[null,null,null,"BG 800",820,{"$f":"E4/$E$2","v":1},{"$f":"CA18","v":7},{"$f":"G4/$G$2","v":1},{"$f":"D4","v":"BG 800"},{"$f":"LINEST(BK18:BK117,BM18:BM117^{1,2,3,4,5,6},0,0)","v":1.0830659638580856E-16},-1.2111372094670782E-13,-3.6536770359835539E-10,8.7368153028134265E-7,-7.7215094251533052E-4,0.3648995012270973,0]
["WT 4L",2.5,"mm","BG 1000",1020,{"$f":"E5/$E$2","v":1.2439024390243902},{"$f":"CS18","v":8},{"$f":"G5/$G$2","v":1.1428571428571428},{"$f":"D5","v":"BG 1000"},{"$f":"LINEST(CC18:CC117,CE18:CE117^{1,2,3,4,5,6},0,0)","v":3.8400710421018372E-16},-1.0502095553434736E-12,8.4104538271664022E-10,1.3456305784766211E-7,-5.7569750565271026E-4,0.35976596437670394,0]
["Länge",820,"mm","BG 1200",1200,{"$f":"E6/$E$2","v":1.4634146341463414},{"$f":"DK18","v":9},{"$f":"G6/$G$2","v":1.2857142857142858},{"$f":"D6","v":"BG 1200"},{"$f":"LINEST(CU18:CU116,CW18:CW116^{1,2,3,4,5,6},0,0)","v":6.5952356269416348E-16},-1.9358022327234007E-12,1.9476342196471649E-9,-5.2879885604381321E-7,-3.9622250780243888E-4,0.35118500195987817,0]
["Rohrreihen",3,null,null,null,null,"Wassermenge =",{"$f":"DF18","v":100}]
[null,null,null,null,null,null,null,null,{"$f":"CONCATENATE(\"Korrekturfaktoren - \",A3)","v":"Korrekturfaktoren - BG;WT2,5;k 100kg_h"},6,5,4,3,2,1,0]
[null,null,null,null,null,null,null,null,{"$f":"D3","v":"BG 630"},{"$f":"LINEST(G18:G117,C18:C117^{0,1,2,3,4,5,6},0,0)","v":4.4566000301881142E-12},-1.2550558344868454E-9,1.3366712201526205E-7,-6.5714332305644957E-6,1.6002518177718619E-4,-1.2425320352228203E-3,0.72419322855457691]
["Grenzen",null,null,null,null,null,null,null,{"$f":"D4","v":"BG 800"},{"$f":"LINEST(J18:J117,C18:C117^{0,1,2,3,4,5,6},0,0)","v":1.0582646592605707E-25},-1.7621592528842504E-23,3.6181316623453139E-22,7.4973374569093213E-20,-4.6128217448810735E-18,8.1173298016182363E-17,0.99999999999999978]
["Maximum",{"$f":"MAX(B18:B117)","v":1000},"m³/h",null,null,null,null,null,{"$f":"D5","v":"BG 1000"},{"$f":"LINEST(M18:M97,C18:C97^{0,1,2,3,4,5,6},0,0)","v":-1.1156618577769332E-11},2.9091676841380912E-9,-2.8336018310601808E-7,1.2729897620643233E-5,-2.9055661853874282E-4,3.0166626458146793E-3,1.2191462572339027]
[null,null,null,null,null,null,null,null,{"$f":"D6","v":"BG 1200"},{"$f":"LINEST(P18:P84,C18:C84^{0,1,2,3,4,5,6},0,0)","v":-2.2304034800705733E-11},5.502366077674025E-9,-5.0170536738490245E-7,2.0985076178010226E-5,-4.7224469569811346E-4,5.6063631895718596E-3,1.398223242791282,null,null,null,null,null,null,null,null,null,null,null,null,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,null,null,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,null,null,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,null,null,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,null,null,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15]
[null,{"$f":"CONCATENATE(\"Master - \",AA13)","v":"Master - BG 800"},null,null,{"$f":"AS13","v":"BG630"},null,null,{"$f":"BK13","v":"BG 800"},null,null,{"$f":"CC13","v":"BG1000"},null,null,{"$f":"CU13","v":"BG1200"},null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"D2","v":"BG 800"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"BG630",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"BG 800",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"BG1000",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"BG1200"]
[null,"Volumen-nstrom","spez. \nLeistung","Korrektur-faktor","Volumen-nstrom","spez. \nLeistung","Korrektur-faktor","Volumen-nstrom","spez. \nLeistung","Korrektur-faktor","Volumen-nstrom","spez. \nLeistung","Korrektur-faktor","Volumen-nstrom","spez. \nLeistung","Korrektur-faktor",null,null,null,null,null,null,null,null,null,null,{"$f":"IF($AA$13=$AS$13,AS14,IF($AA$13=$BK$13,BK14,IF($AA$13=$CC$13,CC14,IF($AA$13=$CU$13,CU14,\"-\"))))","v":"q sensibel"},"S","QA","VA","DPA","TAI","UR","TAO","UR","PT","PS","QW","VW","TWI","TWO",null,{"$f":"IF($AA$13=$AS$13,BI14,IF($AA$13=$BK$13,CA14,IF($AA$13=$CC$13,CS14,IF($AA$13=$CU$13,DK14,\"-\"))))","v":"DPW"},null,"q sensibel","S","QA","VA","DPA","TAI","UR","TAO","UR","PT","PS","QW","VW","TWI","TWO",null,"DPW",null,"q sensibel","S","QA","VA","DPA","TAI","UR","TAO","UR","PT","PS","QW","VW","TWI","TWO",null,"DPW",null,"q sensibel","S","QA","VA","DPA","TAI","UR","TAO","UR","PT","PS","QW","VW","TWI","TWO",null,"DPW",null,"q sensibel","S","QA","VA","DPA","TAI","UR","TAO","UR","PT","PS","QW","VW","TWI","TWO",null,"DPW"]
[null,"[m³/h]","[W/K]","[-]","[m³/h]","[W/K]","[-]","[m³/h]","[W/K]","[-]","[m³/h]","[W/K]","[-]","[m³/h]","[W/K]","[-]",null,null,null,null,null,null,null,null,null,null,"W/K",0,"m3/h","m/s","Pa","°C"," % ","°C"," % ","kW","kW","l/h","m/s","°C","°C",null,"kPa",null,"W/K",null,"m3/h","m/s","Pa","°C"," % ","°C"," % ","kW","kW","l/h","m/s","°C","°C",null,"kPa",null,"W/K",null,"m3/h","m/s","Pa","°C"," % ","°C"," % ","kW","kW","l/h","m/s","°C","°C",null,"kPa",null,"W/K",null,"m3/h","m/s","Pa","°C"," % ","°C"," % ","kW","kW","l/h","m/s","°C","°C",null,"kPa",null,"W/K",null,"m3/h","m/s","Pa","°C"," % ","°C"," % ","kW","kW","l/h","m/s","°C","°C",null,"kPa"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,"S","QA","VA","DPA","TAI","RH","TAO","RH","QTOT","QSEN","QW","VW","TWI","TWO",null,"DPW",null,null,"S","QA","VA","DPA","TAI","RH","TAO","RH","QTOT","QSEN","QW","VW","TWI","TWO","GLI","DPW",null,null,"S","QA","VA","DPA","TAI","RH","TAO","RH","QTOT","QSEN","QW","VW","TWI","TWO","GLI","DPW",null,null,"S","QA","VA","DPA","TAI","RH","TAO","RH","QTOT","QSEN","QW","VW","TWI","TWO","GLI","DPW",null,null,"S","QA","VA","DPA","TAI","RH","TAO","RH","QTOT","QSEN","QW","VW","TWI","TWO","GLI","DPW"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,"m3/h","m/s","Pa","°C","%","°C","%","kW","kW","l/h","m/s","°C","°C",null,"kPa",null,null,null,"m3/h","m/s","Pa","°C","%","°C","%","kW","kW","l/h","m/s","°C","°C","%","kPa",null,null,null,"m3/h","m/s","Pa","°C","%","°C","%","kW","kW","l/h","m/s","°C","°C","%","kPa",null,null,null,"m3/h","m/s","Pa","°C","%","°C","%","kW","kW","l/h","m/s","°C","°C","%","kPa",null,null,null,"m3/h","m/s","Pa","°C","%","°C","%","kW","kW","l/h","m/s","°C","°C","%","kPa"]
[null,{"$f":"AC18","v":10},{"$f":"$J$4*B18^6+$K$4*B18^5+$L$4*B18^4+$M$4*B18^3+$N$4*B18^2+$O$4*B18","v":3.5726499338696196},{"$f":"1/C18*C18","v":1},{"$f":"IF($B18*$F$3>$B$11,\"\",$B18*$F$3)","v":7.1951219512195124},{"$f":"IF(E18>$B$11,\"\",$J$3*E18^6+$K$3*E18^5+$L$3*E18^4+$M$3*E18^3+$N$3*E18^2+$O$3*E18)","v":2.5749974091196126},{"$f":"IF(E18>$B$11,\"\",1/$C18*F18)","v":0.72075279044498308},{"$f":"IF($B18*$F$4>$B$11,\"\",$B18*$F$4)","v":10},{"$f":"IF(H18>$B$11,\"\",$J$4*H18^6+$K$4*H18^5+$L$4*H18^4+$M$4*H18^3+$N$4*H18^2+$O$4*H18)","v":3.5726499338696196},{"$f":"IF(H18>$B$11,\"\",1/$C18*I18)","v":1},{"$f":"IF($B18*$F$5>$B$11,\"\",$B18*$F$5)","v":12.439024390243903},{"$f":"IF(K18>$B$11,\"\",$J$5*K18^6+$K$5*K18^5+$L$5*K18^4+$M$5*K18^3+$N$5*K18^2+$O$5*K18)","v":4.3863391329573105},{"$f":"IF(K18>$B$11,\"\",1/$C18*L18)","v":1.2277550877217813},{"$f":"IF($B18*$F$6>$B$11,\"\",$B18*$F$6)","v":14.634146341463413},{"$f":"IF(N18>$B$11,\"\",$J$6*N18^6+$K$6*N18^5+$L$6*N18^4+$M$6*N18^3+$N$6*N18^2+$O$6*N18)","v":5.0528691622684665},{"$f":"IF(N18>$B$11,\"\",1/$C18*O18)","v":1.4143196942879841},null,null,null,null,null,null,null,null,null,null,3,0,10,0.02,0,26,45,16,83,0.03,0.03,100,0.4,16,16.5,null,7,null,{"$f":"BC18/(AX18-BF18)*1000","v":3},null,10,0.03,0,26,45,16,83,0.03,0.03,100,0.4,16,16.399999999999999,0,5,null,{"$f":"BU18/(BP18-BX18)*1000","v":3},null,10,0.02,0,26,45,16,83,0.03,0.03,100,0.4,16,16.5,0,7,null,{"$f":"CM18/(CH18-CP18)*1000","v":3},null,10,0.02,0,26,45,16,83,0.03,0.03,100,0.4,16,16.600000000000001,0,8,null,{"$f":"DE18/(CZ18-DH18)*1000","v":3},null,10,0.01,0,26,45,16,83,0.03,0.03,100,0.4,16,16.600000000000001,0,9]
[null,20,6.9960602603132038,{"$f":"1/C19*C19","v":0.99999999999999989},14.390243902439025,{"$f":"IF(E19>$B$11,\"\",$J$3*E19^6+$K$3*E19^5+$L$3*E19^4+$M$3*E19^3+$N$3*E19^2+$O$3*E19)","v":5.0512765008743044},{"$f":"IF(E19>$B$11,\"\",1/$C19*F19)","v":0.72201729443767904},20,{"$f":"IF(H19>$B$11,\"\",$J$4*H19^6+$K$4*H19^5+$L$4*H19^4+$M$4*H19^3+$N$4*H19^2+$O$4*H19)","v":6.9960602603132038},{"$f":"IF(H19>$B$11,\"\",1/$C19*I19)","v":0.99999999999999989},24.878048780487806,8.5963502402426606,1.2287415946096802,29.268292682926827,{"$f":"IF(N19>$B$11,\"\",$J$6*N19^6+$K$6*N19^5+$L$6*N19^4+$M$6*N19^3+$N$6*N19^2+$O$6*N19)","v":9.9272980737001983},1.418984071651745,null,null,null,null,null,null,null,null,null,null,6,0,20,0.04,0,26,45,16,83,0.06,0.06,100,0.4,16,16.600000000000001,null,7,null,6,null,20,0.05,0,26,45,16,83,0.06,0.06,100,0.4,16,16.600000000000001,0,5,null,6,null,20,0.04,0,26,45,16,83,0.06,0.06,100,0.4,16,16.600000000000001,0,7,null,6,null,20,0.03,0,26,45,16,83,0.06,0.06,100,0.4,16,16.7,0,8,null,6,null,20,0.03,0,26,45,16,83,0.06,0.06,100,0.4,16,16.8,0,9]
[null,30,10.275339777918893,1,21.585365853658537,7.4325141753821438,0.72333512428992219,30,10.275339777918893,1,37.31707317073171,12.632266004707153,1.2293769624877182,43.90243902439024,14.616367465036767,1.4224704760076636,null,null,null,null,null,null,null,null,null,null,10,0,30,0.06,0,26,45,16,83,0.1,0.1,100,0.4,16,16.8,null,7,null,10,null,30,0.08,0,26,45,16,83,0.1,0.1,100,0.4,16,16.8,0,5,null,10,null,30,0.06,0,26,45,16,83,0.1,0.1,100,0.4,16,16.8,0,7,null,10,null,30,0.05,0,26,45,16,83,0.1,0.1,100,0.4,16,16.8,0,8,null,10,null,30,0.04,0,26,45,16,83,0.1,0.1,100,0.4,16,16.899999999999999,0,9]
[null,40,13.41550685925495,1,28.780487804878049,9.7222780950118644,0.72470449286862093,40,13.41550685925495,1,49.756097560975611,16.496729521104641,1.2296762018890137,58.536585365853654,19.115000168279067,1.4248436804377771,null,null,null,null,null,null,null,null,null,null,13.000000000000002,0,40,0.08,0,26,45,16,83,0.13,0.13,100,0.4,16,17.100000000000001,null,7,null,13.000000000000002,null,40,0.11,0,26,45,16,82,0.13,0.13,100,0.4,16,17.100000000000001,0,5,null,13.000000000000002,null,40,0.08,0,26,45,16,83,0.13,0.13,100,0.4,16,17.100000000000001,0,7,null,13.000000000000002,null,40,0.06,0,26,45,16,83,0.13,0.13,100,0.4,16,17.100000000000001,0,8,null,13.000000000000002,null,40,0.05,0,26,45,16,83,0.13,0.13,100,0.4,16,17.100000000000001,0,9]
[null,50,16.421488192456987,1,35.975609756097562,11.924028869709474,0.72612352363938815,50,16.421488192456987,1,62.195121951219512,20.192759325735363,1.2296546506065549,73.170731707317074,23.419816865041813,1.4261689677918121,null,null,null,null,null,null,null,null,null,null,16,0,50,0.1,0,26,45,16,82,0.16,0.16,100,0.4,16,17.399999999999999,null,7,null,16,null,50,0.13,0,26,45,16,81,0.16,0.16,100,0.4,16,17.399999999999999,0,5,null,16,null,50,0.1,0,26,45,16,82,0.16,0.16,100,0.4,16,17.399999999999999,0,7,null,16,null,50,0.08,0,26,45,16,83,0.16,0.16,100,0.4,16,17.399999999999999,0,8,null,16,null,50,7.0000000000000007E-2,0,26,45,16,83,0.16,0.16,100,0.4,16,17.399999999999999,0,9]
[null,60,19.298117600795937,1,43.170731707317074,14.041122220760817,0.7275902505735431,60,19.298117600795937,1,74.634146341463421,23.723715450301157,1.2293279552469247,87.804878048780481,27.528996499000705,1.4265120085010412,null,null,null,null,null,null,null,null,null,null,19,0,60,0.12,0,26,45,16,82,0.19,0.19,100,0.4,16,17.600000000000001,null,7,null,19,null,60,0.16,0,26,45,16,81,0.19,0.19,100,0.4,16,17.600000000000001,0,5,null,19,null,60,0.12,0,26,45,16,82,0.19,0.19,100,0.4,16,17.600000000000001,0,7,null,19,null,60,0.09,0,26,45,16,82,0.19,0.19,100,0.4,16,17.7,0,8,null,19,null,60,0.08,0,26,45,16,83,0.19,0.19,100,0.4,16,17.7,0,9]
[null,70,22.050134940226759,1,50.365853658536587,16.076811122990058,0.72910261849058455,70,22.050134940226759,1,87.073170731707322,27.093266499972188,1.2287120497636994,102.4390243902439,31.442141352432362,1.4259387272533861,null,null,null,null,null,null,null,null,null,null,22,0,70,0.14000000000000001,0,26,45,16,81,0.22,0.22,100,0.4,16,17.899999999999999,null,7,null,20.999999999999996,null,70,0.19,0,26,45,16,80,0.21,0.21,100,0.4,16,17.8,0,5,null,22,null,70,0.14000000000000001,0,26,45,16,81,0.22,0.22,100,0.4,16,17.899999999999999,0,7,null,22,null,70,0.11,0,26,45,16,82,0.22,0.22,100,0.4,16,17.899999999999999,0,8,null,22,null,70,0.09,0,26,45,16,82,0.22,0.22,100,0.4,16,17.899999999999999,0,9]
[null,80,24.682185074917932,1,57.560975609756099,18.034247925394098,0.73065848386821008,80,24.682185074917932,1,99.512195121951223,30.30535775566527,1.2278231308808074,117.07317073170731,35.160146786846916,1.4245151586103575,null,null,null,null,null,null,null,null,null,null,25,0,80,0.15,0,26,45,16,80,0.25,0.25,100,0.4,16,18.100000000000001,null,7,null,24,null,80,0.22,0,26,45,16,79,0.24,0.24,100,0.4,16,18,0,5,null,25,null,80,0.15,0,26,45,16,80,0.25,0.25,100,0.4,16,18.100000000000001,0,7,null,25,null,80,0.12,0,26,45,16,81,0.25,0.25,100,0.4,16,18.2,0,8,null,25,null,80,0.11,0,26,45,16,82,0.25,0.25,100,0.4,16,18.2,0,9]
[null,90,27.198816930761662,0.99999999999999989,64.756097560975604,19.916486450212922,0.73225561615099222,90,27.198816930761662,0.99999999999999989,111.95121951219512,33.364180300533747,1.2266776303346894,131.70731707317074,38.685075647713369,1.4223072917543274,null,null,null,null,null,null,null,null,null,null,27.000000000000004,0,90,0.17,0,26,45,16,80,0.27,0.27,100,0.4,16,18.3,null,7,null,26.000000000000004,null,90,0.24,1,26,45,17,78,0.26,0.26,100,0.4,16,18.2,0,5,null,27.000000000000004,null,90,0.17,0,26,45,16,80,0.27,0.27,100,0.4,16,18.3,0,7,null,28.000000000000004,null,90,0.14000000000000001,0,26,45,16,81,0.28000000000000003,0.28000000000000003,100,0.4,16,18.399999999999999,0,8,null,28.000000000000004,null,90,0.12,0,26,45,16,81,0.28000000000000003,0.28000000000000003,100,0.4,16,18.399999999999999,0,9]
[null,100,29.604482626864851,1,71.951219512195124,21.72648407043593,0.73389169958741451,100,29.604482626864851,1,124.39024390243902,36.274141170668884,1.2252921838854089,146.34146341463415,42.020037333277571,1.4193809046723929,null,null,null,null,null,null,null,null,null,null,30,0,100,0.19,0,26,45,16,79,0.3,0.3,100,0.4,16,18.600000000000001,null,7,null,28.000000000000004,null,100,0.27,1,26,45,17,77,0.28000000000000003,0.28000000000000003,100,0.4,16,18.399999999999999,0,5,null,30,null,100,0.19,0,26,45,16,79,0.3,0.3,100,0.4,16,18.600000000000001,0,7,null,31,null,100,0.16,0,26,45,16,80,0.31,0.31,100,0.4,16,18.600000000000001,0,8,null,31,null,100,0.13,0,26,45,16,81,0.31,0.31,100,0.4,16,18.7,0,9]
[null,110,31.903536685020818,0.99999999999999989,79.146341463414629,23.467103765744106,0.73556433562308643,110,31.903536685020818,0.99999999999999989,136.82926829268294,39.039834530012875,1.2236835970709998,160.97560975609755,45.169071527473051,1.4158013882103735,null,null,null,null,null,null,null,null,null,null,32,0,110,0.21,0,26,45,17,78,0.32,0.32,100,0.4,16,18.8,null,7,null,30,null,110,0.3,1,26,45,17,75,0.3,0.3,100,0.4,16,18.600000000000001,0,5,null,32,null,110,0.21,0,26,45,17,78,0.32,0.32,100,0.4,16,18.8,0,7,null,33,null,110,0.17,0,26,45,16,79,0.33,0.33,100,0.4,16,18.8,0,8,null,34,null,110,0.15,0,26,45,16,80,0.34,0.34,100,0.4,16,18.899999999999999,0,9]
[null,120,34.100235317161761,1,86.341463414634148,25.141116156888216,0.73727104587560854,120,34.100235317161761,1,149.26829268292684,41.666013869483344,1.2218688077062601,175.60975609756096,48.137036596924389,1.4116335605666119,null,null,null,null,null,null,null,null,null,null,34,0,120,0.23,0,26,45,17,77,0.34,0.34,100,0.4,16,19,null,7,null,32,null,120,0.32,1,26,45,17,75,0.32,0.32,100,0.4,16,18.8,0,5,null,34,null,120,0.23,0,26,45,17,77,0.34,0.34,100,0.4,16,19,0,7,null,34.999999999999993,null,120,0.19,0,26,45,16,78,0.35,0.35,100,0.4,16,19.100000000000001,0,8,null,36,null,120,0.16,0,26,45,16,79,0.36,0.36,100,0.4,16,19.100000000000001,0,9]
[null,130,36.198735790791993,1,93.536585365853654,26.751201518502892,0.73900927571364783,130,36.198735790791993,1,161.70731707317074,44.157565230309473,1.2198648451568852,190.2439024390244,50.929502652043453,1.406941472939466,null,null,null,null,null,null,null,null,null,null,36,0,130,0.25,1,26,45,17,76,0.36,0.36,100,0.4,16,19.100000000000001,null,7,null,34,null,130,0.35,1,26,45,17,74,0.34,0.34,100,0.4,16,18.899999999999999,0,5,null,36,null,130,0.25,1,26,45,17,76,0.36,0.36,100,0.4,16,19.100000000000001,0,7,null,38,null,130,0.2,0,26,45,17,78,0.38,0.38,100,0.4,16,19.3,0,8,null,39,null,130,0.17,0,26,45,16,79,0.39,0.39,100,0.4,16,19.3,0,9]
[null,140,38.203095872401882,1,100.73170731707317,28.299951770356657,0.74077639845939003,140,38.203095872401882,1,174.14634146341464,46.519481451579608,1.2176887864521349,204.8780487804878,53.552649272218233,1.4017882071935679,null,null,null,null,null,null,null,null,null,null,{"$f":"IF($AA$13=$AS$13,AS31,IF($AA$13=$BK$13,BK31,IF($AA$13=$CC$13,CC31,IF($AA$13=$CU$13,CU31,\"-\"))))","v":39},0,140,0.27,1,26,45,17,75,0.39,0.39,100,0.4,16,19.3,null,7,null,36,null,140,0.38,1,26,45,18,73,0.36,0.36,100,0.4,16,19.100000000000001,0,5,null,39,null,140,0.27,1,26,45,17,75,0.39,0.39,100,0.4,16,19.3,0,7,null,40,null,140,0.22,0,26,45,17,77,0.4,0.4,100,0.4,16,19.399999999999999,0,8,null,40.999999999999993,null,140,0.19,0,26,45,17,78,0.41,0.41,100,0.4,16,19.5,0,9]
[null,150,40.117273348862589,1,107.92682926829268,29.789872447037887,0.74256972022956524,150,40.117273348862589,1,186.58536585365854,48.756837442000496,1.2153577093340233,219.51219512195121,56.013167895094469,1.3962356665668696,null,null,null,null,null,null,null,null,null,null,40,0,150,0.28999999999999998,1,26,45,17,75,0.4,0.4,100,0.4,16,19.5,null,7,null,38,null,150,0.4,1,26,45,18,72,0.38,0.38,100,0.4,16,19.2,0,5,null,40,null,150,0.28999999999999998,1,26,45,17,75,0.4,0.4,100,0.4,16,19.5,0,7,null,41.999999999999993,null,150,0.23,0,26,45,17,76,0.42,0.42,100,0.4,16,19.600000000000001,0,8,null,43,null,150,0.2,0,26,45,17,77,0.43,0.43,100,0.4,16,19.7,0,9]
[null,160,41.945125626801513,0.99999999999999989,115.1219512195122,31.223384646076724,0.74438648542575914,160,41.945125626801513,0.99999999999999989,199.02439024390245,50.874766475868043,1.2128886423780501,234.14634146341461,58.318168869949915,1.3903443606016184,null,null,null,null,null,null,null,null,null,null,41.999999999999993,0,160,0.31,1,26,45,17,74,0.42,0.42,100,0.4,16,19.600000000000001,null,7,null,39,null,160,0.43,2,26,45,18,71,0.39,0.39,100,0.4,16,19.399999999999999,0,5,null,41.999999999999993,null,160,0.31,1,26,45,17,74,0.42,0.42,100,0.4,16,19.600000000000001,0,7,null,44,null,160,0.25,1,26,45,17,75,0.44,0.44,100,0.4,16,19.8,0,8,null,45,null,160,0.21,0,26,45,17,76,0.45,0.45,100,0.4,16,19.899999999999999,0,9]
[null,170,43.690409409958534,1,122.3170731707317,32.602826954502881,0.74622388287969632,170,43.690409409958534,1,211.46341463414635,52.878437513249587,1.2102985123594834,248.78048780487805,60.475093175161398,1.3841731856460255,null,null,null,null,null,null,null,null,null,null,44,0,170,0.33,1,26,45,18,73,0.44,0.44,100,0.4,16,19.8,null,7,null,40.999999999999993,null,170,0.46,2,26,45,18,70,0.41,0.41,100,0.4,16,19.5,0,5,null,44,null,170,0.33,1,26,45,18,73,0.44,0.44,100,0.4,16,19.8,0,7,null,46,null,170,0.26,1,26,45,17,75,0.46,0.46,100,0.4,16,20,0,8,null,47,null,170,0.22,0,26,45,17,76,0.47,0.47,100,0.4,16,20.100000000000001,0,9]
[null,180,45.356780454522955,1,129.51219512195121,33.930457353839437,0.74807905265365693,180,45.356780454522955,1,223.90243902439025,54.77303354437781,1.2076040890798252,263.41463414634148,62.49162879976447,1.3777792024374789,null,null,null,null,null,null,null,null,null,null,46,0,180,0.35,1,26,45,18,72,0.46,0.46,100,0.4,16,19.899999999999999,null,7,null,41.999999999999993,null,180,0.48,2,26,45,18,69,0.42,0.42,100,0.4,16,19.600000000000001,0,5,null,46,null,180,0.35,1,26,45,18,72,0.46,0.46,100,0.4,16,19.899999999999999,0,7,null,48,null,180,0.28000000000000003,1,26,45,17,74,0.48,0.48,100,0.4,16,20.100000000000001,0,8,null,49,null,180,0.24,1,26,45,17,75,0.49,0.49,100,0.4,16,20.2,0,9]
[null,190,46.947793402451211,1,136.70731707317071,35.208455103532536,0.74994909349017991,190,46.947793402451211,1,236.34146341463415,56.563730958256173,1.2048219279098833,278.04878048780489,64.375631789105924,1.3712174124406191,null,null,null,null,null,null,null,null,null,null,47,0,190,0.37,1,26,45,18,71,0.47,0.47,100,0.4,16,20.100000000000001,null,7,null,43,null,190,0.51,2,26,45,19,69,0.43,0.43,100,0.4,16,19.7,0,5,null,47,null,190,0.37,1,26,45,18,71,0.47,0.47,100,0.4,16,20.100000000000001,0,7,null,50,null,190,0.3,1,26,45,18,73,0.5,0.5,100,0.4,16,20.3,0,8,null,51.000000000000007,null,190,0.25,1,26,45,17,75,0.51,0.51,100,0.4,16,20.399999999999999,0,9]
[null,200,48.466901692765354,0.99999999999999989,143.90243902439025,36.438922602817001,0.75183107089876622,200,48.466901692765354,0.99999999999999989,248.78048780487805,58.25567993547584,1.2019683103484136,292.6829268292683,66.135051954588846,1.3645405347720176,null,null,null,null,null,null,null,null,null,null,49,0,200,0.39,1,26,45,18,71,0.49,0.49,100,0.4,16,20.2,null,7,null,45,null,200,0.54,2,26,45,19,68,0.45,0.45,100,0.4,16,19.8,0,5,null,49,null,200,0.39,1,26,45,18,71,0.49,0.49,100,0.4,16,20.2,0,7,null,51.000000000000007,null,200,0.31,1,26,45,18,72,0.51,0.51,100,0.4,16,20.399999999999999,0,8,null,53.000000000000007,null,200,0.26,1,26,45,17,74,0.53,0.53,100,0.4,16,20.6,0,9]
[null,210,49.917457550832253,1,151.09756097560975,37.62388723101791,0.7537220258604822,210,49.917457550832253,1,261.21951219512192,59.853985865244297,1.1990591829380215,307.3170731707317,67.777863247510595,1.3577987856951772,null,null,null,null,null,null,null,null,null,null,50,0,210,0.41,1,26,45,18,70,0.5,0.5,100,0.4,16,20.3,null,7,null,46,null,210,0.56000000000000005,2,26,45,19,67,0.46,0.46,100,0.4,16,20,0,5,null,50,null,210,0.41,1,26,45,18,70,0.5,0.5,100,0.4,16,20.3,0,7,null,53.000000000000007,null,210,0.33,1,26,45,18,72,0.53,0.53,100,0.4,16,20.5,0,8,null,55.000000000000007,null,210,0.28000000000000003,1,26,45,18,73,0.55000000000000004,0.55000000000000004,100,0.4,16,20.7,0,9]
[null,220,51.302712055623573,1,158.29268292682926,38.765303166288135,0.75561898412422934,220,51.302712055623573,1,273.65853658536588,61.363691786625395,1.1961100949223402,321.95121951219511,69.311998796993251,1.3510396628124377,null,null,null,null,null,null,null,null,null,null,51.000000000000007,0,220,0.43,1,26,45,18,70,0.51,0.51,100,0.4,16,20.399999999999999,null,7,null,47,null,220,0.59,3,26,45,19,67,0.47,0.47,100,0.4,16,20,0,5,null,51.000000000000007,null,220,0.43,1,26,45,18,70,0.51,0.51,100,0.4,16,20.399999999999999,0,7,null,54.000000000000007,null,220,0.34,1,26,45,18,71,0.54,0.54,100,0.4,16,20.7,0,8,null,56.000000000000007,null,220,0.28999999999999998,1,26,45,18,72,0.56000000000000005,0.56000000000000005,100,0.4,16,20.8,0,9]
[null,230,52.625815284956424,1,165.48780487804876,39.865053182781729,0.75751896606108304,230,52.625815284956424,1,286.09756097560978,62.789761853991038,1.1931361350698175,336.58536585365852,70.745290612006897,1.344307736211549,null,null,null,null,null,null,null,null,null,null,53.000000000000007,0,230,0.45,2,26,45,18,69,0.53,0.53,100,0.4,16,20.5,null,7,null,48,null,230,0.62,3,26,45,19,66,0.48,0.48,100,0.4,16,20.100000000000001,0,5,null,53.000000000000007,null,230,0.45,2,26,45,18,69,0.53,0.53,100,0.4,16,20.5,0,7,null,56.000000000000007,null,230,0.36,1,26,45,18,71,0.56000000000000005,0.56000000000000005,100,0.4,16,20.8,0,8,null,57.999999999999993,null,230,0.3,1,26,45,18,72,0.57999999999999996,0.57999999999999996,100,0.4,16,21,0,9]
[null,240,53.889816538714911,1,172.6829268292683,40.924950426263351,0.75941899703559979,240,53.889816538714911,1,298.53658536585368,64.137065826684307,1.1901518681290684,351.21951219512192,72.085413947485719,1.3376444489414607,null,null,null,null,null,null,null,null,null,null,54.000000000000007,0,240,0.46,2,26,45,19,68,0.54,0.54,100,0.4,16,20.6,null,7,null,49,null,240,0.65,3,26,45,19,66,0.49,0.49,100,0.4,16,20.2,0,5,null,54.000000000000007,null,240,0.46,2,26,45,19,68,0.54,0.54,100,0.4,16,20.6,0,7,null,56.999999999999993,null,240,0.37,1,26,45,18,70,0.56999999999999995,0.56999999999999995,100,0.4,16,20.9,0,8,null,59,null,240,0.32,1,26,45,18,71,0.59,0.59,100,0.4,16,21.1,0,9]
[null,250,55.097664640052301,1,179.8780487804878,41.946740168153532,0.76131611824543777,250,55.097664640052301,1,310.97560975609758,65.410364582894346,1.1871712714180158,365.85365853658539,73.339836334536614,1.3310879292917159,null,null,null,null,null,null,null,null,null,null,55.000000000000007,0,250,0.48,2,26,45,19,68,0.55000000000000004,0.55000000000000004,100,0.4,16,20.7,null,7,null,50,null,250,0.67,3,26,45,19,65,0.5,0.5,100,0.4,16,20.3,0,5,null,55.000000000000007,null,250,0.48,2,26,45,19,68,0.55000000000000004,0.55000000000000004,100,0.4,16,20.7,0,7,null,57.999999999999993,null,250,0.39,1,26,45,18,69,0.57999999999999996,0.57999999999999996,100,0.4,16,21,0,8,null,61,null,250,0.33,1,26,45,18,71,0.61,0.61,100,0.4,16,21.2,0,9]
[null,260,56.252208314573963,1,187.07317073170731,42.93210153800996,0.76320739797315662,260,56.252208314573963,1,323.41463414634148,66.614296657742614,1.1842076720832311,380.48780487804879,74.51577127474053,1.3246728174302589,null,null,null,null,null,null,null,null,null,null,56.000000000000007,0,260,0.5,2,26,45,19,67,0.56000000000000005,0.56000000000000005,100,0.4,16,20.8,null,6,null,51.000000000000007,null,260,0.7,4,26,45,19,65,0.51,0.51,100,0.4,16,20.399999999999999,0,5,null,56.000000000000007,null,260,0.5,2,26,45,19,67,0.56000000000000005,0.56000000000000005,100,0.4,16,20.8,0,6,null,60,null,260,0.4,1,26,45,19,69,0.6,0.6,100,0.4,16,21.1,0,8,null,62,null,260,0.34,1,26,45,18,70,0.62,0.62,100,0.4,16,21.3,0,9]
[null,270,57.356196647501093,0.99999999999999989,194.26829268292681,43.882649234444621,0.76508994318674906,270,57.356196647501093,0.99999999999999989,335.85365853658539,67.753365805580756,1.1812736855963173,395.1219512195122,75.620136598546765,1.3184301090131887,null,null,null,null,null,null,null,null,null,null,56.999999999999993,0,270,0.52,2,26,45,19,67,0.56999999999999995,0.56999999999999995,100,0.4,16,20.9,null,6,null,52.000000000000007,null,270,0.73,4,26,45,20,64,0.52,0.52,100,0.4,16,20.5,0,5,null,56.999999999999993,null,270,0.52,2,26,45,19,67,0.56999999999999995,0.56999999999999995,100,0.4,16,20.9,0,6,null,61,null,270,0.42,1,26,45,19,68,0.61,0.61,100,0.4,16,21.2,0,8,null,63,null,270,0.36,1,26,45,18,70,0.63,0.63,100,0.4,16,21.4,0,9]
[null,280,58.412279618815198,0.99999999999999989,201.46341463414635,44.799935214476939,0.76696091141846845,280,58.412279618815198,0.99999999999999989,348.29268292682929,68.831929586500067,1.178381156080212,409.7560975609756,76.659517487759672,1.3123870184149917,null,null,null,null,null,null,null,null,null,null,57.999999999999993,0,280,0.54,2,26,45,19,66,0.57999999999999996,0.57999999999999996,100,0.4,16,21,null,6,null,53.000000000000007,null,280,0.75,4,26,45,20,64,0.53,0.53,100,0.4,16,20.6,0,5,null,57.999999999999993,null,280,0.54,2,26,45,19,66,0.57999999999999996,0.57999999999999996,100,0.4,16,21,0,6,null,62,null,280,0.44,2,26,45,19,68,0.62,0.62,100,0.4,16,21.3,0,8,null,64,null,280,0.37,1,26,45,18,69,0.64,0.64,100,0.4,16,21.5,0,9]
[null,290,59.423008716383272,0.99999999999999989,208.65853658536585,45.6854503613228,0.76881752284493554,290,59.423008716383272,0.99999999999999989,360.73170731707319,69.854188977052459,1.1755410990792401,424.39024390243901,77.640134162118215,1.3065668642374275,null,null,null,null,null,null,null,null,null,null,59,0,290,0.56000000000000005,2,26,45,19,66,0.59,0.59,100,0.4,16,21.1,null,6,null,54.000000000000007,null,290,0.78,5,26,45,20,63,0.54,0.54,100,0.4,16,20.6,0,5,null,59,null,290,0.56000000000000005,2,26,45,19,66,0.59,0.59,100,0.4,16,21.1,0,6,null,63,null,290,0.45,2,26,45,19,67,0.63,0.63,100,0.4,16,21.4,0,8,null,66,null,290,0.38,1,26,45,19,68,0.66,0.66,100,0.4,16,21.6,0,9]
[null,300,60.390837627063767,1,215.85365853658536,46.540626130619565,0.77065707248549042,300,60.390837627063767,1,373.17073170731709,70.824179005182998,1.1727636474020953,439.02439024390242,78.567814229968235,1.3009889797381875,null,null,null,null,null,null,null,null,null,null,60,0,300,0.57999999999999996,3,26,45,19,65,0.6,0.6,100,0.4,16,21.2,null,6,null,55.000000000000007,null,300,0.81,5,26,45,20,63,0.55000000000000004,0.55000000000000004,100,0.4,16,20.7,0,5,null,60,null,300,0.57999999999999996,3,26,45,19,65,0.6,0.6,100,0.4,16,21.2,0,6,null,64,null,300,0.47,2,26,45,19,67,0.64,0.64,100,0.4,16,21.5,0,8,null,67,null,300,0.4,1,26,45,19,68,0.67,0.67,100,0.4,16,21.7,0,9]
[null,310,61.318123005793282,1,223.04878048780486,47.366836175086931,0.77247694243040921,310,61.318123005793282,1,385.60975609756099,71.745760409374085,1.1700580006761723,453.65853658536582,79.447969703027383,1.2956686507759085,null,null,null,null,null,null,null,null,null,null,{"$f":"IF($AA$13=$AS$13,AS48,IF($AA$13=$BK$13,BK48,IF($AA$13=$CC$13,CC48,IF($AA$13=$CU$13,CU48,\"-\"))))","v":61},0,310,0.6,3,26,45,19,65,0.61,0.61,100,0.4,16,21.3,null,6,null,55.000000000000007,null,310,0.83,5,26,45,20,62,0.55000000000000004,0.55000000000000004,100,0.4,16,20.8,0,5,null,61,null,310,0.6,3,26,45,19,65,0.61,0.61,100,0.4,16,21.3,0,6,null,65,null,310,0.48,2,26,45,19,66,0.65,0.65,100,0.4,16,21.6,0,8,null,68,null,310,0.41,1,26,45,19,67,0.68,0.68,100,0.4,16,21.8,0,9]
[null,320,62.207125322654029,1,230.2439024390244,48.165397947623887,0.77427461400604947,320,62.207125322654029,1,398.04878048780489,72.622612322000961,1.1674323792543733,468.29268292682923,80.285578675242874,1.2906170837957882,null,null,null,null,null,null,null,null,null,null,62,0,320,0.62,3,26,45,20,64,0.62,0.62,100,0.4,16,21.4,null,6,null,56.000000000000007,null,320,0.86,5,26,45,20,62,0.56000000000000005,0.56000000000000005,100,0.4,16,20.8,0,5,null,62,null,320,0.62,3,26,45,20,64,0.62,0.62,100,0.4,16,21.4,0,6,null,66,null,320,0.5,2,26,45,19,66,0.66,0.66,100,0.4,16,21.7,0,8,null,68.999999999999986,null,320,0.42,1,26,45,19,67,0.69,0.69,100,0.4,16,21.9,0,9]
[null,330,63.060009787922077,0.99999999999999989,237.4390243902439,48.937574282841361,0.77604767978032252,330,63.060009787922077,0.99999999999999989,410.48780487804879,73.458225976899087,1.1648939831114422,482.92682926829269,81.085171665741797,1.2858414062801506,null,null,null,null,null,null,null,null,null,null,63,0,330,0.64,3,26,45,20,64,0.63,0.63,100,0.4,16,21.4,null,6,null,56.999999999999993,null,330,0.89,6,26,45,20,62,0.56999999999999995,0.56999999999999995,100,0.4,16,20.9,0,5,null,63,null,330,0.64,3,26,45,20,64,0.63,0.63,100,0.4,16,21.4,0,6,null,67,null,330,0.51,2,26,45,19,65,0.67,0.67,100,0.4,16,21.8,0,8,null,69.999999999999986,null,330,0.44,2,26,45,19,67,0.7,0.7,100,0.4,16,22,0,9]
[null,340,63.878847355096234,1,244.63414634146341,49.684574957031046,0.77779385530924461,340,63.878847355096234,1,422.92682926829269,74.255899441142802,1.1624489563557958,497.5609756097561,81.850822625874216,1.2813447019617235,null,null,null,null,null,null,null,null,null,null,64,0,340,0.66,3,26,45,20,63,0.64,0.64,100,0.4,16,21.5,null,6,null,57.999999999999993,null,340,0.91,6,26,45,20,61,0.57999999999999996,0.57999999999999996,100,0.4,16,21,0,5,null,64,null,340,0.66,3,26,45,20,63,0.64,0.64,100,0.4,16,21.5,0,6,null,68,null,340,0.53,2,26,45,19,65,0.68,0.68,100,0.4,16,21.8,0,8,null,71,null,340,0.45,2,26,45,19,66,0.71,0.71,100,0.4,16,22.1,0,9]
[null,350,64.665615801907805,1,251.82926829268291,50.407558226570018,0.77951099052369743,350,64.665615801907805,1,435.36585365853659,75.01873337103568,1.1601023579647474,512.19512195121945,82.586144610348938,1.2771260829454969,null,null,null,null,null,null,null,null,null,null,65,0,350,0.68,3,26,45,20,63,0.65,0.65,100,0.4,16,21.6,null,6,null,57.999999999999993,null,350,0.94,6,26,45,20,61,0.57999999999999996,0.57999999999999996,100,0.4,16,21,0,5,null,65,null,350,0.68,3,26,45,20,63,0.65,0.65,100,0.4,16,21.6,0,6,null,68.999999999999986,null,350,0.54,2,26,45,20,65,0.69,0.69,100,0.4,16,21.9,0,8,null,72,null,350,0.46,2,26,45,19,66,0.72,0.72,100,0.4,16,22.2,0,9]
[null,360,65.422200889311029,1,259.02439024390242,51.107632344761321,0.78119708065510085,360,65.422200889311029,1,447.80487804878049,75.749627792312452,1.1578581393260459,526.82926829268297,83.294290112462178,1.2731808007099799,null,null,null,null,null,null,null,null,null,null,65,0,360,0.7,4,26,45,20,63,0.65,0.65,100,0.4,16,21.6,null,6,null,59,null,360,0.97,7,26,45,21,61,0.59,0.59,100,0.4,16,21.1,0,5,null,65,null,360,0.7,4,26,45,20,63,0.65,0.65,100,0.4,16,21.6,0,6,null,69.999999999999986,null,360,0.56000000000000005,2,26,45,20,64,0.7,0.7,100,0.4,16,22,0,8,null,73,null,360,0.48,2,26,45,19,65,0.73,0.73,100,0.4,16,22.2,0,9]
[null,370,66.150397598454248,1,266.21951219512192,51.785857057110519,0.78285027659940498,370,66.150397598454248,1,460.2439024390244,76.451279904552393,1.1557191291370084,541.46341463414637,83.977956063418617,1.2695003977630053,null,null,null,null,null,null,null,null,null,null,66,0,370,0.72,4,26,45,20,62,0.66,0.66,100,0.4,16,21.7,null,6,null,60,null,370,1,7,26,45,21,60,0.6,0.6,100,0.4,16,21.1,0,5,null,66,null,370,0.72,4,26,45,20,62,0.66,0.66,100,0.4,16,21.7,0,6,null,69.999999999999986,null,370,0.57999999999999996,3,26,45,20,64,0.7,0.7,100,0.4,16,22.1,0,8,null,73,null,370,0.49,2,26,45,19,65,0.73,0.73,100,0.4,16,22.3,0,9]
[null,380,66.851911445631956,1,273.41463414634143,52.443245075038099,0.78446889462073399,380,66.851911445631956,1,472.6829268292683,77.126182909804328,1.1536870261746821,556.09756097560978,84.639393495745409,1.2660729015142569,null,null,null,null,null,null,null,null,null,null,67,0,380,0.74,4,26,45,20,62,0.67,0.67,100,0.4,16,21.8,null,6,null,60,null,380,1.02,7,26,45,21,60,0.6,0.6,100,0.4,16,21.2,0,5,null,67,null,380,0.74,4,26,45,20,62,0.67,0.67,100,0.4,16,21.8,0,6,null,71,null,380,0.59,3,26,45,20,63,0.71,0.71,100,0.4,16,22.1,0,8,null,74,null,380,0.5,2,26,45,20,64,0.74,0.74,100,0.4,16,22.4,0,9]
[null,390,67.528359875217404,1,280.60975609756099,53.08076352802793,0.78605142529914052,390,67.528359875217404,1,485.1219512195122,77.776625865423185,1.1517624004069267,570.73170731707319,85.280421870798847,1.2628830617000719,null,null,null,null,null,null,null,null,null,null,68,0,390,0.75,4,26,45,20,62,0.68,0.68,100,0.4,16,21.8,null,6,null,61,null,390,1.05,8,26,45,21,60,0.61,0.61,100,0.4,16,21.2,0,5,null,68,null,390,0.75,4,26,45,20,62,0.68,0.68,100,0.4,16,21.8,0,6,null,72,null,390,0.61,3,26,45,20,63,0.72,0.72,100,0.4,16,22.2,0,8,null,75,null,390,0.52,2,26,45,20,64,0.75,0.75,100,0.4,16,22.5,0,9]
[null,400,68.181273730576038,1,287.80487804878049,53.699335394211538,0.78759654163119508,400,68.181273730576038,1,497.5609756097561,78.404694561118134,1.1499447028657868,585.36585365853659,85.90244807036359,1.2599126324599661,null,null,null,null,null,null,null,null,null,null,68,0,400,0.77,4,26,45,20,61,0.68,0.68,100,0.4,16,21.9,null,6,null,61,null,400,1.08,8,26,45,21,59,0.61,0.61,100,0.4,16,21.3,0,5,null,68,null,400,0.77,4,26,45,20,61,0.68,0.68,100,0.4,16,21.9,0,6,null,73,null,400,0.62,3,26,45,20,63,0.73,0.73,100,0.4,16,22.3,0,8,null,76,null,400,0.53,2,26,45,20,64,0.76,0.76,100,0.4,16,22.5,0,9]
[null,410,68.812098802959838,1,295,54.299840909388394,0.78910310619755109,410,68.812098802959838,1,510,79.012273420212225,1.148232284651862,600,86.506490052345072,1.2571406999233126,null,null,null,null,null,null,null,null,null,null,68.999999999999986,0,410,0.79,5,26,45,20,61,0.69,0.69,100,0.4,16,21.9,null,6,null,62,null,410,1.1000000000000001,9,26,45,21,59,0.62,0.62,100,0.4,16,21.3,0,5,null,68.999999999999986,null,410,0.79,5,26,45,20,61,0.69,0.69,100,0.4,16,21.9,0,6,null,73,null,410,0.64,3,26,45,20,62,0.73,0.73,100,0.4,16,22.3,0,8,null,76,null,410,0.54,2,26,45,20,63,0.76,0.76,100,0.4,16,22.6,0,9]
[null,420,69.422197458382144,1,302.19512195121951,54.883118954482129,0.79057017731805401,420,69.422197458382144,1,522.43902439024384,79.601048425113589,1.146622425382509,614.63414634146341,87.093205170553802,1.2545440559233989,null,null,null,null,null,null,null,null,null,null,68.999999999999986,0,420,0.81,5,26,45,20,61,0.69,0.69,100,0.4,16,22,null,6,null,63,null,420,1.1299999999999999,9,26,45,21,59,0.63,0.63,100,0.4,16,21.4,0,5,null,68.999999999999986,null,420,0.81,5,26,45,20,61,0.69,0.69,100,0.4,16,22,0,6,null,74,null,420,0.65,3,26,45,20,62,0.74,0.74,100,0.4,16,22.4,0,8,null,77,null,420,0.56000000000000005,2,26,45,20,63,0.77,0.77,100,0.4,16,22.6,0,9]
[null,430,70.012850342473314,1,309.39024390243901,55.449968421432644,0.79199701412233325,430,70.012850342473314,1,534.8780487804878,80.172511066998268,1.145111371338664,629.26829268292681,87.662923158583396,1.2520976182197037,null,null,null,null,null,null,null,null,null,null,69.999999999999986,0,430,0.83,5,26,45,21,60,0.7,0.7,100,0.4,16,22,null,6,null,63,null,430,1.1599999999999999,9,26,45,21,59,0.63,0.63,100,0.4,16,21.4,0,5,null,69.999999999999986,null,430,0.83,5,26,45,21,60,0.7,0.7,100,0.4,16,22,0,6,null,75,null,430,0.67,3,26,45,20,62,0.75,0.75,100,0.4,16,22.4,0,8,null,78,null,430,0.56999999999999995,3,26,45,20,63,0.78,0.78,100,0.4,16,22.7,0,9]
[null,440,70.585258163317377,1,316.58536585365852,56.001149557524087,0.79338308047199946,440,70.585258163317377,1,547.31707317073176,80.727963319704443,1.1436943835059621,643.90243902439022,88.215683777780072,1.24977489738254,null,null,null,null,null,null,null,null,null,null,71,0,440,0.85,5,26,45,21,60,0.71,0.71,100,0.4,16,22.1,null,6,null,64,null,440,1.18,10,26,45,21,58,0.64,0.64,100,0.4,16,21.5,0,5,null,71,null,440,0.85,5,26,45,21,60,0.71,0.71,100,0.4,16,22.1,0,6,null,75,null,440,0.68,4,26,45,20,61,0.75,0.75,100,0.4,16,22.5,0,8,null,79,null,440,0.57999999999999996,3,26,45,20,62,0.79,0.79,100,0.4,16,22.8,0,9]
[null,450,71.140543552268937,0.99999999999999989,323.78048780487802,56.537385288149068,0.79472804767944283,450,71.140543552268937,0.99999999999999989,559.7560975609756,81.268523637838484,1.1423657956468696,658.53658536585363,88.751279129306312,1.2475485102823016,null,null,null,null,null,null,null,null,null,null,71,0,450,0.87,6,26,45,21,60,0.71,0.71,100,0.4,16,22.1,null,6,null,64,null,450,1.21,10,26,45,21,58,0.64,0.64,100,0.4,16,21.5,0,5,null,71,null,450,0.87,6,26,45,21,60,0.71,0.71,100,0.4,16,22.1,0,6,null,76,null,450,0.7,4,26,45,20,61,0.76,0.76,100,0.4,16,22.5,0,8,null,79,null,450,0.6,3,26,45,20,62,0.79,0.79,100,0.4,16,22.8,0,9]
[null,460,71.679753002751454,1,330.97560975609753,57.059362518008413,0.79603179597756379,460,71.679753002751454,1,572.19512195121956,81.79513397909227,1.1411190824827833,673.17073170731703,89.26930063029593,1.2453907399327853,null,null,null,null,null,null,null,null,null,null,72,0,460,0.89,6,26,45,21,60,0.72,0.72,100,0.4,16,22.2,null,6,null,65,null,460,1.24,11,26,45,21,58,0.65,0.65,100,0.4,16,21.6,0,5,null,72,null,460,0.89,6,26,45,21,60,0.72,0.72,100,0.4,16,22.2,0,6,null,76,null,460,0.72,4,26,45,20,61,0.76,0.76,100,0.4,16,22.6,0,8,null,80,null,460,0.61,3,26,45,20,62,0.8,0.8,100,0.4,16,22.9,0,9]
[null,470,72.203858887035651,1,338.17073170731709,57.567733410747067,0.79729441470452311,470,72.203858887035651,1,584.63414634146341,82.308567850772164,1.1399469380098579,687.80487804878044,89.769190654103028,1.2432741412692179,null,null,null,null,null,null,null,null,null,null,72,0,470,0.91,6,26,45,21,59,0.72,0.72,100,0.4,16,22.2,null,6,null,65,null,470,1.26,11,26,45,21,58,0.65,0.65,100,0.4,16,21.6,0,5,null,72,null,470,0.91,6,26,45,21,59,0.72,0.72,100,0.4,16,22.2,0,6,null,77,null,470,0.73,4,26,45,21,61,0.77,0.77,100,0.4,16,22.6,0,8,null,80,null,470,0.62,3,26,45,20,61,0.8,0.8,100,0.4,16,22.9,0,9]
[null,480,72.713761550999081,1,345.36585365853659,58.063116647025964,0.79851620117743982,480,72.713761550999081,1,597.07317073170736,82.809439380539715,1.1388413639206363,702.43902439024384,90.250298834641967,1.2411721923001238,null,null,null,null,null,null,null,null,null,null,{"$f":"IF($AA$13=$AS$13,AS65,IF($AA$13=$BK$13,BK65,IF($AA$13=$CC$13,CC65,IF($AA$13=$CU$13,CU65,\"-\"))))","v":73},0,480,0.93,6,26,45,21,59,0.73,0.73,100,0.4,16,22.3,null,6,null,66,null,480,1.29,12,26,45,21,57,0.66,0.66,100,0.4,16,21.6,0,5,null,73,null,480,0.93,6,26,45,21,59,0.73,0.73,100,0.4,16,22.3,0,6,null,78,null,480,0.75,4,26,45,21,60,0.78,0.78,100,0.4,16,22.7,0,8,null,81,null,480,0.63,3,26,45,20,61,0.81,0.81,100,0.4,16,23,0,9]
[null,490,73.210291486866467,1,352.5609756097561,58.546098661029717,0.79969765823883621,490,73.210291486866467,1,609.51219512195121,83.298213411363633,1.1377937680565975,717.07317073170725,90.71194303482244,1.2390599899618715,null,null,null,null,null,null,null,null,null,null,73,0,490,0.95,6,26,45,21,59,0.73,0.73,100,0.4,16,22.3,null,6,null,66,null,490,1.32,12,26,45,21,57,0.66,0.66,100,0.4,16,21.7,0,5,null,73,null,490,0.95,6,26,45,21,59,0.73,0.73,100,0.4,16,22.3,0,6,null,78,null,490,0.76,4,26,45,21,60,0.78,0.78,100,0.4,16,22.7,0,8,null,81.999999999999986,null,490,0.65,3,26,45,20,61,0.82,0.82,100,0.4,16,23,0,9]
[null,500,73.694211583930269,0.99999999999999989,359.7560975609756,59.017234855410237,0.80083949046928282,500,73.694211583930269,0.99999999999999989,621.95121951219517,83.77521662068358,1.1367950727754521,731.70731707317077,91.153474979074957,1.2369149899278093,null,null,null,null,null,null,null,null,null,null,74,0,500,0.97,7,26,45,21,59,0.74,0.74,100,0.4,16,22.4,null,6,null,66,null,500,1.35,12,26,45,21,57,0.66,0.66,100,0.4,16,21.7,0,5,null,74,null,500,0.97,7,26,45,21,59,0.74,0.74,100,0.4,16,22.4,0,6,null,79,null,500,0.78,5,26,45,21,60,0.79,0.79,100,0.4,16,22.8,0,8,null,81.999999999999986,null,500,0.66,3,26,45,21,61,0.82,0.82,100,0.4,16,23.1,0,9]
[null,510,74.166219457252794,0.99999999999999989,366.95121951219511,59.477050794666468,0.80194259906893695,510,74.166219457252794,0.99999999999999989,634.39024390243901,84.240649663785206,1.1358358330821892,746.34146341463418,91.574350549970234,1.2347177895827759,null,null,null,null,null,null,null,null,null,null,74,0,510,0.99,7,26,45,21,59,0.74,0.74,100,0.4,16,22.4,null,6,null,67,null,510,1.37,13,26,45,22,57,0.67,0.67,100,0.4,16,21.8,0,5,null,74,null,510,0.99,7,26,45,21,59,0.74,0.74,100,0.4,16,22.4,0,6,null,79,null,510,0.79,5,26,45,21,60,0.79,0.79,100,0.4,16,22.8,0,8,null,82.999999999999986,null,510,0.67,3,26,45,21,60,0.83,0.83,100,0.4,16,23.1,0,9]
[null,520,74.626949854348425,1,374.14634146341461,59.926043376959925,0.80300807541939356,520,74.626949854348425,1,646.82926829268297,84.694600341387201,1.1349063643454287,760.97560975609758,91.974204748931527,1.2324529533692619,null,null,null,null,null,null,null,null,null,null,75,0,520,1.01,7,26,45,21,58,0.75,0.75,100,0.4,16,22.4,null,6,null,67,null,520,1.4,13,26,45,22,57,0.67,0.67,100,0.4,16,21.8,0,5,null,75,null,520,1.01,7,26,45,21,58,0.75,0.75,100,0.4,16,22.4,0,6,null,80,null,520,0.81,5,26,45,21,59,0.8,0.8,100,0.4,16,22.9,0,8,null,82.999999999999986,null,520,0.69,4,26,45,21,60,0.83,0.83,100,0.4,16,23.2,0,9]
[null,530,75.076977139846761,1,381.34146341463412,60.364681984365888,0.80403719334522339,530,75.076977139846761,1,659.26829268292681,85.137057791439361,1.1339968794009057,775.60975609756099,92.35293132103871,1.2301098797439838,null,null,null,null,null,null,null,null,null,null,75,0,530,1.03,8,26,45,21,58,0.75,0.75,100,0.4,16,22.5,null,6,null,68,null,530,1.43,14,26,45,22,57,0.68,0.68,100,0.4,16,21.8,0,5,null,75,null,530,1.03,8,26,45,21,58,0.75,0.75,100,0.4,16,22.5,0,6,null,80,null,530,0.82,5,26,45,21,59,0.8,0.8,100,0.4,16,22.9,0,8,null,83.999999999999986,null,530,0.7,4,26,45,21,60,0.84,0.84,100,0.4,16,23.2,0,9]
[null,540,75.516817858136676,1,388.53658536585363,60.793409611561287,0.80503140010170604,540,75.516817858136676,1,671.70731707317077,85.567927705132632,1.1330976348325168,790.2439024390244,92.710767043925756,1.2276837090525854,null,null,null,null,null,null,null,null,null,null,76,0,540,1.05,8,26,45,21,58,0.76,0.76,100,0.4,16,22.5,null,6,null,68,null,540,1.45,14,26,45,22,56,0.68,0.68,100,0.4,16,21.9,0,5,null,76,null,540,1.05,8,26,45,21,58,0.76,0.76,100,0.4,16,22.5,0,6,null,80,null,540,0.84,5,26,45,21,59,0.8,0.8,100,0.4,16,22.9,0,8,null,83.999999999999986,null,540,0.71,4,26,45,21,60,0.84,0.84,100,0.4,16,23.2,0,9]
[null,550,75.946933373991044,1,395.73170731707313,61.212643972947632,0.80599230612135087,550,75.946933373991044,1,684.14634146341461,85.98704856712061,1.1321990862183768,804.8780487804878,93.048380680770663,1.2251762717339185,null,null,null,null,null,null,null,null,null,null,76,0,550,1.06,8,26,45,21,58,0.76,0.76,100,0.4,16,22.6,null,6,null,68,null,550,1.48,15,26,45,22,56,0.68,0.68,100,0.4,16,21.9,0,5,null,76,null,550,1.06,8,26,45,21,58,0.76,0.76,100,0.4,16,22.6,0,6,null,81,null,550,0.86,5,26,45,21,59,0.81,0.81,100,0.4,16,23,0,8,null,84.999999999999986,null,550,0.73,4,26,45,21,59,0.85,0.85,100,0.4,16,23.3,0,9]
[null,560,76.367732591172086,1,402.92682926829269,61.622778588210537,0.80692167355684952,560,76.367732591172086,1,696.58536585365857,86.394208919952405,1.1312920521348484,819.51219512195121,93.366966597378962,1.2225970764015055,null,null,null,null,null,null,null,null,null,null,76,0,560,1.08,8,26,45,21,57,0.76,0.76,100,0.4,16,22.6,null,6,null,68.999999999999986,null,560,1.51,15,26,45,22,56,0.69,0.69,100,0.4,16,21.9,0,5,null,76,null,560,1.08,8,26,45,21,57,0.76,0.76,100,0.4,16,22.6,0,6,null,81,null,560,0.87,6,26,45,21,58,0.81,0.81,100,0.4,16,23,0,8,null,84.999999999999986,null,560,0.74,4,26,45,21,59,0.85,0.85,100,0.4,16,23.3,0,9]
[null,570,76.779574749017598,1,410.1219512195122,62.02418384631487,0.80782140366189614,570,76.779574749017598,1,709.02439024390242,86.789165652717287,1.1303678867253399,834.14634146341461,93.668343043357481,1.2199643375148543,null,null,null,null,null,null,null,null,null,null,77,0,570,1.1000000000000001,9,26,45,21,57,0.77,0.77,100,0.4,16,22.6,null,6,null,68.999999999999986,null,570,1.53,16,26,45,22,56,0.69,0.69,100,0.4,16,22,0,5,null,77,null,570,1.1000000000000001,9,26,45,21,57,0.77,0.77,100,0.4,16,22.6,0,6,null,81.999999999999986,null,570,0.89,6,26,45,21,58,0.82,0.82,100,0.4,16,23.1,0,8,null,84.999999999999986,null,570,0.75,4,26,45,21,59,0.85,0.85,100,0.4,16,23.4,0,9]
[null,580,77.182772297007745,0.99999999999999989,417.3170731707317,62.417208047935773,0.80869352305392106,580,77.182772297007745,0.99999999999999989,721.46341463414637,87.171663313900751,1.1294186606624423,848.78048780487802,93.955055097383877,1.2173060425432058,null,null,null,null,null,null,null,null,null,null,77,0,580,1.1200000000000001,9,26,45,21,57,0.77,0.77,100,0.4,16,22.7,null,6,null,69.999999999999986,null,580,1.56,16,26,45,22,56,0.7,0.7,100,0.4,16,22,0,5,null,77,null,580,1.1200000000000001,9,26,45,21,57,0.77,0.77,100,0.4,16,22.7,0,6,null,81.999999999999986,null,580,0.9,6,26,45,21,58,0.82,0.82,100,0.4,16,23.1,0,8,null,86,null,580,0.77,4,26,45,21,59,0.86,0.86,100,0.4,16,23.4,0,9]
[null,590,77.577593847313153,1,424.51219512195121,62.802178426326009,0.80954016890407998,590,77.577593847313153,1,733.90243902439022,87.541454448452328,1.1284373503611089,863.41463414634143,94.230482276567614,1.2146610587334068,null,null,null,null,null,null,null,null,null,null,78,0,590,1.1399999999999999,9,26,45,21,57,0.78,0.78,100,0.4,16,22.7,null,6,null,69.999999999999986,null,590,1.59,17,26,45,22,56,0.7,0.7,100,0.4,16,22,0,5,null,78,null,590,1.1399999999999999,9,26,45,21,57,0.78,0.78,100,0.4,16,22.7,0,6,null,82.999999999999986,null,590,0.92,6,26,45,21,58,0.83,0.83,100,0.4,16,23.1,0,8,null,86,null,590,0.78,5,26,45,21,58,0.86,0.86,100,0.4,16,23.4,0,9]
[null,600,77.964267205322841,1,431.70731707317071,63.179402146618798,0.81036357309987472,600,77.964267205322841,1,746.34146341463418,87.898320959064648,1.1274180353363674,878.04878048780483,94.498950809902738,1.2120802798163288,null,null,null,null,null,null,null,null,null,null,78,0,600,1.1599999999999999,9,26,45,22,57,0.78,0.78,100,0.4,16,22.7,null,6,null,69.999999999999986,null,600,1.61,17,26,45,22,55,0.7,0.7,100,0.4,16,22,0,5,null,78,null,600,1.1599999999999999,9,26,45,22,57,0.78,0.78,100,0.4,16,22.7,0,6,null,82.999999999999986,null,600,0.93,6,26,45,21,58,0.83,0.83,100,0.4,16,23.2,0,8,null,87,null,600,0.79,5,26,45,21,58,0.87,0.87,100,0.4,16,23.5,0,9]
[null,610,78.342982478153715,1,438.90243902439022,63.549167283566703,0.81116604542452375,610,78.342982478153715,1,758.78048780487802,88.242096491664256,1.126356103640437,892.68292682926824,94.765850575813943,1.2096278132153038,null,null,null,null,null,null,null,null,null,null,78,0,610,1.18,10,26,45,22,57,0.78,0.78,100,0.4,16,22.8,null,{"$f":"IF($AA$13=$AS$13,BI78,IF($AA$13=$BK$13,CA78,IF($AA$13=$CC$13,CS78,IF($AA$13=$CU$13,DK78,\"-\"))))","v":6},null,71,null,610,1.64,18,26,45,22,55,0.71,0.71,100,0.4,16,22.1,0,5,null,78,null,610,1.18,10,26,45,22,57,0.78,0.78,100,0.4,16,22.8,0,6,null,82.999999999999986,null,610,0.95,7,26,45,21,58,0.83,0.83,100,0.4,16,23.2,0,8,null,87,null,610,0.81,5,26,45,21,58,0.87,0.87,100,0.4,16,23.5,0,9]
[null,620,78.713895261140635,1,446.09756097560972,63.911743777716737,0.81194995579476292,620,78.713895261140635,1,771.21951219512198,88.572689845114184,1.1252484653601005,907.31707317073165,95.037756703796902,1.207382208547809,null,null,null,null,null,null,null,null,null,null,79,0,620,1.2,10,26,45,22,56,0.79,0.79,100,0.4,16,22.8,null,6,null,71,null,620,1.67,18,26,45,22,55,0.71,0.71,100,0.4,16,22.1,0,5,null,79,null,620,1.2,10,26,45,22,56,0.79,0.79,100,0.4,16,22.8,0,6,null,83.999999999999986,null,620,0.96,7,26,45,21,57,0.84,0.84,100,0.4,16,23.2,0,8,null,87,null,620,0.82,5,26,45,21,58,0.87,0.87,100,0.4,16,23.5,0,9]
[null,630,79.077129902306609,1,453.29268292682923,64.267384370021205,0.81271771559512029,630,79.077129902306609,1,783.65853658536582,88.890109405127475,1.1240937742042991,921.95121951219505,95.322555840148937,1.2054377284293478,null,null,null,null,null,null,null,null,null,null,79,0,630,1.22,10,26,45,22,56,0.79,0.79,100,0.4,16,22.8,null,6,null,71,null,630,1.69,19,26,45,22,55,0.71,0.71,100,0.4,16,22.1,0,5,null,79,null,630,1.22,10,26,45,22,56,0.79,0.79,100,0.4,16,22.8,0,6,null,83.999999999999986,null,630,0.98,7,26,45,21,57,0.84,0.84,100,0.4,16,23.3,0,8,null,88,null,630,0.83,5,26,45,21,58,0.88,0.88,100,0.4,16,23.6,0,9]
[null,640,79.43278284481471,1,460.48780487804879,64.616325514883954,0.81347175814201056,640,79.43278284481471,1,796.09756097560978,89.194488602392738,1.1228926572627975,936.58536585365846,95.629577077792817,1.2039056627868783,null,null,null,null,null,null,null,null,null,null,79,0,640,1.24,11,26,45,22,56,0.79,0.79,100,0.4,16,22.8,null,6,null,72,null,640,1.72,20,26,45,22,55,0.72,0.72,100,0.4,16,22.2,0,5,null,79,null,640,1.24,11,26,45,22,56,0.79,0.79,100,0.4,16,22.8,0,6,null,84.999999999999986,null,640,1,7,26,45,21,57,0.85,0.85,100,0.4,16,23.3,0,8,null,88,null,640,0.85,5,26,45,21,58,0.88,0.88,100,0.4,16,23.6,0,9]
[null,{"$f":"AC82","v":650},{"$f":"$J$4*B82^6+$K$4*B82^5+$L$4*B82^4+$M$4*B82^3+$N$4*B82^2+$O$4*B82","v":79.780926047400044},0.99999999999999989,{"$f":"IF($B82*$F$3>$B$11,\"\",$B82*$F$3)","v":467.6829268292683},64.958788271643812,0.81421451830541558,{"$f":"IF($B82*$F$4>$B$11,\"\",$B82*$F$4)","v":650},79.780926047400044,0.99999999999999989,{"$f":"IF($B82*$F$5>$B$11,\"\",$B82*$F$5)","v":808.53658536585363},{"$f":"IF(K82>$B$11,\"\",$J$5*K82^6+$K$5*K82^5+$L$5*K82^4+$M$5*K82^3+$N$5*K82^2+$O$5*K82)","v":89.486112394911657},{"$f":"IF(K82>$B$11,\"\",1/$C82*L82)","v":1.1216479530676979},{"$f":"IF($B82*$F$6>$B$11,\"\",$B82*$F$6)","v":951.21951219512198},95.969727550196183,{"$f":"IF(N82>$B$11,\"\",1/$C82*O82)","v":1.2029156880577936},null,null,null,null,null,null,null,null,null,null,{"$f":"IF($AA$13=$AS$13,AS82,IF($AA$13=$BK$13,BK82,IF($AA$13=$CC$13,CC82,IF($AA$13=$CU$13,CU82,\"-\"))))","v":80},0,650,1.26,11,26,45,22,56,0.8,0.8,100,0.4,16,22.9,null,6,null,{"$f":"BC82/(AX82-BF82)*1000","v":72},null,650,1.75,20,26,45,22,55,0.72,0.72,100,0.4,16,22.2,0,5,null,{"$f":"BU82/(BP82-BX82)*1000","v":80},null,650,1.26,11,26,45,22,56,0.8,0.8,100,0.4,16,22.9,0,6,null,{"$f":"CM82/(CH82-CP82)*1000","v":84.999999999999986},null,650,1.01,7,26,45,22,57,0.85,0.85,100,0.4,16,23.3,0,8,null,{"$f":"DE82/(CZ82-DH82)*1000","v":88},null,650,0.86,5,26,45,21,58,0.88,0.88,100,0.4,16,23.6,0,9]
[null,660,80.121610482782813,{"$f":"1/C83*C83","v":1},474.8780487804878,{"$f":"IF(E83>$B$11,\"\",$J$3*E83^6+$K$3*E83^5+$L$3*E83^4+$M$3*E83^3+$N$3*E83^2+$O$3*E83)","v":65.294979174492639},{"$f":"IF(E83>$B$11,\"\",1/$C83*F83)","v":0.81494841130937767},660,{"$f":"IF(H83>$B$11,\"\",$J$4*H83^6+$K$4*H83^5+$L$4*H83^4+$M$4*H83^3+$N$4*H83^2+$O$4*H83)","v":80.121610482782813},{"$f":"IF(H83>$B$11,\"\",1/$C83*I83)","v":1},820.97560975609758,89.765444774546836,1.120364958138683,965.85365853658539,{"$f":"IF(N83>$B$11,\"\",$J$6*N83^6+$K$6*N83^5+$L$6*N83^4+$M$6*N83^3+$N$6*N83^2+$O$6*N83)","v":96.355632689378695},{"$f":"IF(N83>$B$11,\"\",1/$C83*O83)","v":1.2026172727779152},null,null,null,null,null,null,null,null,null,null,80,0,660,1.28,11,26,45,22,56,0.8,0.8,100,0.4,16,22.9,null,6,null,72,null,660,1.78,21,26,45,22,55,0.72,0.72,100,0.4,16,22.2,0,5,null,80,null,660,1.28,11,26,45,22,56,0.8,0.8,100,0.4,16,22.9,0,6,null,84.999999999999986,null,660,1.03,8,26,45,22,57,0.85,0.85,100,0.4,16,23.3,0,8,null,89,null,660,0.87,6,26,45,21,57,0.89,0.89,100,0.4,16,23.7,0,9]
[null,670,80.454869714061772,0.99999999999999989,482.07317073170731,65.625091080830174,0.81567581072547957,670,80.454869714061772,0.99999999999999989,833.41463414634143,90.033157297782225,1.1190516822382768,980.48780487804879,96.801781148016346,{"$f":"IF(N84>$B$11,\"\",1/$C84*O84)","v":1.2031811311366463},null,null,null,null,null,null,null,null,null,null,80,0,670,1.3,12,26,45,22,56,0.8,0.8,100,0.4,16,22.9,null,6,null,72,null,670,1.8,21,26,45,22,54,0.72,0.72,100,0.4,16,22.2,0,5,null,80,null,670,1.3,12,26,45,22,56,0.8,0.8,100,0.4,16,22.9,0,6,null,86,null,670,1.04,8,26,45,22,57,0.86,0.86,100,0.4,16,23.4,0,8,null,89,null,670,0.89,6,26,45,21,57,0.89,0.89,100,0.4,16,23.7,0,9]
[null,680,80.780723549088719,1,489.26829268292681,65.949303998054461,0.81639902566580103,680,80.780723549088719,1,845.85365853658539,90.29015864069504,1.1177191126027441,995.1219512195122,97.324674385636797,{"$f":"IF(N85>$B$11,\"\",1/$C85*O85)","v":1.2048007260852853},null,null,null,null,null,null,null,null,null,null,81,0,680,1.32,12,26,45,22,56,0.81,0.81,100,0.4,16,23,null,6,null,73,null,680,1.83,22,26,45,22,54,0.73,0.73,100,0.4,16,22.3,0,5,null,81,null,680,1.32,12,26,45,22,56,0.81,0.81,100,0.4,16,23,0,6,null,86,null,680,1.06,8,26,45,22,56,0.86,0.86,100,0.4,16,23.4,0,8,null,89,null,680,0.9,6,26,45,22,57,0.89,0.89,100,0.4,16,23.7,0,9]
[null,690,81.099181772824096,1,496.46341463414632,66.267785888788211,0.81712027717392077,690,81.099181772824096,1,858.29268292682923,90.537625178138512,1.1163814874452553,"","","",null,null,null,null,null,null,null,null,null,null,81,0,690,1.34,12,26,45,22,55,0.81,0.81,100,0.4,16,23,null,6,null,73,null,690,1.86,23,26,45,22,54,0.73,0.73,100,0.4,16,22.3,0,5,null,81,null,690,1.34,12,26,45,22,55,0.81,0.81,100,0.4,16,23,0,6,null,86,null,690,1.07,8,26,45,22,56,0.86,0.86,100,0.4,16,23.4,0,8,null,90,null,690,0.91,6,26,45,22,57,0.9,0.9,100,0.4,16,23.7,0,9]
[null,700,81.410247957672368,1,503.65853658536582,66.58069345454129,0.81784167380448947,700,81.410247957672368,1,870.73170731707319,90.777032587137228,1.1150565790480693,"","","",null,null,null,null,null,null,null,null,null,null,81,0,700,1.36,13,26,45,22,55,0.81,0.81,100,0.4,16,23,null,6,null,73,null,700,1.88,23,26,45,22,54,0.73,0.73,100,0.4,16,22.3,0,5,null,81,null,700,1.36,13,26,45,22,55,0.81,0.81,100,0.4,16,23,0,6,null,86,null,700,1.0900000000000001,8,26,45,22,56,0.86,0.86,100,0.4,16,23.5,0,8,null,90,null,700,0.93,6,26,45,22,57,0.9,0.9,100,0.4,16,23.8,0,9]
[null,710,81.713923351798883,1,510.85365853658533,66.888172897808886,0.81856518637391285,710,81.713923351798883,1,883.17073170731703,91.010188474492963,1.1137659867666778,"","","",null,null,null,null,null,null,null,null,null,null,81.999999999999986,0,710,1.37,13,26,45,22,55,0.82,0.82,100,0.4,16,23,null,6,null,74,null,710,1.91,24,26,45,22,54,0.74,0.74,100,0.4,16,22.3,0,5,null,81.999999999999986,null,710,1.37,13,26,45,22,55,0.82,0.82,100,0.4,16,23,0,6,null,87,null,710,1.1000000000000001,9,26,45,22,56,0.87,0.87,100,0.4,16,23.5,0,8,null,90,null,710,0.94,6,26,45,22,57,0.9,0.9,100,0.4,16,23.8,0,9]
[null,720,82.010210845427423,1,518.04878048780483,67.190360662605855,0.81929262185712493,720,82.010210845427423,1,895.60975609756099,91.239266028603083,1.1125354402584156,"","","",null,null,null,null,null,null,null,null,null,null,81.999999999999986,0,720,1.39,13,26,45,22,55,0.82,0.82,100,0.4,16,23.1,null,6,null,74,null,720,1.94,24,26,45,22,54,0.74,0.74,100,0.4,16,22.4,0,5,null,81.999999999999986,null,720,1.39,13,26,45,22,55,0.82,0.82,100,0.4,16,23.1,0,6,null,87,null,720,1.1200000000000001,9,26,45,22,56,0.87,0.87,100,0.4,16,23.5,0,8,null,91,null,720,0.95,7,26,45,22,56,0.91,0.91,100,0.4,16,23.8,0,9]
[null,730,82.299119015118208,1,525.2439024390244,67.487384153437006,0.82002559639842187,730,82.299119015118208,1,908.04878048780483,91.4668386954894,1.1113951132172764,"","","",null,null,null,null,null,null,null,null,null,null,81.999999999999986,0,730,1.41,14,26,45,22,55,0.82,0.82,100,0.4,16,23.1,null,6,null,74,null,730,1.96,25,26,45,22,54,0.74,0.74,100,0.4,16,22.4,0,5,null,81.999999999999986,null,730,1.41,14,26,45,22,55,0.82,0.82,100,0.4,16,23.1,0,6,null,87,null,730,1.1399999999999999,9,26,45,22,56,0.87,0.87,100,0.4,16,23.5,0,8,null,91,null,730,0.97,7,26,45,22,56,0.91,0.91,100,0.4,16,23.8,0,9]
[null,740,82.580666246027249,1,532.43902439024384,67.779362432702612,0.82076550739820786,740,82.580666246027249,1,920.48780487804879,91.695915879039944,1.1103799478422252,"","","",null,null,null,null,null,null,null,null,null,null,82.999999999999986,0,740,1.43,14,26,45,22,55,0.83,0.83,100,0.4,16,23.1,null,6,null,74,null,740,1.99,26,26,45,22,54,0.74,0.74,100,0.4,16,22.4,0,5,null,82.999999999999986,null,740,1.43,14,26,45,22,55,0.83,0.83,100,0.4,16,23.1,0,6,null,88,null,740,1.1499999999999999,9,26,45,22,56,0.88,0.88,100,0.4,16,23.5,0,8,null,91,null,740,0.98,7,26,45,22,56,0.91,0.91,100,0.4,16,23.9,0,9]
[null,750,82.854884932145296,1,539.63414634146341,68.066406896541395,0.82151350463264716,750,82.854884932145296,1,932.92682926829264,91.929979665460792,1.1095299901840141,"","","",null,null,null,null,null,null,null,null,null,null,82.999999999999986,0,750,1.45,14,26,45,22,55,0.83,0.83,100,0.4,16,23.1,null,6,null,75,null,750,2.02,26,26,45,22,54,0.75,0.75,100,0.4,16,22.4,0,5,null,82.999999999999986,null,750,1.45,14,26,45,22,55,0.83,0.83,100,0.4,16,23.1,0,6,null,88,null,750,1.17,10,26,45,22,55,0.88,0.88,100,0.4,16,23.6,0,8,null,92,null,750,0.99,7,26,45,22,56,0.92,0.92,100,0.4,16,23.9,0,9]
[null,760,83.121825754518937,1,546.82926829268285,68.348621929107566,0.82227046035970619,760,83.121825754518937,1,945.36585365853659,92.173022571940635,1.1088907364011988,"","","",null,null,null,null,null,null,null,null,null,null,82.999999999999986,0,760,1.47,15,26,45,22,55,0.83,0.83,100,0.4,16,23.2,null,6,null,75,null,760,2.04,27,26,45,23,53,0.75,0.75,100,0.4,16,22.4,0,5,null,82.999999999999986,null,760,1.47,15,26,45,22,55,0.83,0.83,100,0.4,16,23.2,0,6,null,88,null,760,1.18,10,26,45,22,55,0.88,0.88,100,0.4,16,23.6,0,8,null,92,null,760,1.01,7,26,45,22,56,0.92,0.92,100,0.4,16,23.9,0,9]
[null,770,83.381562037451431,1,554.02439024390242,68.626105535285518,0.82303693836368286,770,83.381562037451431,1,957.80487804878044,92.429586319526663,1.1085134898049913,"","","",null,null,null,null,null,null,null,null,null,null,82.999999999999986,0,770,1.49,15,26,45,22,54,0.83,0.83,100,0.4,16,23.2,null,6,null,75,null,770,2.0699999999999998,28,26,45,23,53,0.75,0.75,100,0.4,16,22.5,0,5,null,82.999999999999986,null,770,1.49,15,26,45,22,54,0.83,0.83,100,0.4,16,23.2,0,6,null,88,null,770,1.2,10,26,45,22,55,0.88,0.88,100,0.4,16,23.6,0,8,null,92,null,770,1.02,7,26,45,22,56,0.92,0.92,100,0.4,16,23.9,0,9]
[null,780,83.634194182684723,1,561.21951219512198,68.898949951839029,0.823813161890948,780,83.634194182684723,1,970.2439024390244,92.704801630210795,1.108455728379625,"","","",null,null,null,null,null,null,null,null,null,null,83.999999999999986,0,780,1.51,15,26,45,22,54,0.84,0.84,100,0.4,16,23.2,null,6,null,75,null,780,2.1,28,26,45,23,53,0.75,0.75,100,0.4,16,22.5,0,5,null,83.999999999999986,null,780,1.51,15,26,45,22,54,0.84,0.84,100,0.4,16,23.2,0,6,null,89,null,780,1.21,10,26,45,22,55,0.89,0.89,100,0.4,16,23.6,0,8,null,92,null,780,1.03,8,26,45,22,56,0.92,0.92,100,0.4,16,24,0,9]
[null,790,83.879854181561996,0.99999999999999989,568.41463414634143,69.167242236997424,0.82459898043315127,790,83.879854181561996,0.99999999999999989,982.68292682926824,93.004429048229781,1.1087814822247688,"","","",null,null,null,null,null,null,null,null,null,null,83.999999999999986,0,790,1.53,16,26,45,22,54,0.84,0.84,100,0.4,16,23.2,null,6,null,76,null,790,2.13,29,26,45,23,53,0.76,0.76,100,0.4,16,22.5,0,5,null,83.999999999999986,null,790,1.53,16,26,45,22,54,0.84,0.84,100,0.4,16,23.2,0,6,null,89,null,790,1.23,11,26,45,22,55,0.89,0.89,100,0.4,16,23.7,0,8,null,93,null,790,1.04,8,26,45,22,55,0.93,0.93,100,0.4,16,24,0,9]
[null,800,84.11871020517151,1,575.60975609756099,69.431064838477113,0.8253938353207011,800,84.11871020517151,1,995.1219512195122,93.334900785575428,1.109561720073037,"","","",null,null,null,null,null,null,null,null,null,null,83.999999999999986,0,800,1.55,16,26,45,22,54,0.84,0.84,100,0.4,16,23.2,null,6,null,76,null,800,2.15,30,26,45,23,53,0.76,0.76,100,0.4,16,22.5,0,5,null,83.999999999999986,null,800,1.55,16,26,45,22,54,0.84,0.84,100,0.4,16,23.2,0,6,null,89,null,800,1.24,11,26,45,22,55,0.89,0.89,100,0.4,16,23.7,0,8,null,93,null,800,1.06,8,26,45,22,55,0.93,0.93,100,0.4,16,24,0,9]
[null,810,84.35097127247036,1,582.80487804878044,69.69049613993937,0.82619672409965794,810,84.35097127247036,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,83.999999999999986,0,810,1.57,16,26,45,22,54,0.84,0.84,100,0.4,16,23.3,null,6,null,76,null,810,2.1800000000000002,30,26,45,23,53,0.76,0.76,100,0.4,16,22.5,0,5,null,83.999999999999986,null,810,1.57,16,26,45,22,54,0.84,0.84,100,0.4,16,23.3,0,6,null,89,null,810,1.26,11,26,45,22,55,0.89,0.89,100,0.4,16,23.7,0,8,null,93,null,810,1.07,8,26,45,22,55,0.93,0.93,100,0.4,16,24,0,9]
[null,820,84.576891996389293,0.99999999999999989,590,69.945610985883775,0.82700616367967095,820,84.576891996389293,0.99999999999999989,"","","","","","",null,null,null,null,null,null,null,null,null,null,{"$f":"IF($AA$13=$AS$13,AS99,IF($AA$13=$BK$13,BK99,IF($AA$13=$CC$13,CC99,IF($AA$13=$CU$13,CU99,\"-\"))))","v":84.999999999999986},0,820,1.59,17,26,45,22,54,0.85,0.85,100,0.4,16,23.3,null,6,null,76,null,820,2.21,31,26,45,23,53,0.76,0.76,100,0.4,16,22.6,0,5,null,84.999999999999986,null,820,1.59,17,26,45,22,54,0.85,0.85,100,0.4,16,23.3,0,6,null,90,null,820,1.28,11,26,45,22,55,0.9,0.9,100,0.4,16,23.7,0,8,null,93,null,820,1.08,8,26,45,22,55,0.93,0.93,100,0.4,16,24,0,9]
[null,830,84.796777407919137,1,597.19512195121945,70.196481184977927,0.8278201522599643,830,84.796777407919137,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,84.999999999999986,0,830,1.61,17,26,45,22,54,0.85,0.85,100,0.4,16,23.3,null,6,null,76,null,830,2.23,32,26,45,23,53,0.76,0.76,100,0.4,16,22.6,0,5,null,84.999999999999986,null,830,1.61,17,26,45,22,54,0.85,0.85,100,0.4,16,23.3,0,6,null,90,null,830,1.29,12,26,45,22,54,0.9,0.9,100,0.4,16,23.7,0,8,null,94,null,830,1.1000000000000001,9,26,45,22,55,0.94,0.94,100,0.4,16,24.1,0,9]
[null,840,85.010987858176236,1,604.39024390243901,70.443175991822585,0.82863613006524384,840,85.010987858176236,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,84.999999999999986,0,840,1.63,18,26,45,22,54,0.85,0.85,100,0.4,16,23.3,null,6,null,77,null,840,2.2599999999999998,32,26,45,23,53,0.77,0.77,100,0.4,16,22.6,0,5,null,84.999999999999986,null,840,1.63,18,26,45,22,54,0.85,0.85,100,0.4,16,23.3,0,6,null,90,null,840,1.31,12,26,45,22,54,0.9,0.9,100,0.4,16,23.8,0,8,null,94,null,840,1.1100000000000001,9,26,45,22,55,0.94,0.94,100,0.4,16,24.1,0,9]
[null,850,85.219943998450219,1,611.58536585365846,70.685762567153319,0.8294509389543695,850,85.219943998450219,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,84.999999999999986,0,850,1.65,18,26,45,22,54,0.85,0.85,100,0.4,16,23.3,null,6,null,77,null,850,2.29,33,26,45,23,53,0.77,0.77,100,0.4,16,22.6,0,5,null,84.999999999999986,null,850,1.65,18,26,45,22,54,0.85,0.85,100,0.4,16,23.3,0,6,null,90,null,850,1.32,12,26,45,22,54,0.9,0.9,100,0.4,16,23.8,0,8,null,94,null,850,1.1200000000000001,9,26,45,22,55,0.94,0.94,100,0.4,16,24.1,0,9]
[null,860,85.424131838231915,1,618.78048780487802,70.924306416477805,0.83026078100258016,860,85.424131838231915,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,84.999999999999986,0,860,1.66,18,26,45,22,54,0.85,0.85,100,0.4,16,23.4,null,6,null,77,null,860,2.31,34,26,45,23,53,0.77,0.77,100,0.4,16,22.6,0,5,null,84.999999999999986,null,860,1.66,18,26,45,22,54,0.85,0.85,100,0.4,16,23.4,0,6,null,91,null,860,1.34,12,26,45,22,54,0.91,0.91,100,0.4,16,23.8,0,8,null,94,null,860,1.1399999999999999,9,26,45,22,55,0.94,0.94,100,0.4,16,24.1,0,9]
[null,870,85.624107881222017,1,625.97560975609758,71.158871807148614,0.83106117620355691,870,85.624107881222017,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,86,0,870,1.68,19,26,45,23,53,0.86,0.86,100,0.4,16,23.4,null,6,null,77,null,870,2.34,35,26,45,23,53,0.77,0.77,100,0.4,16,22.7,0,5,null,86,null,870,1.68,19,26,45,23,53,0.86,0.86,100,0.4,16,23.4,0,6,null,91,null,870,1.35,13,26,45,22,54,0.91,0.91,100,0.4,16,23.8,0,8,null,94,null,870,1.1499999999999999,9,26,45,22,54,0.94,0.94,100,0.4,16,24.1,0,9]
[null,880,85.820504339320053,1,633.17073170731703,71.389522163873522,0.83184691949153766,880,85.820504339320053,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,86,0,880,1.7,19,26,45,23,53,0.86,0.86,100,0.4,16,23.4,null,6,null,78,null,880,2.37,35,26,45,23,52,0.78,0.78,100,0.4,16,22.7,0,5,null,86,null,880,1.7,19,26,45,23,53,0.86,0.86,100,0.4,16,23.4,0,6,null,91,null,880,1.37,13,26,45,22,54,0.91,0.91,100,0.4,16,23.8,0,8,null,95,null,880,1.1599999999999999,9,26,45,22,54,0.95,0.95,100,0.4,16,24.2,0,9]
[null,890,86.014034424595081,1,640.36585365853659,71.61632044265923,0.83261203734655964,890,86.014034424595081,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,86,0,890,1.72,20,26,45,23,53,0.86,0.86,100,0.4,16,23.4,null,6,null,78,null,890,2.39,36,26,45,23,52,0.78,0.78,100,0.4,16,22.7,0,5,null,86,null,890,1.72,20,26,45,23,53,0.86,0.86,100,0.4,16,23.4,0,6,null,91,null,890,1.38,13,26,45,22,54,0.91,0.91,100,0.4,16,23.9,0,8,null,95,null,890,1.18,10,26,45,22,54,0.95,0.95,100,0.4,16,24.2,0,9]
[null,900,86.205497719236632,1,647.56097560975604,71.839329483193438,0.83334974431871522,900,86.205497719236632,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,86,0,900,1.74,20,26,45,23,53,0.86,0.86,100,0.4,16,23.4,null,6,null,78,null,900,2.42,37,26,45,23,52,0.78,0.78,100,0.4,16,22.7,0,5,null,86,null,900,1.74,20,26,45,23,53,0.86,0.86,100,0.4,16,23.4,0,6,null,91,null,900,1.4,13,26,45,22,54,0.91,0.91,100,0.4,16,23.9,0,8,null,95,null,900,1.19,10,26,45,22,54,0.95,0.95,100,0.4,16,24.2,0,9]
[null,910,86.395785623485779,1,654.7560975609756,72.058612339661352,0.83405239989012825,910,86.395785623485779,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,86,0,910,1.76,20,26,45,23,53,0.86,0.86,100,0.4,16,23.4,null,6,null,78,null,910,2.4500000000000002,38,26,45,23,52,0.78,0.78,100,0.4,16,22.7,0,5,null,86,null,910,1.76,20,26,45,23,53,0.86,0.86,100,0.4,16,23.4,0,6,null,92,null,910,1.42,14,26,45,22,54,0.92,0.92,100,0.4,16,23.9,0,8,null,95,null,910,1.2,10,26,45,22,54,0.95,0.95,100,0.4,16,24.2,0,9]
[null,920,86.585886881548618,1,661.95121951219505,72.274232589999031,0.83471146618699832,920,86.585886881548618,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,87,0,920,1.78,21,26,45,23,53,0.87,0.87,100,0.4,16,23.5,null,6,null,78,null,920,2.48,38,26,45,23,52,0.78,0.78,100,0.4,16,22.7,0,5,null,87,null,920,1.78,21,26,45,23,53,0.87,0.87,100,0.4,16,23.5,0,6,null,92,null,920,1.43,14,26,45,22,53,0.92,0.92,100,0.4,16,23.9,0,8,null,95,null,920,1.22,10,26,45,22,54,0.95,0.95,100,0.4,16,24.2,0,9]
[null,930,86.776893185487722,1,669.14634146341461,72.486254623581317,0.83531746715845401,930,86.776893185487722,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,87,0,930,1.8,21,26,45,23,53,0.87,0.87,100,0.4,16,23.5,null,6,null,78,null,930,2.5,39,26,45,23,52,0.78,0.78,100,0.4,16,22.8,0,5,null,87,null,930,1.8,21,26,45,23,53,0.87,0.87,100,0.4,16,23.5,0,6,null,92,null,930,1.45,14,26,45,23,53,0.92,0.92,100,0.4,16,23.9,0,8,null,96,null,930,1.23,11,26,45,22,54,0.96,0.96,100,0.4,16,24.2,0,9]
[null,940,86.970004857098218,1,676.34146341463418,72.694743907348226,0.83585994995394219,940,86.970004857098218,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,87,0,940,1.82,22,26,45,23,53,0.87,0.87,100,0.4,16,23.5,null,6,null,79,null,940,2.5299999999999998,40,26,45,23,52,0.79,0.79,100,0.4,16,22.8,0,5,null,87,null,940,1.82,22,26,45,23,53,0.87,0.87,100,0.4,16,23.5,0,6,null,92,null,940,1.46,14,26,45,23,53,0.92,0.92,100,0.4,16,23.9,0,8,null,96,null,940,1.24,11,26,45,22,54,0.96,0.96,100,0.4,16,24.3,0,9]
[null,950,87.166536607760747,1,683.53658536585363,72.899767230363892,0.83632744935598791,950,87.166536607760747,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,87,0,950,1.84,22,26,45,23,53,0.87,0.87,100,0.4,16,23.5,null,6,null,79,null,950,2.56,41,26,45,23,52,0.79,0.79,100,0.4,16,22.8,0,5,null,87,null,950,1.84,22,26,45,23,53,0.87,0.87,100,0.4,16,23.5,0,6,null,92,null,950,1.48,15,26,45,23,53,0.92,0.92,100,0.4,16,24,0,8,null,96,null,950,1.26,11,26,45,22,54,0.96,0.96,100,0.4,16,24.3,0,9]
[null,960,87.367923376277417,1,690.73170731707319,73.101392926814611,0.83670745625920961,960,87.367923376277417,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,87,0,960,1.86,23,26,45,23,53,0.87,0.87,100,0.4,16,23.5,null,6,null,79,null,960,2.58,41,26,45,23,52,0.79,0.79,100,0.4,16,22.8,0,5,null,87,null,960,1.86,23,26,45,23,53,0.87,0.87,100,0.4,16,23.5,0,6,null,93,null,960,1.49,15,26,45,23,53,0.93,0.93,100,0.4,16,24,0,8,null,96,null,960,1.27,11,26,45,22,54,0.96,0.96,100,0.4,16,24.3,0,9]
[null,970,{"$f":"$J$4*B114^6+$K$4*B114^5+$L$4*B114^4+$M$4*B114^3+$N$4*B114^2+$O$4*B114","v":87.575726244688724},1,697.92682926829264,73.299691077440485,0.8369863913276534,970,87.575726244688724,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,88,0,970,1.88,23,26,45,23,53,0.88,0.88,100,0.4,16,23.5,null,6,null,79,null,970,2.61,42,26,45,23,52,0.79,0.79,100,0.4,16,22.8,0,5,null,88,null,970,1.88,23,26,45,23,53,0.88,0.88,100,0.4,16,23.5,0,6,null,93,null,970,1.51,15,26,45,23,53,0.93,0.93,100,0.4,16,24,0,8,null,96,null,970,1.28,11,26,45,22,54,0.96,0.96,100,0.4,16,24.3,0,9]
[null,980,{"$f":"$J$4*B115^6+$K$4*B115^5+$L$4*B115^4+$M$4*B115^3+$N$4*B115^2+$O$4*B115","v":87.791638432068964},1,705.1219512195122,73.494733689404768,0.83714958510853177,980,87.791638432068964,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,88,0,980,1.9,23,26,45,23,53,0.88,0.88,100,0.4,16,23.6,null,6,null,79,null,980,2.64,43,26,45,23,52,0.79,0.79,100,0.4,16,22.8,0,5,null,88,null,980,1.9,23,26,45,23,53,0.88,0.88,100,0.4,16,23.6,0,6,null,93,null,980,1.53,16,26,45,23,53,0.93,0.93,100,0.4,16,24,0,8,null,97,null,980,1.3,12,26,45,23,53,0.97,0.97,100,0.4,16,24.3,0,9]
[null,990,{"$f":"$J$4*B116^6+$K$4*B116^5+$L$4*B116^4+$M$4*B116^3+$N$4*B116^2+$O$4*B116","v":88.017491366305023},1,712.31707317073165,73.686594854597502,0.83718126602738308,990,88.017491366305023,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,{"$f":"IF($AA$13=$AS$13,AS116,IF($AA$13=$BK$13,BK116,IF($AA$13=$CC$13,CC116,IF($AA$13=$CU$13,CU116,\"-\"))))","v":88},0,990,1.92,24,26,45,23,53,0.88,0.88,100,0.4,16,23.6,null,6,null,80,null,990,2.66,44,26,45,23,52,0.8,0.8,100,0.4,16,22.9,0,5,null,88,null,990,1.92,24,26,45,23,53,0.88,0.88,100,0.4,16,23.6,0,6,null,93,null,990,1.54,16,26,45,23,53,0.93,0.93,100,0.4,16,24,0,8,null,97,null,990,1.31,12,26,45,23,53,0.97,0.97,100,0.4,16,24.3,0,9]
[null,1000,{"$f":"$J$4*B117^6+$K$4*B117^5+$L$4*B117^4+$M$4*B117^3+$N$4*B117^2+$O$4*B117","v":88.255260833854777},1,719.51219512195121,73.87535088637685,0.83706455783356792,1000,88.255260833854777,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,88,0,1000,1.94,24,26,45,23,52,0.88,0.88,100,0.4,16,23.6,null,6,null,80,null,1000,2.69,45,26,45,23,52,0.8,0.8,100,0.4,16,22.9,0,5,null,88,null,1000,1.94,24,26,45,23,52,0.88,0.88,100,0.4,16,23.6,0,6,null,93,null,1000,1.56,16,26,45,23,53,0.93,0.93,100,0.4,16,24,0,8,null,97,null,1000,1.32,12,26,45,23,53,0.97,0.97,100,0.4,16,24.3,0,9]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"q sensibel"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"W/K"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"DW18/(DT18-DP18)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"DW82/(DT82-DP82)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"DW114/(DT114-DP114)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"DW115/(DT115-DP115)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"DW116/(DT116-DP116)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"DW117/(DT117-DP117)*1000","v":{"$error":"#DIV/0!"}}]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"q sensibel"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"W/K"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"EM18/(EJ18-EF18)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"EM82/(EJ82-EF82)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"EM114/(EJ114-EF114)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"EM115/(EJ115-EF115)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"EM116/(EJ116-EF116)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"BU441/(BP441-BX441)*1000","v":{"$error":"#DIV/0!"}}]

{"sheet":"BG;WT2,5;h","index":7,"n_rows":441,"n_cols":113,"rows_kept":441,"cut":false,"hidden":true,"merged":[]}
["TT",null,"Master auswählen ->","BG","WT","Verhältnis","DpH =","Verhältnis",{"$f":"CONCATENATE(\"Polynom 6 Ordnung - \",A3)","v":"Polynom 6 Ordnung - BG;WT2,5;h"},6,5,4,3,2,1,0]
["2017-08-14",null,null,"BG 800",{"$f":"VLOOKUP(D2,D3:F6,2,0)","v":820},{"$f":"VLOOKUP(D2,D3:F6,3,0)","v":1},{"$f":"VLOOKUP(D2,D3:G6,4,0)","v":2},{"$f":"VLOOKUP(E2,E3:H6,4,0)","v":1},{"$f":"D2","v":"BG 800"},{"$f":"VLOOKUP($I2,$I$3:$P$6,2,0)","v":-1.1272515986343666E-15},{"$f":"VLOOKUP($I2,$I$3:$P$6,3,0)","v":3.805556241997797E-12},{"$f":"VLOOKUP($I2,$I$3:$P$6,4,0)","v":-5.0700197601788311E-9},{"$f":"VLOOKUP($I2,$I$3:$P$6,5,0)","v":3.4046035050996859E-6},{"$f":"VLOOKUP($I2,$I$3:$P$6,6,0)","v":-1.240901202992864E-3},{"$f":"VLOOKUP($I2,$I$3:$P$6,7,0)","v":0.27137689994379355},{"$f":"VLOOKUP($I2,$I$3:$P$6,8,0)","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"  Datentabelle aus Eurocoil entnehmen"]
[{"$f":"MID(CELL(\"dateiname\",A1),FIND(\"]\",CELL(\"dateiname\",A1))+1,255)","v":"BG;WT2,5;h"},null,null,"BG 630",590,{"$f":"E3/$E$2","v":0.71951219512195119},{"$f":"BC18","v":1},{"$f":"G3/$G$2","v":0.5},{"$f":"D3","v":"BG 630"},{"$f":"LINEST(AP18:AP117,AR18:AR117^{1,2,3,4,5,6},0,0)","v":-1.0632921310143854E-15},3.5858514113277551E-12,-4.7665713730329927E-9,3.1844233640596841E-6,-1.1456303236966005E-3,0.2418965836022402,0]
[null,null,null,"BG 800",820,{"$f":"E4/$E$2","v":1},{"$f":"BR18","v":2},{"$f":"G4/$G$2","v":1},{"$f":"D4","v":"BG 800"},{"$f":"LINEST(BE18:BE117,BG18:BG117^{1,2,3,4,5,6},0,0)","v":-1.1272515986343666E-15},3.805556241997797E-12,-5.0700197601788311E-9,3.4046035050996859E-6,-1.240901202992864E-3,0.27137689994379355,0]
["WT 4L",2.5,"mm","BG 1000",1020,{"$f":"E5/$E$2","v":1.2439024390243902},{"$f":"CG18","v":2},1,{"$f":"D5","v":"BG 1000"},{"$f":"LINEST(BT18:BT117,BV18:BV117^{1,2,3,4,5,6},0,0)","v":-1.0533899171333763E-15},3.5924964377269486E-12,-4.8503157076668502E-9,3.3199387011673363E-6,-1.247468164390513E-3,0.28700192016743137,0]
["Länge",820,"mm","BG 1200",1200,{"$f":"E6/$E$2","v":1.4634146341463414},{"$f":"CV18","v":2},1,{"$f":"D6","v":"BG 1200"},{"$f":"LINEST(CI18:CI116,CK18:CK116^{1,2,3,4,5,6},0,0)","v":-1.1243960372549887E-15},3.7947227790113298E-12,-5.0752622583859397E-9,3.4500448791136683E-6,-1.2955328331244712E-3,0.30220703780447411,0]
["Rohrreihen",3,null,null,null,null,"Wassermenge =",{"$f":"CQ18","v":100}]
[null,null,null,null,null,null,null,null,{"$f":"CONCATENATE(\"Korrekturfaktoren - \",A3)","v":"Korrekturfaktoren - BG;WT2,5;h"},6,5,4,3,2,1,0]
[null,null,null,null,null,null,null,null,{"$f":"D3","v":"BG 630"},{"$f":"LINEST(G18:G117,C18:C117^{0,1,2,3,4,5,6},0,0)","v":-3.7006780469048956E-9},5.2916092210101542E-7,-2.8874068169499873E-5,7.4643517079846689E-4,-9.2559773650928833E-3,5.3477354565385993E-2,0.55401145099493976]
["Grenzen",null,null,null,null,null,null,null,{"$f":"D4","v":"BG 800"},{"$f":"LINEST(J18:J117,C18:C117^{0,1,2,3,4,5,6},0,0)","v":0},0,0,0,0,0,1]
["Maximum",{"$f":"MAX(B18:B117)","v":1000},"m³/h",null,null,null,null,null,{"$f":"D5","v":"BG 1000"},{"$f":"LINEST(M18:M97,C18:C97^{0,1,2,3,4,5,6},0,0)","v":5.0598450582631205E-9},-6.4793604545780126E-7,3.1562663484728062E-5,-7.2739043704325929E-4,8.0969034809547265E-3,-4.4325601737440629E-2,1.3798932203341547]
[null,null,null,null,null,null,null,null,{"$f":"D6","v":"BG 1200"},{"$f":"LINEST(P18:P84,C18:C84^{0,1,2,3,4,5,6},0,0)","v":1.0586314274067539E-8},-1.3177185971155788E-6,6.2301969705487415E-5,-1.3909372253769986E-3,1.502647645343452E-2,-8.3048451703332346E-2,1.7437833789697272,null,null,null,null,null,null,null,null,null,null,null,null,1,2,3,4,6,9,10,11,12,13,14,15,null,null,null,1,2,3,4,6,9,10,11,12,13,14,15,null,null,null,1,2,3,4,6,9,10,11,12,13,14,15,null,null,null,1,2,3,4,6,9,10,11,12,13,14,15,null,null,null,1,2,3,4,6,9,10,11,12,13,14,15]
[null,{"$f":"CONCATENATE(\"Master - \",AA13)","v":"Master - BG 800"},null,null,{"$f":"AP13","v":"BG630"},null,null,{"$f":"BE13","v":"BG 800"},null,null,{"$f":"BT13","v":"BG1000"},null,null,{"$f":"CI13","v":"BG1200"},null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"D2","v":"BG 800"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,"BG630",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"BG 800",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"BG1000",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"BG1200"]
[null,"Volumen-nstrom","spez. \nLeistung","Korrektur-faktor","Volumen-nstrom","spez. \nLeistung","Korrektur-faktor","Volumen-nstrom","spez. \nLeistung","Korrektur-faktor","Volumen-nstrom","spez. \nLeistung","Korrektur-faktor","Volumen-nstrom","spez. \nLeistung","Korrektur-faktor",null,null,null,null,null,null,null,null,null,null,{"$f":"IF($AA$13=$AP$13,AP14,IF($AA$13=$BE$13,BE14,IF($AA$13=$BT$13,BT14,IF($AA$13=$CI$13,CI14,\"-\"))))","v":"q sensibel"},{"$f":"IF($AA$13=$AP$13,AQ14,IF($AA$13=$BE$13,BF14,IF($AA$13=$BT$13,BU14,IF($AA$13=$CI$13,CJ14,\"-\"))))","v":"S"},{"$f":"IF($AA$13=$AP$13,AR14,IF($AA$13=$BE$13,BG14,IF($AA$13=$BT$13,BV14,IF($AA$13=$CI$13,CK14,\"-\"))))","v":"QA"},{"$f":"IF($AA$13=$AP$13,AS14,IF($AA$13=$BE$13,BH14,IF($AA$13=$BT$13,BW14,IF($AA$13=$CI$13,CL14,\"-\"))))","v":"VA"},{"$f":"IF($AA$13=$AP$13,AT14,IF($AA$13=$BE$13,BI14,IF($AA$13=$BT$13,BX14,IF($AA$13=$CI$13,CM14,\"-\"))))","v":"DPA"},{"$f":"IF($AA$13=$AP$13,AU14,IF($AA$13=$BE$13,BJ14,IF($AA$13=$BT$13,BY14,IF($AA$13=$CI$13,CN14,\"-\"))))","v":"TAI"},{"$f":"IF($AA$13=$AP$13,AV14,IF($AA$13=$BE$13,BK14,IF($AA$13=$BT$13,BZ14,IF($AA$13=$CI$13,CO14,\"-\"))))","v":"TAO"},{"$f":"IF($AA$13=$AP$13,AW14,IF($AA$13=$BE$13,BL14,IF($AA$13=$BT$13,CA14,IF($AA$13=$CI$13,CP14,\"-\"))))","v":"PS"},{"$f":"IF($AA$13=$AP$13,AX14,IF($AA$13=$BE$13,BM14,IF($AA$13=$BT$13,CB14,IF($AA$13=$CI$13,CQ14,\"-\"))))","v":"QW"},{"$f":"IF($AA$13=$AP$13,AY14,IF($AA$13=$BE$13,BN14,IF($AA$13=$BT$13,CC14,IF($AA$13=$CI$13,CR14,\"-\"))))","v":"VW"},{"$f":"IF($AA$13=$AP$13,AZ14,IF($AA$13=$BE$13,BO14,IF($AA$13=$BT$13,CD14,IF($AA$13=$CI$13,CS14,\"-\"))))","v":"TWI"},{"$f":"IF($AA$13=$AP$13,BA14,IF($AA$13=$BE$13,BP14,IF($AA$13=$BT$13,CE14,IF($AA$13=$CI$13,CT14,\"-\"))))","v":"TWO"},null,{"$f":"IF($AA$13=$AP$13,BC14,IF($AA$13=$BE$13,BR14,IF($AA$13=$BT$13,CG14,IF($AA$13=$CI$13,CV14,\"-\"))))","v":"DPW"},null,"q sensibel","S","QA","VA","DPA","TAI","TAO","PS","QW","VW","TWI","TWO",null,"DPW",null,"q sensibel","S","QA","VA","DPA","TAI","TAO","PS","QW","VW","TWI","TWO",null,"DPW",null,"q sensibel","S","QA","VA","DPA","TAI","TAO","PS","QW","VW","TWI","TWO",null,"DPW",null,"q sensibel","S","QA","VA","DPA","TAI","TAO","PS","QW","VW","TWI","TWO",null,"DPW"]
[null,"[m³/h]","[W/K]","[-]","[m³/h]","[W/K]","[-]","[m³/h]","[W/K]","[-]","[m³/h]","[W/K]","[-]","[m³/h]","[W/K]","[-]",null,null,null,null,null,null,null,null,null,null,"W/K",0,"m3/h","m/s","Pa","°C","°C","kW","l/h","m/s","°C","°C",null,"kPa",null,"W/K",null,"m3/h","m/s","Pa","°C","°C","kW","l/h","m/s","°C","°C",null,"kPa",null,"W/K",null,"m3/h","m/s","Pa","°C","°C","kW","l/h","m/s","°C","°C",null,"kPa",null,"W/K",null,"m3/h","m/s","Pa","°C","°C","kW","l/h","m/s","°C","°C",null,"kPa",null,"W/K",null,"m3/h","m/s","Pa","°C","°C","kW","l/h","m/s","°C","°C",null,"kPa"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,"S","QA","VA","DPA","TAI","TAO","QTOT","QW","VW","TWI","TWO",null,"DPW",null,null,"S","QA","VA","DPA","TAI","TAO","QTOT","QW","VW","TWI","TWO","GLI","DPW",null,null,"S","QA","VA","DPA","TAI","TAO","QTOT","QW","VW","TWI","TWO","GLI","DPW",null,null,"S","QA","VA","DPA","TAI","TAO","QTOT","QW","VW","TWI","TWO","GLI","DPW",null,null,"S","QA","VA","DPA","TAI","TAO","QTOT","QW","VW","TWI","TWO","GLI","DPW",null,"QA","VA","DPA","TAI","TAO","QTOT","QW","VW","TWI","TWO","GLI","DPW"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,"m3/h","m/s","Pa","°C","°C","kW","l/h","m/s","°C","°C",null,"kPa",null,null,null,"m3/h","m/s","Pa","°C","°C","kW","l/h","m/s","°C","°C","%","kPa",null,null,null,"m3/h","m/s","Pa","°C","°C","kW","l/h","m/s","°C","°C","%","kPa",null,null,null,"m3/h","m/s","Pa","°C","°C","kW","l/h","m/s","°C","°C","%","kPa",null,null,null,"m3/h","m/s","Pa","°C","°C","kW","l/h","m/s","°C","°C","%","kPa",null,"m3/h","m/s","Pa","°C","°C","kW","l/h","m/s","°C","°C","%","kPa"]
[null,{"$f":"AC18","v":10},{"$f":"$J$4*B18^6+$K$4*B18^5+$L$4*B18^4+$M$4*B18^3+$N$4*B18^2+$O$4*B18","v":2.5930331618745197},{"$f":"1/C18*C18","v":1},{"$f":"IF($B18*$F$3>$B$11,\"\",$B18*$F$3)","v":7.1951219512195124},{"$f":"IF(E18>$B$11,\"\",$J$3*E18^6+$K$3*E18^5+$L$3*E18^4+$M$3*E18^3+$N$3*E18^2+$O$3*E18)","v":1.6823398484457965},{"$f":"IF(E18>$B$11,\"\",1/$C18*F18)","v":0.64879226119484823},{"$f":"IF($B18*$F$4>$B$11,\"\",$B18*$F$4)","v":10},{"$f":"IF(H18>$B$11,\"\",$J$4*H18^6+$K$4*H18^5+$L$4*H18^4+$M$4*H18^3+$N$4*H18^2+$O$4*H18)","v":2.5930331618745197},{"$f":"IF(H18>$B$11,\"\",1/$C18*I18)","v":1},{"$f":"IF($B18*$F$5>$B$11,\"\",$B18*$F$5)","v":12.439024390243903},{"$f":"IF(K18>$B$11,\"\",$J$5*K18^6+$K$5*K18^5+$L$5*K18^4+$M$5*K18^3+$N$5*K18^2+$O$5*K18)","v":3.3832787441252803},{"$f":"IF(K18>$B$11,\"\",1/$C18*L18)","v":1.3047572217238776},{"$f":"IF($B18*$F$6>$B$11,\"\",$B18*$F$6)","v":14.634146341463413},{"$f":"IF(N18>$B$11,\"\",$J$6*N18^6+$K$6*N18^5+$L$6*N18^4+$M$6*N18^3+$N$6*N18^2+$O$6*N18)","v":4.1556752717192351},{"$f":"IF(N18>$B$11,\"\",1/$C18*O18)","v":1.6026309778140559},null,null,null,null,null,null,null,null,null,null,3.125,0,10,0.02,0,23,53.8,0.1,100,0.4,55,54.1,null,2,null,{"$f":"ABS(AW18/(AU18-AZ18)*1000)","v":3.125},null,10,0.03,0,23,52.8,0.1,100,0.4,55,54.1,0,1,null,{"$f":"ABS(BL18/(BJ18-BO18)*1000)","v":3.125},null,10,0.02,0,23,53.8,0.1,100,0.4,55,54.1,0,2,null,{"$f":"ABS(CA18/(BY18-CD18)*1000)","v":3.125},null,10,0.02,0,23,54.2,0.1,100,0.4,55,54.1,0,2,null,{"$f":"ABS(CP18/(CN18-CS18)*1000)","v":3.125},null,10,0.01,0,23,54.5,0.1,100,0.4,55,54.1,0,2,null,10,0.01,0,23,54.5,0.1,100,0.4,55,54.1,0,2]
[null,20,4.9576152481937665,{"$f":"1/C19*C19","v":1},14.390243902439025,{"$f":"IF(E19>$B$11,\"\",$J$3*E19^6+$K$3*E19^5+$L$3*E19^4+$M$3*E19^3+$N$3*E19^2+$O$3*E19)","v":3.2530018465576882},{"$f":"IF(E19>$B$11,\"\",1/$C19*F19)","v":0.6561626273323391},20,{"$f":"IF(H19>$B$11,\"\",$J$4*H19^6+$K$4*H19^5+$L$4*H19^4+$M$4*H19^3+$N$4*H19^2+$O$4*H19)","v":4.9576152481937665},{"$f":"IF(H19>$B$11,\"\",1/$C19*I19)","v":1},24.878048780487806,6.4172627654752255,1.2944253323840047,29.268292682926827,{"$f":"IF(N19>$B$11,\"\",$J$6*N19^6+$K$6*N19^5+$L$6*N19^4+$M$6*N19^3+$N$6*N19^2+$O$6*N19)","v":7.8181445383562798},1.5769970332418808,null,null,null,null,null,null,null,null,null,null,5.9375,0,20,0.04,0,23,51.2,0.19,100,0.4,55,53.4,null,2,null,{"$f":"ABS(AW19/(AU19-AZ19)*1000)","v":5.625},null,20,0.05,0,23,49.4,0.18,100,0.4,55,53.5,0,1,null,{"$f":"ABS(BL19/(BJ19-BO19)*1000)","v":5.9375},null,20,0.04,0,23,51.2,0.19,100,0.4,55,53.4,0,2,null,{"$f":"ABS(CA19/(BY19-CD19)*1000)","v":5.9375},null,20,0.03,0,23,52.2,0.19,100,0.4,55,53.3,0,2,null,{"$f":"ABS(CP19/(CN19-CS19)*1000)","v":6.25},null,20,0.03,0,23,52.8,0.2,100,0.4,55,53.3,0,2,null,20,0.03,0,23,52.8,0.2,100,0.4,55,53.3,0,2]
[null,30,7.1124051475024412,1,21.585365853658537,4.7186533821064369,0.66343990313367018,30,7.1124051475024412,1,37.31707317073171,9.1362689919585343,1.2845540717216852,43.90243902439024,11.044279255566046,1.5528191977989756,null,null,null,null,null,null,null,null,null,null,8.125,0,30,0.06,0,23,48.8,0.26,100,0.4,55,52.7,null,2,null,7.5,null,30,0.08,0,23,46.7,0.24,100,0.4,55,52.9,0,1,null,8.125,null,30,0.06,0,23,48.8,0.26,100,0.4,55,52.7,0,2,null,8.4375,null,30,0.05,0,23,50.1,0.27,100,0.4,55,52.6,0,2,null,8.75,null,30,0.04,0,23,50.9,0.28000000000000003,100,0.4,55,52.6,0,2,null,30,0.04,0,23,50.9,0.28000000000000003,100,0.4,55,52.6,0,2]
[null,40,9.0749345184401147,1,28.780487804878049,6.0856716099006105,0.67060226137550938,40,9.0749345184401147,1,49.756097560975611,11.57207809807981,1.2751693221108695,58.536585365853654,13.885958420095614,1.5301442001459713,null,null,null,null,null,null,null,null,null,null,10,0,40,0.08,0,23,46.8,0.32,100,0.4,55,52.2,null,2,null,9.0625,null,40,0.11,0,23,44.6,0.28999999999999998,100,0.4,55,52.5,0,1,null,10,null,40,0.08,0,23,46.8,0.32,100,0.4,55,52.2,0,2,null,10.625,null,40,0.06,0,23,48.2,0.34,100,0.4,55,52.1,0,2,null,10.9375,null,40,0.05,0,23,49.2,0.35,100,0.4,55,51.9,0,2,null,40,0.05,0,23,49.2,0.35,100,0.4,55,51.9,0,2]
[null,50,10.861651427363256,1,35.975609756097562,7.3601514840579938,0.67762729574582969,50,10.861651427363256,1,62.195121951219512,13.754055864512665,1.2662950893326137,73.170731707317074,16.390354322318789,1.5090112614944839,null,null,null,null,null,null,null,null,null,null,11.5625,0,50,0.1,0,23,45.2,0.37,100,0.4,55,51.8,null,2,null,10.3125,null,50,0.13,0,23,42.9,0.33,100,0.4,55,52.1,0,1,null,11.5625,null,50,0.1,0,23,45.2,0.37,100,0.4,55,51.8,0,2,null,12.1875,null,50,0.08,0,23,46.6,0.39,100,0.4,55,51.6,0,2,null,12.8125,null,50,7.0000000000000007E-2,0,23,47.7,0.41,100,0.4,55,51.4,0,2,null,50,7.0000000000000007E-2,0,23,47.7,0.41,100,0.4,55,51.4,0,2]
[null,60,12.48796317434611,1,43.170731707317074,8.5479136840551071,0.6844922238091633,60,12.48796317434611,1,74.634146341463421,15.709271728104655,1.2579530791999807,87.804878048780481,18.600210347140646,1.4894510888173389,null,null,null,null,null,null,null,null,null,null,13.125,0,60,0.12,0,23,43.8,0.42,100,0.4,55,51.4,null,2,null,11.5625,null,60,0.16,0,23,41.5,0.37,100,0.4,55,51.8,0,1,null,13.125,null,60,0.12,0,23,43.8,0.42,100,0.4,55,51.4,0,2,null,14.0625,null,60,0.09,0,23,45.3,0.45,100,0.4,55,51.1,0,2,null,14.6875,null,60,0.08,0,23,46.4,0.47,100,0.4,55,50.9,0,2,null,60,0.08,0,23,46.4,0.47,100,0.4,55,50.9,0,2]
[null,70,13.968278307560411,0.99999999999999989,50.365853658536587,9.6545124345548299,0.69117411766697612,70,13.968278307560411,0.99999999999999989,87.073170731707322,17.46261452231408,1.2501622703824808,102.4390243902439,20.55411082327204,1.4714849153704941,null,null,null,null,null,null,null,null,null,null,14.375,0,70,0.14000000000000001,0,23,42.6,0.46,100,0.4,55,51,null,2,null,12.5,null,70,0.19,0,23,40.299999999999997,0.4,100,0.4,55,51.5,0,1,null,14.375,null,70,0.14000000000000001,0,23,42.6,0.46,100,0.4,55,51,0,2,null,15.3125,null,70,0.11,0,23,44.1,0.49,100,0.4,55,50.7,0,2,null,16.25,null,70,0.09,0,23,45.2,0.52,100,0.4,55,50.5,0,2,null,70,0.09,0,23,45.2,0.52,100,0.4,55,50.5,0,2]
[null,80,15.316047826033975,0.99999999999999989,57.560975609756099,10.685243219012118,0.69765016017053116,80,15.316047826033975,0.99999999999999989,99.512195121951223,19.036905408078674,1.2429384932919865,117.07317073170731,22.286742920874111,1.455123617660129,null,null,null,null,null,null,null,null,null,null,15.3125,0,80,0.15,0,23,41.5,0.49,100,0.4,55,50.7,null,2,null,13.75,null,80,0.22,0,23,39.299999999999997,0.44,100,0.4,55,51.2,0,1,null,15.3125,null,80,0.15,0,23,41.5,0.49,100,0.4,55,50.7,0,2,null,16.5625,null,80,0.12,0,23,43,0.53,100,0.4,55,50.3,0,2,null,17.5,null,80,0.11,0,23,44.1,0.56000000000000005,100,0.4,55,50.1,0,2,null,80,0.11,0,23,44.1,0.56000000000000005,100,0.4,55,50.1,0,2]
[null,90,16.543805570788102,1,64.756097560975604,11.645150387057839,0.70389792343909274,90,16.543805570788102,1,111.95121951219512,20.453007995116096,1.2362940260390023,131.70731707317074,23.829150597572728,1.4403669394935699,null,null,null,null,null,null,null,null,null,null,16.5625,0,90,0.17,0,23,40.6,0.53,100,0.4,55,50.4,null,2,null,14.375,null,90,0.24,1,23,38.5,0.46,100,0.4,55,51,0,1,null,16.5625,null,90,0.17,0,23,40.6,0.53,100,0.4,55,50.4,0,2,null,17.8125,null,90,0.14000000000000001,0,23,42.1,0.56999999999999995,100,0.4,55,50,0,2,null,19.0625,null,90,0.12,0,23,43.2,0.61,100,0.4,55,49.7,0,2,null,90,0.12,0,23,43.2,0.61,100,0.4,55,49.7,0,2]
[null,100,17.66320780435386,1,71.951219512195124,12.539034655660705,0.70989566530321402,100,17.66320780435386,1,124.39024390243902,21.729935653656344,1.2302372193288733,146.34146341463415,25.208980592842977,1.4272028542080073,null,null,null,null,null,null,null,null,null,null,17.5,0,100,0.19,0,23,39.799999999999997,0.56000000000000005,100,0.4,55,50.1,null,2,null,15.3125,null,100,0.27,1,23,37.700000000000003,0.49,100,0.4,55,50.7,0,1,null,17.5,null,100,0.19,0,23,39.799999999999997,0.56000000000000005,100,0.4,55,50.1,0,2,null,19.0625,null,100,0.16,0,23,41.2,0.61,100,0.4,55,49.7,0,2,null,20,null,100,0.13,0,23,42.3,0.64,100,0.4,55,49.4,0,2,null,100,0.13,0,23,42.3,0.64,100,0.4,55,49.4,0,2]
[null,110,18.685071978667203,1,79.146341463414629,13.371460504067279,0.71562263818590111,110,18.685071978667203,1,136.82926829268294,22.884956016605962,1.2247721626512211,160.97560975609755,26.450720470763567,1.4156070953840814,null,null,null,null,null,null,null,null,null,null,18.4375,0,110,0.21,0,23,39.1,0.59,100,0.4,55,49.9,null,2,null,15.9375,null,110,0.3,1,23,37,0.51,100,0.4,55,50.5,0,1,null,18.4375,null,110,0.21,0,23,39.1,0.59,100,0.4,55,49.9,0,2,null,20,null,110,0.17,0,23,40.5,0.64,100,0.4,55,49.4,0,2,null,21.25,null,110,0.15,0,23,41.6,0.68,100,0.4,55,49.1,0,2,null,110,0.15,0,23,41.6,0.68,100,0.4,55,49.1,0,2]
[null,120,19.619414691342946,1,86.341463414634148,14.146763462520161,0.72105940391597978,120,19.619414691342946,1,149.26829268292684,23.933692672144151,1.2198984041407146,175.60975609756096,27.575928711141245,1.4055428841773301,null,null,null,null,null,null,null,null,null,null,19.375,0,120,0.23,0,23,38.4,0.62,100,0.4,55,49.6,null,2,null,16.875,null,120,0.32,1,23,36.4,0.54,100,0.4,55,50.3,0,1,null,19.375,null,120,0.23,0,23,38.4,0.62,100,0.4,55,49.6,0,2,null,20.9375,null,120,0.19,0,23,39.799999999999997,0.67,100,0.4,55,49.1,0,2,null,22.1875,null,120,0.16,0,23,40.9,0.71,100,0.4,55,48.8,0,2,null,120,0.16,0,23,40.9,0.71,100,0.4,55,48.8,0,2]
[null,130,20.475488830327546,0.99999999999999989,93.536585365853654,14.86905729475418,0.72618814710448698,130,20.475488830327546,0.99999999999999989,161.70731707317074,24.890224046750717,1.2156107359881061,190.2439024390244,28.603456849005159,1.3969608777612559,null,null,null,null,null,null,null,null,null,null,20,0,130,0.25,1,23,37.799999999999997,0.64,100,0.4,55,49.4,null,2,null,17.5,null,130,0.35,1,23,35.9,0.56000000000000005,100,0.4,55,50.1,0,1,null,20,null,130,0.25,1,23,37.799999999999997,0.64,100,0.4,55,49.4,0,2,null,21.875,null,130,0.2,0,23,39.200000000000003,0.7,100,0.4,55,48.9,0,2,null,23.4375,null,130,0.17,0,23,40.200000000000003,0.75,100,0.4,55,48.5,0,2,null,130,0.17,0,23,40.200000000000003,0.75,100,0.4,55,48.5,0,2]
[null,140,21.261819906930846,0.99999999999999989,100.73170731707317,15.542241074270768,0.73099297907251892,140,21.261819906930846,0.99999999999999989,174.14634146341464,25.767179478665902,1.2118990562170275,204.8780487804878,29.549663662471254,1.3897993582778285,null,null,null,null,null,null,null,null,null,null,20.9375,0,140,0.27,1,23,37.299999999999997,0.67,100,0.4,55,49.2,null,2,null,18.125,null,140,0.38,1,23,35.4,0.57999999999999996,100,0.4,55,50,0,1,null,20.9375,null,140,0.27,1,23,37.299999999999997,0.67,100,0.4,55,49.2,0,2,null,22.8125,null,140,0.22,0,23,38.6,0.73,100,0.4,55,48.6,0,2,null,24.375,null,140,0.19,0,23,39.6,0.78,100,0.4,55,48.2,0,2,null,140,0.19,0,23,39.6,0.78,100,0.4,55,48.2,0,2]
[null,150,21.986241577236505,1,107.92682926829268,16.170006154390403,0.73546022395806154,150,21.986241577236505,1,186.58536585365854,26.575832481782026,1.2087483160058317,219.51219512195121,30.428621408976575,1.3839846752380318,null,null,null,null,null,null,null,null,null,null,21.5625,0,150,0.28999999999999998,1,23,36.799999999999997,0.69,100,0.4,55,49,null,2,null,18.75,null,150,0.4,1,23,34.9,0.6,100,0.4,55,49.8,0,1,null,21.5625,null,150,0.28999999999999998,1,23,36.799999999999997,0.69,100,0.4,55,49,0,2,null,23.75,null,150,0.23,0,23,38.1,0.76,100,0.4,55,48.4,0,2,null,25.3125,null,150,0.2,0,23,39.1,0.81,100,0.4,55,48,0,2,null,150,0.2,0,23,39.1,0.81,100,0.4,55,48,0,2]
[null,160,22.655930351891438,1,115.1219512195122,16.755843032083142,0.73957867859901305,160,22.655930351891438,1,199.02439024390245,27.326191199967017,1.2061385595531582,234.14634146341461,31.25231410988367,1.3794319467121137,null,null,null,null,null,null,null,null,null,null,22.1875,0,160,0.31,1,23,36.299999999999997,0.71,100,0.4,55,48.8,null,2,null,19.0625,null,160,0.43,2,23,34.5,0.61,100,0.4,55,49.6,0,1,null,22.1875,null,160,0.31,1,23,36.299999999999997,0.71,100,0.4,55,48.8,0,2,null,24.375,null,160,0.25,1,23,37.6,0.78,100,0.4,55,48.2,0,2,null,25.9375,null,160,0.21,0,23,38.6,0.83,100,0.4,55,47.7,0,2,null,160,0.21,0,23,38.6,0.83,100,0.4,55,47.7,0,2]
[null,170,23.277439494273963,1,122.3170731707317,17.303048105577304,0.74333983812238869,170,23.277439494273963,1,211.46341463414635,28.027086051819857,1.2040450608287163,248.78048780487805,32.030827883454734,1.3760460162009669,null,null,null,null,null,null,null,null,null,null,22.8125,0,170,0.33,1,23,35.9,0.73,100,0.4,55,48.6,null,2,null,19.6875,null,170,0.46,2,23,34.1,0.63,100,0.4,55,49.5,0,1,null,22.8125,null,170,0.33,1,23,35.9,0.73,100,0.4,55,48.6,0,2,null,25,null,170,0.26,1,23,37.200000000000003,0.8,100,0.4,55,48,0,2,null,26.875,null,170,0.22,0,23,38.1,0.86,100,0.4,55,47.5,0,2,null,170,0.22,0,23,38.1,0.86,100,0.4,55,47.5,0,2]
[null,180,23.856732107040898,1,129.51219512195121,17.814730325746197,0.74673807987676943,180,23.856732107040898,1,223.90243902439025,28.686254565857695,1.2024385585229189,263.41463414634148,32.772533326196019,1.3737226531761144,null,null,null,null,null,null,null,null,null,null,23.4375,0,180,0.35,1,23,35.5,0.75,100,0.4,55,48.4,null,2,null,20.3125,null,180,0.48,2,23,33.799999999999997,0.65,100,0.4,55,49.4,0,1,null,23.4375,null,180,0.35,1,23,35.5,0.75,100,0.4,55,48.4,0,2,null,25.9375,null,180,0.28000000000000003,1,23,36.799999999999997,0.83,100,0.4,55,47.8,0,2,null,27.5,null,180,0.24,1,23,37.700000000000003,0.88,100,0.4,55,47.3,0,2,null,180,0.24,1,23,37.700000000000003,0.88,100,0.4,55,47.3,0,2]
[null,190,24.399213407053512,1,136.70731707317071,18.293817741273003,0.74977079941374203,190,24.399213407053512,1,236.34146341463415,29.310423406135129,1.201285587250196,278.04878048780489,33.484259942572038,1.3723499763681788,null,null,null,null,null,null,null,null,null,null,24.0625,0,190,0.37,1,23,35.200000000000003,0.77,100,0.4,55,48.3,null,2,null,20.625,null,190,0.51,2,23,33.5,0.66,100,0.4,55,49.2,0,1,null,24.0625,null,190,0.37,1,23,35.200000000000003,0.77,100,0.4,55,48.3,0,2,null,26.5625,null,190,0.3,1,23,36.4,0.85,100,0.4,55,47.6,0,2,null,28.4375,null,190,0.25,1,23,37.299999999999997,0.91,100,0.4,55,47.1,0,2,null,190,0.25,1,23,37.299999999999997,0.91,100,0.4,55,47.1,0,2]
[null,200,24.909762188682201,1,143.90243902439025,18.743063937593732,0.7524384936163574,200,24.909762188682201,1,248.78048780487805,29.905387588294971,1.2005488997354838,292.6829268292683,34.171462623089809,1.3718100704556577,null,null,null,null,null,null,null,null,null,null,24.6875,0,200,0.39,1,23,34.799999999999997,0.79,100,0.4,55,48.1,null,2,null,21.25,null,200,0.54,2,23,33.200000000000003,0.68,100,0.4,55,49.1,0,1,null,24.6875,null,200,0.39,1,23,34.799999999999997,0.79,100,0.4,55,48.1,0,2,null,27.1875,null,200,0.31,1,23,36,0.87,100,0.4,55,47.4,0,2,null,29.0625,null,200,0.26,1,23,36.9,0.93,100,0.4,55,46.9,0,2,null,200,0.26,1,23,36.9,0.93,100,0.4,55,46.9,0,2]
[null,210,25.392761475490168,1,151.09756097560975,19.165054369618268,0.75474478772688569,210,25.392761475490168,1,261.21951219512192,30.476086886051235,1.2001879714999741,307.3170731707317,34.838380170753013,1.3719807593349007,null,null,null,null,null,null,null,null,null,null,25.3125,0,210,0.41,1,23,34.5,0.81,100,0.4,55,48,null,2,null,21.5625,null,210,0.56000000000000005,2,23,32.9,0.69,100,0.4,55,49,0,1,null,25.3125,null,210,0.41,1,23,34.5,0.81,100,0.4,55,48,0,2,null,27.8125,null,210,0.33,1,23,35.700000000000003,0.89,100,0.4,55,47.3,0,2,null,29.6875,null,210,0.28000000000000003,1,23,36.6,0.95,100,0.4,55,46.7,0,2,null,210,0.28000000000000003,1,23,36.6,0.95,100,0.4,55,46.7,0,2]
[null,220,25.852128360295843,0.99999999999999989,158.29268292682926,19.562212588229574,0.75669640486055934,220,25.852128360295843,0.99999999999999989,273.65853658536588,31.026679428103698,1.200159576638766,321.95121951219511,35.488185875886259,1.3727374930719298,null,null,null,null,null,null,null,null,null,null,25.625,0,220,0.43,1,23,34.200000000000003,0.82,100,0.4,55,47.8,null,2,null,22.1875,null,220,0.59,3,23,32.6,0.71,100,0.4,55,48.8,0,1,null,25.625,null,220,0.43,1,23,34.200000000000003,0.82,100,0.4,55,47.8,0,2,null,28.4375,null,220,0.34,1,23,35.4,0.91,100,0.4,55,47.1,0,2,null,30.3125,null,220,0.28999999999999998,1,23,36.200000000000003,0.97,100,0.4,55,46.5,0,2,null,220,0.28999999999999998,1,23,36.200000000000003,0.97,100,0.4,55,46.5,0,2]
[null,230,26.291343033614218,1,165.48780487804876,19.936806360560976,0.7583030785103374,230,26.291343033614218,1,286.09756097560978,31.560612485484484,1.2004184208137771,336.58536585365852,36.123130139329206,1.3739553012999288,null,null,null,null,null,null,null,null,null,null,26.25,0,230,0.45,2,23,33.9,0.84,100,0.4,55,47.7,null,2,null,22.5,null,230,0.62,3,23,32.4,0.72,100,0.4,55,48.7,0,1,null,26.25,null,230,0.45,2,23,33.9,0.84,100,0.4,55,47.7,0,2,null,28.75,null,230,0.36,1,23,35,0.92,100,0.4,55,46.9,0,2,null,30.9375,null,230,0.3,1,23,35.9,0.99,100,0.4,55,46.4,0,2,null,230,0.3,1,23,35.9,0.99,100,0.4,55,46.4,0,2]
[null,240,26.713477000476992,1,172.6829268292683,20.29095368405148,0.75957741044676319,240,26.713477000476992,1,298.53658536585368,32.080690449336444,1.2009178157064173,351.21951219512192,36.744675144000709,1.3755107634751029,null,null,null,null,null,null,null,null,null,null,26.5625,0,240,0.46,2,23,33.700000000000003,0.85,100,0.4,55,47.5,null,2,null,22.8125,null,240,0.65,3,23,32.1,0.73,100,0.4,55,48.6,0,1,null,26.5625,null,240,0.46,2,23,33.700000000000003,0.85,100,0.4,55,47.5,0,2,null,29.375,null,240,0.37,1,23,34.799999999999997,0.94,100,0.4,55,46.8,0,2,null,31.5625,null,240,0.32,1,23,35.6,1.01,100,0.4,55,46.2,0,2,null,240,0.32,1,23,35.6,1.01,100,0.4,55,46.2,0,2]
[null,250,27.121220485631554,1,179.8780487804878,20.626628694279297,0.7605346781944049,250,27.121220485631554,1,310.97560975609758,32.589139999123404,1.2016103779838623,365.85365853658539,37.353621574832843,1.3772839461491886,null,null,null,null,null,null,null,null,null,null,27.1875,0,250,0.48,2,23,33.4,0.87,100,0.4,55,47.4,null,2,null,23.125,null,250,0.67,3,23,31.9,0.74,100,0.4,55,48.5,0,1,null,27.1875,null,250,0.48,2,23,33.4,0.87,100,0.4,55,47.4,0,2,null,30,null,250,0.39,1,23,34.5,0.96,100,0.4,55,46.6,0,2,null,32.1875,null,250,0.33,1,23,35.299999999999997,1.03,100,0.4,55,46,0,2,null,250,0.33,1,23,35.299999999999997,1.03,100,0.4,55,46,0,2]
[null,260,27.516909027118885,0.99999999999999989,187.07317073170731,20.945667466573433,0.7611925978288745,260,27.516909027118885,0.99999999999999989,323.41463414634148,33.087672461272277,1.2024487353816959,380.48780487804879,37.950227387075302,1.3791602592309335,null,null,null,null,null,null,null,null,null,null,27.5,0,260,0.5,2,23,33.200000000000003,0.88,100,0.4,55,47.3,null,2,null,23.75,null,260,0.7,4,23,31.7,0.76,100,0.4,55,48.4,0,1,null,27.5,null,260,0.5,2,23,33.200000000000003,0.88,100,0.4,55,47.3,0,2,null,30.3125,null,260,0.4,1,23,34.200000000000003,0.97,100,0.4,55,46.5,0,2,null,32.5,null,260,0.34,1,23,35.1,1.04,100,0.4,55,45.9,0,2,null,260,0.34,1,23,35.1,1.04,100,0.4,55,45.9,0,2]
[null,270,27.902549258230238,1,194.26829268292681,21.249773711403339,0.76157104910890638,270,27.902549258230238,1,335.85365853658539,33.577543358247041,1.2033862227962158,395.1219512195122,38.53431862296911,1.3810321869283282,null,"Beispiel: BG600- heizen",null,null,null,null,null,null,null,null,28.125,0,270,0.52,2,23,33,0.9,100,0.4,55,47.2,null,2,null,24.0625,null,270,0.73,4,23,31.5,0.77,100,0.4,55,48.3,0,1,null,28.125,null,270,0.52,2,23,33,0.9,100,0.4,55,47.2,0,2,null,30.9375,null,270,0.42,1,23,34,0.99,100,0.4,55,46.4,0,2,null,33.125,null,270,0.36,1,23,34.799999999999997,1.06,100,0.4,55,45.7,0,2,null,270,0.36,1,23,34.799999999999997,1.06,100,0.4,55,45.7,0,2]
[null,280,28.27984387784268,1,201.46341463414635,21.540524363546748,0.76169177088080742,280,28.27984387784268,1,348.29268292682929,34.059609148054548,1.2043775522657794,409.7560975609756,39.105392276790852,1.3828008544074748,null,null,null,null,null,null,null,null,null,null,28.4375,0,280,0.54,2,23,32.799999999999997,0.91,100,0.4,55,47.1,null,2,null,24.375,null,280,0.75,4,23,31.3,0.78,100,0.4,55,48.2,0,1,null,28.4375,null,280,0.54,2,23,32.799999999999997,0.91,100,0.4,55,47.1,0,2,null,31.5625,null,280,0.44,2,23,33.799999999999997,1.01,100,0.4,55,46.2,0,2,null,33.75,null,280,0.37,1,23,34.6,1.08,100,0.4,55,45.6,0,2,null,280,0.37,1,23,34.6,1.08,100,0.4,55,45.6,0,2]
[null,290,28.650215809133492,1,208.65853658536585,21.81937506503553,0.76157803523698631,290,28.650215809133492,1,360.73170731707319,34.534381154182128,1.2053794423137576,424.39024390243901,39.662711208266785,1.384377397800354,null,null,null,null,null,null,null,null,null,null,{"$f":"IF($AA$13=$AP$13,AP46,IF($AA$13=$BE$13,BE46,IF($AA$13=$BT$13,BT46,IF($AA$13=$CI$13,CI46,\"-\"))))","v":28.75},{"$f":"IF($AA$13=$AP$13,AQ46,IF($AA$13=$BE$13,BF46,IF($AA$13=$BT$13,BU46,IF($AA$13=$CI$13,CJ46,\"-\"))))","v":0},{"$f":"IF($AA$13=$AP$13,AR46,IF($AA$13=$BE$13,BG46,IF($AA$13=$BT$13,BV46,IF($AA$13=$CI$13,CK46,\"-\"))))","v":290},{"$f":"IF($AA$13=$AP$13,AS46,IF($AA$13=$BE$13,BH46,IF($AA$13=$BT$13,BW46,IF($AA$13=$CI$13,CL46,\"-\"))))","v":0.56000000000000005},{"$f":"IF($AA$13=$AP$13,AT46,IF($AA$13=$BE$13,BI46,IF($AA$13=$BT$13,BX46,IF($AA$13=$CI$13,CM46,\"-\"))))","v":2},{"$f":"IF($AA$13=$AP$13,AU46,IF($AA$13=$BE$13,BJ46,IF($AA$13=$BT$13,BY46,IF($AA$13=$CI$13,CN46,\"-\"))))","v":23},{"$f":"IF($AA$13=$AP$13,AV46,IF($AA$13=$BE$13,BK46,IF($AA$13=$BT$13,BZ46,IF($AA$13=$CI$13,CO46,\"-\"))))","v":32.6},{"$f":"IF($AA$13=$AP$13,AW46,IF($AA$13=$BE$13,BL46,IF($AA$13=$BT$13,CA46,IF($AA$13=$CI$13,CP46,\"-\"))))","v":0.92},{"$f":"IF($AA$13=$AP$13,AX46,IF($AA$13=$BE$13,BM46,IF($AA$13=$BT$13,CB46,IF($AA$13=$CI$13,CQ46,\"-\"))))","v":100},{"$f":"IF($AA$13=$AP$13,AY46,IF($AA$13=$BE$13,BN46,IF($AA$13=$BT$13,CC46,IF($AA$13=$CI$13,CR46,\"-\"))))","v":0.4},{"$f":"IF($AA$13=$AP$13,AZ46,IF($AA$13=$BE$13,BO46,IF($AA$13=$BT$13,CD46,IF($AA$13=$CI$13,CS46,\"-\"))))","v":55},{"$f":"IF($AA$13=$AP$13,BA46,IF($AA$13=$BE$13,BP46,IF($AA$13=$BT$13,CE46,IF($AA$13=$CI$13,CT46,\"-\"))))","v":46.9},null,{"$f":"IF($AA$13=$AP$13,BC46,IF($AA$13=$BE$13,BR46,IF($AA$13=$BT$13,CG46,IF($AA$13=$CI$13,CV46,\"-\"))))","v":2},null,24.6875,null,290,0.78,5,23,31.2,0.79,100,0.4,55,48.1,0,1,null,28.75,null,290,0.56000000000000005,2,23,32.6,0.92,100,0.4,55,46.9,0,2,null,31.875,null,290,0.45,2,23,33.6,1.02,100,0.4,55,46.1,0,2,null,34.0625,null,290,0.38,1,23,34.299999999999997,1.0900000000000001,100,0.4,55,45.5,0,2,null,290,0.38,1,23,34.299999999999997,1.0900000000000001,100,0.4,55,45.5,0,2]
[null,300,29.01483154667347,1,215.85365853658536,22.087665541879705,0.76125430907118408,300,29.01483154667347,1,373.17073170731709,35.002076685967353,1.2063511942043419,439.02439024390242,40.205391104356636,1.3856841126126118,null,null,null,null,null,null,null,null,null,null,29.375,0,300,0.57999999999999996,3,23,32.4,0.94,100,0.4,55,46.8,null,2,null,25,null,300,0.81,5,23,31,0.8,100,0.4,55,48,0,1,null,29.375,null,300,0.57999999999999996,3,23,32.4,0.94,100,0.4,55,46.8,0,2,null,32.1875,null,300,0.47,2,23,33.299999999999997,1.03,100,0.4,55,46,0,2,null,34.6875,null,300,0.4,1,23,34.1,1.1100000000000001,100,0.4,55,45.3,0,2,null,300,0.4,1,23,34.1,1.1100000000000001,100,0.4,55,45.3,0,2]
[null,310,29.374623691898989,1,223.04878048780486,22.346624874569528,0.76074591146957704,310,29.374623691898989,1,385.60975609756099,35.46266734939914,1.207255205082989,453.65853658536582,40.732479489407922,1.3866553633720671,null,null,null,null,null,null,null,null,null,null,29.6875,0,310,0.6,3,23,32.200000000000003,0.95,100,0.4,55,46.7,null,2,null,25.3125,null,310,0.83,5,23,30.8,0.81,100,0.4,55,47.9,0,1,null,29.6875,null,310,0.6,3,23,32.200000000000003,0.95,100,0.4,55,46.7,0,2,null,32.8125,null,310,0.48,2,23,33.1,1.05,100,0.4,55,45.9,0,2,null,35.3125,null,310,0.41,1,23,33.9,1.1299999999999999,100,0.4,55,45.2,0,2,null,310,0.41,1,23,33.9,1.1299999999999999,100,0.4,55,45.2,0,2]
[null,320,29.730312676962868,0.99999999999999989,230.2439024390244,22.597376662355749,0.76007867484911384,320,29.730312676962868,0.99999999999999989,398.04878048780489,35.915924548351143,1.2080574105828803,468.29268292682923,41.243026783679397,1.3872382450803278,null,null,null,null,null,null,null,null,null,null,30,0,320,0.62,3,23,32,0.96,100,0.4,55,46.6,null,2,null,25.625,null,320,0.86,5,23,30.7,0.82,100,0.4,55,47.9,0,1,null,30,null,320,0.62,3,23,32,0.96,100,0.4,55,46.6,0,2,null,33.125,null,320,0.5,2,23,33,1.06,100,0.4,55,45.8,0,2,null,35.625,null,320,0.42,1,23,33.700000000000003,1.1399999999999999,100,0.4,55,45.1,0,2,null,320,0.42,1,23,33.700000000000003,1.1399999999999999,100,0.4,55,45.1,0,2]
[null,{"$f":"AC50","v":330},30.082427676964357,1,{"$f":"IF($B50*$F$3>$B$11,\"\",$B50*$F$3)","v":237.4390243902439},22.840944081307839,0.75927861695810905,{"$f":"IF($B50*$F$4>$B$11,\"\",$B50*$F$4)","v":330},30.082427676964357,1,{"$f":"IF($B50*$F$5>$B$11,\"\",$B50*$F$5)","v":410.48780487804879},36.361462176247116,1.2087276521266577,{"$f":"IF($B50*$F$6>$B$11,\"\",$B50*$F$6)","v":482.92682926829269},41.736149410235527,1.3873929942893211,null,null,null,null,null,null,null,null,null,null,30.3125,0,330,0.64,3,23,31.8,0.97,100,0.4,55,46.5,null,2,null,25.9375,null,330,0.89,6,23,30.5,0.83,100,0.4,55,47.8,0,1,null,30.3125,null,330,0.64,3,23,31.8,0.97,100,0.4,55,46.5,0,2,null,33.4375,null,330,0.51,2,23,32.799999999999997,1.07,100,0.4,55,45.6,0,2,null,35.9375,null,330,0.44,2,23,33.5,1.1499999999999999,100,0.4,55,44.9,0,2,null,330,0.44,2,23,33.5,1.1499999999999999,100,0.4,55,44.9,0,2]
[null,340,30.431326710557656,1,244.63414634146341,23.078254836150442,0.75837162985548756,340,30.431326710557656,1,422.92682926829269,36.798776498157423,1.209239966701507,497.5609756097561,42.211084950210136,1.3870931540939253,null,null,null,null,null,null,null,null,null,null,30.625,0,340,0.66,3,23,31.7,0.98,100,0.4,55,46.4,null,2,null,26.25,null,340,0.91,6,23,30.4,0.84,100,0.4,55,47.7,0,1,null,30.625,null,340,0.66,3,23,31.7,0.98,100,0.4,55,46.4,0,2,null,34.0625,null,340,0.53,2,23,32.6,1.0900000000000001,100,0.4,55,45.5,0,2,null,36.5625,null,340,0.45,2,23,33.299999999999997,1.17,100,0.4,55,44.8,0,2,null,340,0.45,2,23,33.299999999999997,1.17,100,0.4,55,44.8,0,2]
[null,350,30.777215928939285,1,251.82926829268291,23.310146005877897,0.75738319085449735,350,30.777215928939285,1,435.36585365853659,37.227283223327987,1.2095727992187824,512.19512195121945,42.667239346440425,1.3863255027665176,null,null,null,null,null,null,null,null,null,null,30.9375,0,350,0.68,3,23,31.5,0.99,100,0.4,55,46.3,null,2,null,26.5625,null,350,0.94,6,23,30.3,0.85,100,0.4,55,47.6,0,1,null,30.9375,null,350,0.68,3,23,31.5,0.99,100,0.4,55,46.3,0,2,null,34.375,null,350,0.54,2,23,32.4,1.1000000000000001,100,0.4,55,45.4,0,2,null,36.875,null,350,0.46,2,23,33.1,1.18,100,0.4,55,44.7,0,2,null,350,0.46,2,23,33.1,1.18,100,0.4,55,44.7,0,2]
[null,360,31.120168093214843,1,259.02439024390242,23.537368783146825,0.75633809922378592,360,31.120168093214843,1,447.80487804878049,37.646351768141329,1.2097091395964983,526.82926829268297,43.104226155470684,1.3850897600025731,null,null,null,null,null,null,null,null,null,null,31.25,0,360,0.7,4,23,31.4,1,100,0.4,55,46.2,null,2,null,26.875,null,360,0.97,7,23,30.1,0.86,100,0.4,55,47.5,0,1,null,31.25,null,360,0.7,4,23,31.4,1,100,0.4,55,46.2,0,2,null,34.6875,null,360,0.56000000000000005,2,23,32.299999999999997,1.1100000000000001,100,0.4,55,45.3,0,2,null,37.1875,null,360,0.48,2,23,33,1.19,100,0.4,55,44.6,0,2,null,360,0.48,2,23,33,1.19,100,0.4,55,44.6,0,2]
[null,370,31.460140240143758,1,266.21951219512192,23.76059310744693,0.75526024124736568,370,31.460140240143758,1,460.2439024390244,38.055336709508794,1.2096365883629927,541.46341463414637,43.521897847926397,1.3833980877298062,null,null,null,null,null,null,null,null,null,null,31.5625,0,370,0.72,4,23,31.2,1.01,100,0.4,55,46.1,null,2,null,26.875,null,370,1,7,23,30,0.86,100,0.4,55,47.5,0,1,null,31.5625,null,370,0.72,4,23,31.2,1.01,100,0.4,55,46.1,0,2,null,35,null,370,0.57999999999999996,3,23,32.1,1.1200000000000001,100,0.4,55,45.2,0,2,null,37.8125,null,370,0.49,2,23,32.799999999999997,1.21,100,0.4,55,44.5,0,2,null,370,0.49,2,23,32.799999999999997,1.21,100,0.4,55,44.5,0,2]
[null,380,31.796990536263507,1,273.41463414634143,23.980412192049641,0.75417238510986462,380,31.796990536263507,1,472.6829268292683,38.453606428694968,1.2093473558398489,556.09756097560978,43.920369157257596,1.3812744041662604,null,null,null,null,null,null,null,null,null,null,32.1875,0,380,0.74,4,23,31.1,1.03,100,0.4,55,46.1,null,2,null,27.1875,null,380,1.02,7,23,29.9,0.87,100,0.4,55,47.4,0,1,null,32.1875,null,380,0.74,4,23,31.1,1.03,100,0.4,55,46.1,0,2,null,35.3125,null,380,0.59,3,23,32,1.1299999999999999,100,0.4,55,45.1,0,2,null,38.125,null,380,0.5,2,23,32.6,1.22,100,0.4,55,44.4,0,2,null,380,0.5,2,23,32.6,1.22,100,0.4,55,44.4,0,2]
[null,390,32.130494320392557,1,280.60975609756099,24.197346944735308,0.75309600603865456,390,32.130494320392557,1,485.1219512195122,38.840568945573949,1.2088382008154368,570.73170731707319,44.300032476853517,1.3787535303724601,null,null,null,null,null,null,null,null,null,null,32.5,0,390,0.75,4,23,31,1.04,100,0.4,55,46,null,2,null,27.5,null,390,1.05,8,23,29.8,0.88,100,0.4,55,47.3,0,1,null,32.5,null,390,0.75,4,23,31,1.04,100,0.4,55,46,0,2,null,35.9375,null,390,0.61,3,23,31.8,1.1499999999999999,100,0.4,55,45,0,2,null,38.4375,null,390,0.52,2,23,32.5,1.23,100,0.4,55,44.3,0,2,null,390,0.52,2,23,32.5,1.23,100,0.4,55,44.3,0,2]
[null,400,32.460359334512077,1,287.80487804878049,24.411850282297976,0.75205114123130268,400,32.460359334512077,1,497.5609756097561,39.215694943317516,1.2081103150827761,585.36585365853659,44.661565305525727,1.375880188055751,null,null,null,null,null,null,null,null,null,null,32.8125,0,400,0.77,4,23,30.8,1.05,100,0.4,55,45.9,null,2,null,27.8125,null,400,1.08,8,23,29.7,0.89,100,0.4,55,47.3,0,1,null,32.8125,null,400,0.77,4,23,30.8,1.05,100,0.4,55,45.9,0,2,null,36.25,null,400,0.62,3,23,31.7,1.1599999999999999,100,0.4,55,44.9,0,2,null,38.75,null,400,0.53,2,23,32.299999999999997,1.24,100,0.4,55,44.2,0,2,null,400,0.53,2,23,32.299999999999997,1.24,100,0.4,55,44.2,0,2]
[null,410,32.786240143026433,1,295,24.624311338828605,0.75105627334539449,410,32.786240143026433,1,510,39.578537983515361,1.2071691603202521,600,45.005929741361626,1.3727078660141607,null,null,null,null,null,null,null,null,null,null,32.8125,0,410,0.79,5,23,30.7,1.05,100,0.4,55,45.8,null,2,null,28.125,null,410,1.1000000000000001,9,23,29.6,0.9,100,0.4,55,47.2,0,1,null,32.8125,null,410,0.79,5,23,30.7,1.05,100,0.4,55,45.8,0,2,null,36.5625,null,410,0.64,3,23,31.5,1.17,100,0.4,55,44.8,0,2,null,39.375,null,410,0.54,2,23,32.200000000000003,1.26,100,0.4,55,44.1,0,2,null,410,0.54,2,23,32.200000000000003,1.26,100,0.4,55,44.1,0,2]
[null,420,33.107751740402762,1,302.19512195121951,24.83505956777644,0.75012824073672113,420,33.107751740402762,1,522.43902439024384,39.928751911726124,1.206024263586567,614.63414634146341,45.334364023949206,1.3692975705331814,null,null,null,null,null,null,null,null,null,null,33.125,0,420,0.81,5,23,30.6,1.06,100,0.4,55,45.7,null,2,null,28.125,null,420,1.1299999999999999,9,23,29.5,0.9,100,0.4,55,47.1,0,1,null,33.125,null,420,0.81,5,23,30.6,1.06,100,0.4,55,45.7,0,2,null,36.875,null,420,0.65,3,23,31.4,1.18,100,0.4,55,44.7,0,2,null,39.6875,null,420,0.56000000000000005,2,23,32,1.27,100,0.4,55,44,0,2,null,420,0.56000000000000005,2,23,32,1.27,100,0.4,55,44,0,2]
[null,430,33.424482347189141,1,309.39024390243901,25.044368737788147,0.74928217220076931,430,33.424482347189141,1,534.8780487804878,40.266105453462018,1.2046889772355212,629.26829268292681,45.648366124969897,1.3657164724589588,null,null,null,null,null,null,null,null,null,null,33.4375,0,430,0.83,5,23,30.5,1.07,100,0.4,55,45.6,null,2,null,28.4375,null,430,1.1599999999999999,9,23,29.4,0.91,100,0.4,55,47,0,1,null,33.4375,null,430,0.83,5,23,30.5,1.07,100,0.4,55,45.6,0,2,null,37.1875,null,430,0.67,3,23,31.3,1.19,100,0.4,55,44.6,0,2,null,40,null,430,0.56999999999999995,3,23,31.9,1.28,100,0.4,55,43.9,0,2,null,430,0.56999999999999995,3,23,31.9,1.28,100,0.4,55,43.9,0,2]
[null,440,33.736005394411961,1,316.58536585365852,25.252460822325361,0.74853144369333613,440,33.736005394411961,1,547.31707317073176,40.590494000604053,1.2031802083873118,643.90243902439022,45.949669387162629,1.3620364607474762,null,null,null,null,null,null,null,null,null,null,33.75,0,440,0.85,5,23,30.4,1.08,100,0.4,55,45.6,null,2,null,28.75,null,440,1.18,10,23,29.3,0.92,100,0.4,55,47,0,1,null,33.75,null,440,0.85,5,23,30.4,1.08,100,0.4,55,45.6,0,2,null,37.5,null,440,0.68,4,23,31.2,1.2,100,0.4,55,44.6,0,2,null,40.3125,null,440,0.57999999999999996,3,23,31.8,1.29,100,0.4,55,43.8,0,2,null,440,0.57999999999999996,3,23,31.8,1.29,100,0.4,55,43.8,0,2]
[null,450,34.041890696351459,1,323.78048780487802,25.45950978306027,0.74788765436547766,450,34.041890696351459,1,559.7560975609756,40.901948588249127,1.201518122277295,658.53658536585363,46.240210211657541,1.3583326091994494,null,null,null,null,null,null,null,null,null,null,34.0625,0,450,0.87,6,23,30.3,1.0900000000000001,100,0.4,55,45.5,null,2,null,29.0625,null,450,1.21,10,23,29.2,0.93,100,0.4,55,46.9,0,1,null,34.0625,null,450,0.87,6,23,30.3,1.0900000000000001,100,0.4,55,45.5,0,2,null,37.8125,null,450,0.7,4,23,31.1,1.21,100,0.4,55,44.5,0,2,null,40.625,null,450,0.6,3,23,31.7,1.3,100,0.4,55,43.7,0,2,null,450,0.6,3,23,31.7,1.3,100,0.4,55,43.7,0,2]
[null,460,34.341714811696974,1,330.97560975609753,25.66564524704917,0.74736061922881358,460,34.341714811696974,1,572.19512195121956,41.200642061989754,1.1997258228921228,673.17073170731703,46.522087793679248,1.3546815599852799,null,null,null,null,null,null,null,null,null,null,34.375,0,460,0.89,6,23,30.2,1.1000000000000001,100,0.4,55,45.4,null,2,null,29.0625,null,460,1.24,11,23,29.1,0.93,100,0.4,55,46.9,0,1,null,34.375,null,460,0.89,6,23,30.2,1.1000000000000001,100,0.4,55,45.4,0,2,null,38.125,null,460,0.72,4,23,30.9,1.22,100,0.4,55,44.4,0,2,null,40.9375,null,460,0.61,3,23,31.5,1.31,100,0.4,55,43.6,0,2,null,460,0.61,3,23,31.5,1.31,100,0.4,55,43.6,0,2]
[null,470,34.635070593080542,1,338.17073170731709,25.870956077684227,0.74695837585077052,470,34.635070593080542,1,584.63414634146341,41.486892435624611,1.1978290133444376,687.80487804878044,46.797515906621157,1.3511598245730283,null,null,null,null,null,null,null,null,null,null,34.6875,0,470,0.91,6,23,30.1,1.1100000000000001,100,0.4,55,45.3,null,2,null,29.375,null,470,1.26,11,23,29,0.94,100,0.4,55,46.8,0,1,null,34.6875,null,470,0.91,6,23,30.1,1.1100000000000001,100,0.4,55,45.3,0,2,null,38.4375,null,470,0.73,4,23,30.8,1.23,100,0.4,55,44.3,0,2,null,41.25,null,470,0.62,3,23,31.4,1.32,100,0.4,55,43.5,0,2,null,470,0.62,3,23,31.4,1.32,100,0.4,55,43.5,0,2]
[null,480,34.921575924989241,1,345.36585365853659,26.075493839423501,0.74668720264609689,480,34.921575924989241,1,597.07317073170736,41.761163439302123,1.1958556374719218,702.43902439024384,47.068766734488605,1.3478419999026177,null,null,null,null,null,null,null,null,null,null,35,0,480,0.93,6,23,30,1.1200000000000001,100,0.4,55,45.3,null,2,null,29.6875,null,480,1.29,12,23,28.9,0.95,100,0.4,55,46.7,0,1,null,35,null,480,0.93,6,23,30,1.1200000000000001,100,0.4,55,45.3,0,2,null,38.75,null,480,0.75,4,23,30.7,1.24,100,0.4,55,44.2,0,2,null,41.5625,null,480,0.63,3,23,31.3,1.33,100,0.4,55,43.4,0,2,null,480,0.63,3,23,31.3,1.33,100,0.4,55,43.4,0,2]
[null,490,35.200881650056829,1,352.5609756097561,26.279276156298593,0.74655164656241413,490,35.200881650056829,1,609.51219512195121,42.024062258095199,1.1938355032089758,717.07317073170725,47.338106752712235,1.3447988951900531,null,null,null,null,null,null,null,null,null,null,35,0,490,0.95,6,23,29.9,1.1200000000000001,100,0.4,55,45.2,null,2,null,29.6875,null,490,1.32,12,23,28.8,0.95,100,0.4,55,46.7,0,1,null,35,null,490,0.95,6,23,29.9,1.1200000000000001,100,0.4,55,45.2,0,2,null,38.75,null,490,0.76,4,23,30.6,1.24,100,0.4,55,44.2,0,2,null,41.875,null,490,0.65,3,23,31.2,1.34,100,0.4,55,43.3,0,2,null,490,0.65,3,23,31.2,1.34,100,0.4,55,43.3,0,2]
[null,500,35.472678683733761,0.99999999999999989,359.7560975609756,26.482289964201044,0.74655455823652461,500,35.472678683733761,0.99999999999999989,621.95121951219517,42.276334461007735,1.1917998873988007,731.70731707317077,47.607724657332028,1.342095562666455,null,null,null,null,null,null,null,null,null,null,35.3125,0,500,0.97,7,23,29.8,1.1299999999999999,100,0.4,55,45.1,null,2,null,30,null,500,1.35,12,23,28.8,0.96,100,0.4,55,46.6,0,1,null,35.3125,null,500,0.97,7,23,29.8,1.1299999999999999,100,0.4,55,45.1,0,2,null,39.0625,null,500,0.78,5,23,30.5,1.25,100,0.4,55,44.1,0,2,null,42.1875,null,500,0.66,3,23,31.1,1.35,100,0.4,55,43.3,0,2,null,500,0.66,3,23,31.1,1.35,100,0.4,55,43.3,0,2]
[null,510,35.736704317336347,1,366.95121951219511,26.684494656946285,0.74669713300902463,510,35.736704317336347,1,634.39024390243901,42.518856120412721,1.1897811209128835,746.34146341463418,47.879651342551483,1.3397892239135334,null,null,null,null,null,null,null,null,null,null,35.625,0,510,0.99,7,23,29.7,1.1399999999999999,100,0.4,55,45.1,null,2,null,30.3125,null,510,1.37,13,23,28.7,0.97,100,0.4,55,46.6,0,1,null,35.625,null,510,0.99,7,23,29.7,1.1399999999999999,100,0.4,55,45.1,0,2,null,39.375,null,510,0.79,5,23,30.4,1.26,100,0.4,55,44,0,2,null,42.5,null,510,0.67,3,23,31,1.36,100,0.4,55,43.2,0,2,null,510,0.67,3,23,31,1.36,100,0.4,55,43.2,0,2]
[null,520,35.992747709474799,1,374.14634146341461,26.885825126116018,0.74697895651457979,520,35.992747709474799,1,646.82926829268297,42.752623121924046,1.1878121522428189,760.97560975609758,48.155671926659267,1.3379270822933775,null,null,null,null,null,null,null,null,null,null,35.9375,0,520,1.01,7,23,29.6,1.1499999999999999,100,0.4,55,45,null,2,null,30.3125,null,520,1.4,13,23,28.6,0.97,100,0.4,55,46.5,0,1,null,35.9375,null,520,1.01,7,23,29.6,1.1499999999999999,100,0.4,55,45,0,2,null,39.6875,null,520,0.81,5,23,30.3,1.27,100,0.4,55,43.9,0,2,null,42.8125,null,520,0.69,4,23,30.9,1.37,100,0.4,55,43.1,0,2,null,520,0.69,4,23,30.9,1.37,100,0.4,55,43.1,0,2]
[null,530,36.240654565859728,1,381.34146341463412,27.086194694678355,0.74739805390255631,530,36.240654565859728,1,659.26829268292681,42.978737664697462,1.1859260871404156,775.60975609756099,48.437229826324398,1.3365440113202143,null,null,null,null,null,null,null,null,null,null,35.9375,0,530,1.03,8,23,29.5,1.1499999999999999,100,0.4,55,44.9,null,2,null,30.625,null,530,1.43,14,23,28.5,0.98,100,0.4,55,46.5,0,1,null,35.9375,null,530,1.03,8,23,29.5,1.1499999999999999,100,0.4,55,44.9,0,2,null,40,null,530,0.82,5,23,30.2,1.28,100,0.4,55,43.8,0,2,null,43.125,null,530,0.7,4,23,30.8,1.38,100,0.4,55,43,0,2,null,530,0.7,4,23,30.8,1.38,100,0.4,55,43,0,2]
[null,540,36.480331007488104,0.99999999999999989,388.53658536585363,27.285497944386847,0.74795094207851653,540,36.480331007488104,0.99999999999999989,671.70731707317077,43.1983919521644,1.1841557014188637,790.2439024390244,48.725322879259068,1.335660108710568,null,null,null,null,null,null,null,null,null,null,36.25,0,540,1.05,8,23,29.5,1.1599999999999999,100,0.4,55,44.9,null,2,null,30.625,null,540,1.45,14,23,28.5,0.98,100,0.4,55,46.4,0,1,null,36.25,null,540,1.05,8,23,29.5,1.1599999999999999,100,0.4,55,44.9,0,2,null,40.3125,null,540,0.84,5,23,30.2,1.29,100,0.4,55,43.8,0,2,null,43.125,null,540,0.71,4,23,30.7,1.38,100,0.4,55,42.9,0,2,null,540,0.71,4,23,30.7,1.38,100,0.4,55,42.9,0,2]
[null,550,36.711746627207503,1,395.73170731707313,27.483613436956304,0.74863268468375943,550,36.711746627207503,1,684.14634146341461,43.41284907319988,1.1825329236998523,804.8780487804878,49.020391515251902,1.3352781062975172,null,null,null,null,null,null,null,null,null,null,36.5625,0,550,1.06,8,23,29.4,1.17,100,0.4,55,44.8,null,2,null,30.9375,null,550,1.48,15,23,28.4,0.99,100,0.4,55,46.4,0,1,null,36.5625,null,550,1.06,8,23,29.4,1.17,100,0.4,55,44.8,0,2,null,40.3125,null,550,0.86,5,23,30.1,1.29,100,0.4,55,43.7,0,2,null,43.4375,null,550,0.73,4,23,30.6,1.39,100,0.4,55,42.8,0,2,null,550,0.73,4,23,30.6,1.39,100,0.4,55,42.8,0,2]
[null,560,36.934936734659573,1,402.92682926829269,27.680406329018112,0.74943694984166431,560,36.934936734659573,1,696.58536585365857,43.623421073719186,1.1810882847075022,819.51219512195121,49.322198975572263,1.3353806270172528,null,null,null,null,null,null,null,null,null,null,36.5625,0,560,1.08,8,23,29.3,1.17,100,0.4,55,44.8,null,2,null,31.25,null,560,1.51,15,23,28.3,1,100,0.4,55,46.3,0,1,null,36.5625,null,560,1.08,8,23,29.3,1.17,100,0.4,55,44.8,0,2,null,40.625,null,560,0.87,6,23,30,1.3,100,0.4,55,43.6,0,2,null,43.75,null,560,0.74,4,23,30.5,1.4,100,0.4,55,42.8,0,2,null,560,0.74,4,23,30.5,1.4,100,0.4,55,42.8,0,2]
[null,570,37.150003789601897,1,410.1219512195122,27.875730880852757,0.75035607099063162,570,37.150003789601897,1,709.02439024390242,43.831444218705968,1.1798503296781404,834.14634146341461,49.629703580742529,1.3359272817795416,null,null,null,null,null,null,null,null,null,null,36.875,0,570,1.1000000000000001,9,23,29.2,1.18,100,0.4,55,44.7,null,2,null,31.25,null,570,1.53,16,23,28.3,1,100,0.4,55,46.3,0,1,null,36.875,null,570,1.1000000000000001,9,23,29.2,1.18,100,0.4,55,44.7,0,2,null,40.9375,null,570,0.89,6,23,29.9,1.31,100,0.4,55,43.6,0,2,null,44.0625,null,570,0.75,4,23,30.4,1.41,100,0.4,55,42.7,0,2,null,570,0.75,4,23,30.4,1.41,100,0.4,55,42.7,0,2]
[null,580,37.357118023609445,1,417.3170731707317,28.069432858900612,0.75138111138982722,580,37.357118023609445,1,721.46341463414637,44.038251444677115,1.1788449905810516,848.78048780487802,49.940923046683224,1.3368516012161564,null,null,null,null,null,null,null,null,null,null,37.1875,0,580,1.1200000000000001,9,23,29.2,1.19,100,0.4,55,44.6,null,2,null,31.5625,null,580,1.56,16,23,28.2,1.01,100,0.4,55,46.2,0,1,null,37.1875,null,580,1.1200000000000001,9,23,29.2,1.19,100,0.4,55,44.6,0,2,null,41.25,null,580,0.9,6,23,29.8,1.32,100,0.4,55,43.5,0,2,null,44.375,null,580,0.77,4,23,30.3,1.42,100,0.4,55,42.6,0,2,null,580,0.77,4,23,30.3,1.42,100,0.4,55,42.6,0,2]
[null,590,37.556517250154485,1,424.51219512195121,28.261351832051218,0.75250193312147351,590,37.556517250154485,1,733.90243902439022,44.245142002573601,1.1780949151346456,863.41463414634143,50.252790849223288,1.3380578000484478,null,null,null,null,null,null,null,null,null,null,37.5,0,590,1.1399999999999999,9,23,29.1,1.2,100,0.4,55,44.6,null,2,null,31.5625,null,590,1.59,17,23,28.2,1.01,100,0.4,55,46.2,0,1,null,37.5,null,590,1.1399999999999999,9,23,29.1,1.2,100,0.4,55,44.6,0,2,null,41.5625,null,590,0.92,6,23,29.7,1.33,100,0.4,55,43.4,0,2,null,44.6875,null,590,0.78,5,23,30.3,1.43,100,0.4,55,42.6,0,2,null,590,0.78,5,23,30.3,1.43,100,0.4,55,42.6,0,2]
[null,600,37.748505863064338,1,431.70731707317071,28.451323361710152,0.75370727161810203,600,37.748505863064338,1,746.34146341463418,44.453348291087423,1.177618750059815,878.04878048780483,50.561004636986468,1.3394173750982481,null,null,null,null,null,null,null,null,null,null,37.5,0,600,1.1599999999999999,9,23,29,1.2,100,0.4,55,44.5,null,2,null,31.875,null,600,1.61,17,23,28.1,1.02,100,0.4,55,46.1,0,1,null,37.5,null,600,1.1599999999999999,9,23,29,1.2,100,0.4,55,44.5,0,2,null,41.5625,null,600,0.93,6,23,29.7,1.33,100,0.4,55,43.4,0,2,null,45,null,600,0.79,5,23,30.2,1.44,100,0.4,55,42.5,0,2,null,600,0.79,5,23,30.2,1.44,100,0.4,55,42.5,0,2]
[null,610,37.933453023360698,1,438.90243902439022,28.639181085644211,0.75498481691100561,610,37.933453023360698,1,758.78048780487802,44.663999880416554,1.1774303766364469,892.68292682926824,50.859866692643834,1.340765541732323,null,null,null,null,null,null,null,null,null,null,{"$f":"IF($AA$13=$AP$13,AP78,IF($AA$13=$BE$13,BE78,IF($AA$13=$BT$13,BT78,IF($AA$13=$CI$13,CI78,\"-\"))))","v":37.8125},{"$f":"IF($AA$13=$AP$13,AQ78,IF($AA$13=$BE$13,BF78,IF($AA$13=$BT$13,BU78,IF($AA$13=$CI$13,CJ78,\"-\"))))","v":0},{"$f":"IF($AA$13=$AP$13,AR78,IF($AA$13=$BE$13,BG78,IF($AA$13=$BT$13,BV78,IF($AA$13=$CI$13,CK78,\"-\"))))","v":610},{"$f":"IF($AA$13=$AP$13,AS78,IF($AA$13=$BE$13,BH78,IF($AA$13=$BT$13,BW78,IF($AA$13=$CI$13,CL78,\"-\"))))","v":1.18},{"$f":"IF($AA$13=$AP$13,AT78,IF($AA$13=$BE$13,BI78,IF($AA$13=$BT$13,BX78,IF($AA$13=$CI$13,CM78,\"-\"))))","v":10},{"$f":"IF($AA$13=$AP$13,AU78,IF($AA$13=$BE$13,BJ78,IF($AA$13=$BT$13,BY78,IF($AA$13=$CI$13,CN78,\"-\"))))","v":23},{"$f":"IF($AA$13=$AP$13,AV78,IF($AA$13=$BE$13,BK78,IF($AA$13=$BT$13,BZ78,IF($AA$13=$CI$13,CO78,\"-\"))))","v":28.9},{"$f":"IF($AA$13=$AP$13,AW78,IF($AA$13=$BE$13,BL78,IF($AA$13=$BT$13,CA78,IF($AA$13=$CI$13,CP78,\"-\"))))","v":1.21},{"$f":"IF($AA$13=$AP$13,AX78,IF($AA$13=$BE$13,BM78,IF($AA$13=$BT$13,CB78,IF($AA$13=$CI$13,CQ78,\"-\"))))","v":100},{"$f":"IF($AA$13=$AP$13,AY78,IF($AA$13=$BE$13,BN78,IF($AA$13=$BT$13,CC78,IF($AA$13=$CI$13,CR78,\"-\"))))","v":0.4},{"$f":"IF($AA$13=$AP$13,AZ78,IF($AA$13=$BE$13,BO78,IF($AA$13=$BT$13,CD78,IF($AA$13=$CI$13,CS78,\"-\"))))","v":55},{"$f":"IF($AA$13=$AP$13,BA78,IF($AA$13=$BE$13,BP78,IF($AA$13=$BT$13,CE78,IF($AA$13=$CI$13,CT78,\"-\"))))","v":44.5},null,{"$f":"IF($AA$13=$AP$13,BC78,IF($AA$13=$BE$13,BR78,IF($AA$13=$BT$13,CG78,IF($AA$13=$CI$13,CV78,\"-\"))))","v":2},null,31.875,null,610,1.64,18,23,28,1.02,100,0.4,55,46.1,0,1,null,37.8125,null,610,1.18,10,23,28.9,1.21,100,0.4,55,44.5,0,2,null,41.875,null,610,0.95,7,23,29.6,1.34,100,0.4,55,43.3,0,2,null,45,null,610,0.81,5,23,30.1,1.44,100,0.4,55,42.4,0,2,null,610,0.81,5,23,30.1,1.44,100,0.4,55,42.4,0,2]
[null,620,38.111790034474097,1,446.09756097560972,28.824758695604928,0.75632130292309629,620,38.111790034474097,1,771.21951219512198,44.878084726456223,1.1775380974197658,907.31707317073165,51.14211644253686,1.3418975177045254,null,null,null,null,null,null,null,null,null,null,37.8125,0,620,1.2,10,23,28.9,1.21,100,0.4,55,44.4,null,2,null,32.1875,null,620,1.67,18,23,28,1.03,100,0.4,55,46,0,1,null,37.8125,null,620,1.2,10,23,28.9,1.21,100,0.4,55,44.4,0,2,null,42.1875,null,620,0.96,7,23,29.5,1.35,100,0.4,55,43.3,0,2,null,45.3125,null,620,0.82,5,23,30,1.45,100,0.4,55,42.4,0,2,null,620,0.82,5,23,30,1.45,100,0.4,55,42.4,0,2]
[null,630,38.284006905840414,1,453.29268292682923,29.00789180872988,0.75770260621033858,630,38.284006905840414,1,783.65853658536582,45.096407575418652,1.1779437739193117,921.95121951219505,51.39875501467003,1.3425646678281447,null,null,null,null,null,null,null,null,null,null,38.125,0,630,1.22,10,23,28.8,1.22,100,0.4,55,44.4,null,2,null,32.1875,null,630,1.69,19,23,27.9,1.03,100,0.4,55,46,0,1,null,38.125,null,630,1.22,10,23,28.8,1.22,100,0.4,55,44.4,0,2,null,42.1875,null,630,0.98,7,23,29.4,1.35,100,0.4,55,43.2,0,2,null,45.625,null,630,0.83,5,23,29.9,1.46,100,0.4,55,42.3,0,2,null,630,0.83,5,23,29.9,1.46,100,0.4,55,42.3,0,2]
[null,640,38.450648104875228,1,460.48780487804879,29.188419732721982,0.75911385558729061,640,38.450648104875228,1,796.09756097560978,45.319545558885835,1.178641916133,936.58536585365846,51.61886184507398,1.3424705275261442,null,null,null,null,null,null,null,null,null,null,38.4375,0,640,1.24,11,23,28.8,1.23,100,0.4,55,44.3,null,2,null,32.5,null,640,1.72,20,23,27.9,1.04,100,0.4,55,45.9,0,1,null,38.4375,null,640,1.24,11,23,28.8,1.23,100,0.4,55,44.3,0,2,null,42.5,null,640,1,7,23,29.4,1.36,100,0.4,55,43.1,0,2,null,45.9375,null,640,0.85,5,23,29.9,1.47,100,0.4,55,42.2,0,2,null,640,0.85,5,23,29.9,1.47,100,0.4,55,42.2,0,2]
[null,{"$f":"AC82","v":650},{"$f":"$J$4*B82^6+$K$4*B82^5+$L$4*B82^4+$M$4*B82^3+$N$4*B82^2+$O$4*B82","v":38.612307497325418},1,{"$f":"IF($B82*$F$3>$B$11,\"\",$B82*$F$3)","v":467.6829268292683},29.366187124807453,0.76053955404870788,{"$f":"IF($B82*$F$4>$B$11,\"\",$B82*$F$4)","v":650},38.612307497325418,1,{"$f":"IF($B82*$F$5>$B$11,\"\",$B82*$F$5)","v":808.53658536585363},{"$f":"IF(K82>$B$11,\"\",$J$5*K82^6+$K$5*K82^5+$L$5*K82^4+$M$5*K82^3+$N$5*K82^2+$O$5*K82)","v":45.547800979295658},{"$f":"IF(K82>$B$11,\"\",1/$C82*L82)","v":1.1796187260357502},{"$f":"IF($B82*$F$6>$B$11,\"\",$B82*$F$6)","v":951.21951219512198},51.789403332541042,{"$f":"IF(N82>$B$11,\"\",1/$C82*O82)","v":1.3412667278724115},null,null,null,null,null,null,null,null,null,null,38.4375,0,650,1.26,11,23,28.7,1.23,100,0.4,55,44.3,null,2,null,32.8125,null,650,1.75,20,23,27.8,1.05,100,0.4,55,45.9,0,1,null,38.4375,null,650,1.26,11,23,28.7,1.23,100,0.4,55,44.3,0,2,null,42.8125,null,650,1.01,7,23,29.3,1.37,100,0.4,55,43.1,0,2,null,45.9375,null,650,0.86,5,23,29.8,1.47,100,0.4,55,42.2,0,2,null,650,0.86,5,23,29.8,1.47,100,0.4,55,42.2,0,2]
[null,660,38.769622476002155,{"$f":"1/C83*C83","v":1},474.8780487804878,{"$f":"IF(E83>$B$11,\"\",$J$3*E83^6+$K$3*E83^5+$L$3*E83^4+$M$3*E83^3+$N$3*E83^2+$O$3*E83)","v":29.541045544471245},{"$f":"IF(E83>$B$11,\"\",1/$C83*F83)","v":0.76196371431671106},660,{"$f":"IF(H83>$B$11,\"\",$J$4*H83^6+$K$4*H83^5+$L$4*H83^4+$M$4*H83^3+$N$4*H83^2+$O$4*H83)","v":38.769622476002155},{"$f":"IF(H83>$B$11,\"\",1/$C83*I83)","v":1},820.97560975609758,45.781151285853781,1.1808510984132399,965.85365853658539,{"$f":"IF(N83>$B$11,\"\",$J$6*N83^6+$K$6*N83^5+$L$6*N83^4+$M$6*N83^3+$N$6*N83^2+$O$6*N83)","v":51.895033541726946},{"$f":"IF(N83>$B$11,\"\",1/$C83*O83)","v":1.3385488490079891},null,null,null,null,null,null,null,null,null,null,38.75,0,660,1.28,11,23,28.6,1.24,100,0.4,55,44.2,null,2,null,{"$f":"ABS(AW83/(AU83-AZ83)*1000)","v":32.8125},null,660,1.78,21,23,27.8,1.05,100,0.4,55,45.8,0,1,null,{"$f":"ABS(BL83/(BJ83-BO83)*1000)","v":38.75},null,660,1.28,11,23,28.6,1.24,100,0.4,55,44.2,0,2,null,{"$f":"ABS(CA83/(BY83-CD83)*1000)","v":42.8125},null,660,1.03,8,23,29.2,1.37,100,0.4,55,43,0,2,null,{"$f":"ABS(CP83/(CN83-CS83)*1000)","v":46.25},null,660,0.87,6,23,29.7,1.48,100,0.4,55,42.1,0,2,null,660,0.87,6,23,29.7,1.48,100,0.4,55,42.1,0,2]
[null,670,38.923267277891512,1,482.07317073170731,29.71285489997112,0.76337000919879294,670,38.923267277891512,1,833.41463414634143,46.019196240888419,1.1823055837613974,980.48780487804879,51.917886954623157,{"$f":"IF(N84>$B$11,\"\",1/$C84*O84)","v":1.3338522324952051},null,null,null,null,null,null,null,null,null,null,39.0625,0,670,1.3,12,23,28.6,1.25,100,0.4,55,44.1,null,2,null,33.125,null,670,1.8,21,23,27.7,1.06,100,0.4,55,45.8,0,1,null,39.0625,null,670,1.3,12,23,28.6,1.25,100,0.4,55,44.1,0,2,null,43.125,null,670,1.04,8,23,29.2,1.38,100,0.4,55,43,0,2,null,46.5625,null,670,0.89,6,23,29.7,1.49,100,0.4,55,42,0,2,null,670,0.89,6,23,29.7,1.49,100,0.4,55,42,0,2]
[null,680,39.073945489643165,1,489.26829268292681,29.881484788629379,0.7647419377331548,680,39.073945489643165,1,845.85365853658539,46.261102276625081,1.1839373192780576,995.1219512195122,51.837363270399521,{"$f":"IF(N85>$B$11,\"\",1/$C85*O85)","v":1.3266477859047889},null,null,null,null,null,null,null,null,null,null,39.0625,0,680,1.32,12,23,28.5,1.25,100,0.4,55,44.1,null,2,null,33.125,null,680,1.83,22,23,27.7,1.06,100,0.4,55,45.8,0,1,null,39.0625,null,680,1.32,12,23,28.5,1.25,100,0.4,55,44.1,0,2,null,43.4375,null,680,1.06,8,23,29.1,1.39,100,0.4,55,42.9,0,2,null,46.5625,null,680,0.9,6,23,29.6,1.49,100,0.4,55,42,0,2,null,680,0.9,6,23,29.6,1.49,100,0.4,55,42,0,2]
[null,690,39.222381741439136,0.99999999999999989,496.46341463414632,30.046815730902765,0.76606300782488623,690,39.222381741439136,0.99999999999999989,858.29268292682923,46.505544042400118,1.1856889351843258,"","","",null,null,null,null,null,null,null,null,null,null,39.375,0,690,1.34,12,23,28.5,1.26,100,0.4,55,44,null,2,null,33.4375,null,690,1.86,23,23,27.6,1.07,100,0.4,55,45.7,0,1,null,39.375,null,690,1.34,12,23,28.5,1.26,100,0.4,55,44,0,2,null,43.4375,null,690,1.07,8,23,29.1,1.39,100,0.4,55,42.8,0,2,null,46.875,null,690,0.91,6,23,29.5,1.5,100,0.4,55,41.9,0,2,null,690,0.91,6,23,29.5,1.5,100,0.4,55,41.9,0,2]
[null,700,39.369312589241957,1,503.65853658536582,30.208740298231163,0.76731693574162108,700,39.369312589241957,1,870.73170731707319,46.750643142307638,1.1874894446361937,"","","",null,null,null,null,null,null,null,null,null,null,39.375,0,700,1.36,13,23,28.4,1.26,100,0.4,55,44,null,2,null,33.4375,null,700,1.88,23,23,27.6,1.07,100,0.4,55,45.7,0,1,null,39.375,null,700,1.36,13,23,28.4,1.26,100,0.4,55,44,0,2,null,43.75,null,700,1.0900000000000001,8,23,29,1.4,100,0.4,55,42.8,0,2,null,47.1875,null,700,0.93,6,23,29.5,1.51,100,0.4,55,41.9,0,2,null,700,0.93,6,23,29.5,1.51,100,0.4,55,41.9,0,2]
[null,710,39.515476585419833,1,510.85365853658533,30.367164134663028,0.76848786244596912,710,39.515476585419833,1,883.17073170731703,46.993904063270463,1.1892531262196639,"","","",null,null,null,null,null,null,null,null,null,null,39.6875,0,710,1.37,13,23,28.4,1.27,100,0.4,55,43.9,null,2,null,33.4375,null,710,1.91,24,23,27.5,1.07,100,0.4,55,45.6,0,1,null,39.6875,null,710,1.37,13,23,28.4,1.27,100,0.4,55,43.9,0,2,null,44.0625,null,710,1.1000000000000001,9,23,28.9,1.41,100,0.4,55,42.7,0,2,null,47.1875,null,710,0.94,6,23,29.4,1.51,100,0.4,55,41.8,0,2,null,710,0.94,6,23,29.4,1.51,100,0.4,55,41.8,0,2]
[null,720,39.661603537750182,1,518.04878048780483,30.522006872260391,0.76956058630381241,720,39.661603537750182,1,895.60975609756099,47.232147293549417,1.1908784083475985,"","","",null,null,null,null,null,null,null,null,null,null,39.6875,0,720,1.39,13,23,28.3,1.27,100,0.4,55,43.9,null,2,null,33.75,null,720,1.94,24,23,27.5,1.08,100,0.4,55,45.6,0,1,null,39.6875,null,720,1.39,13,23,28.3,1.27,100,0.4,55,43.9,0,2,null,44.0625,null,720,1.1200000000000001,9,23,28.9,1.41,100,0.4,55,42.7,0,2,null,47.5,null,720,0.95,7,23,29.3,1.52,100,0.4,55,41.8,0,2,null,720,0.95,7,23,29.3,1.52,100,0.4,55,41.8,0,2]
[null,730,39.808402956806503,1,525.2439024390244,30.673202940281215,0.77052081123582628,730,39.808402956806503,1,908.04878048780483,47.461439631686346,1.1922467646638237,"","","",null,null,null,null,null,null,null,null,null,null,40,0,730,1.41,14,23,28.3,1.28,100,0.4,55,43.8,null,2,null,33.75,null,730,1.96,25,23,27.5,1.08,100,0.4,55,45.5,0,1,null,40,null,730,1.41,14,23,28.3,1.28,100,0.4,55,43.8,0,2,null,44.375,null,730,1.1399999999999999,9,23,28.8,1.42,100,0.4,55,42.6,0,2,null,47.8125,null,730,0.97,7,23,29.3,1.53,100,0.4,55,41.7,0,2,null,730,0.97,7,23,29.3,1.53,100,0.4,55,41.7,0,2]
[null,740,39.956551691718488,1,532.43902439024384,30.820702268139144,0.77135540889348397,740,39.956551691718488,1,920.48780487804879,47.677021685868453,1.1932216286759834,"","","",null,null,null,null,null,null,null,null,null,null,40,0,740,1.43,14,23,28.2,1.28,100,0.4,55,43.8,null,2,null,34.0625,null,740,1.99,26,23,27.4,1.0900000000000001,100,0.4,55,45.5,0,1,null,40,null,740,1.43,14,23,28.2,1.28,100,0.4,55,43.8,0,2,null,44.375,null,740,1.1499999999999999,9,23,28.8,1.42,100,0.4,55,42.6,0,2,null,47.8125,null,740,0.98,7,23,29.2,1.53,100,0.4,55,41.6,0,2,null,740,0.98,7,23,29.2,1.53,100,0.4,55,41.6,0,2]
[null,750,40.106680754314624,0.99999999999999989,539.63414634146341,30.964470882143502,0.77205269296219137,750,40.106680754314624,0.99999999999999989,932.92682926829264,47.873232563737588,1.1936473341436376,"","","",null,null,null,null,null,null,null,null,null,null,40.3125,0,750,1.45,14,23,28.2,1.29,100,0.4,55,43.8,null,2,null,34.0625,null,750,2.02,26,23,27.4,1.0900000000000001,100,0.4,55,45.5,0,1,null,40.3125,null,750,1.45,14,23,28.2,1.29,100,0.4,55,43.8,0,2,null,44.6875,null,750,1.17,10,23,28.7,1.43,100,0.4,55,42.5,0,2,null,48.125,null,750,0.99,7,23,29.2,1.54,100,0.4,55,41.6,0,2,null,750,0.99,7,23,29.2,1.54,100,0.4,55,41.6,0,2]
[null,760,40.259361331641827,1,546.82926829268285,31.104491396014538,0.77260270325172731,760,40.259361331641827,1,945.36585365853659,48.043431752622496,1.1933480851039429,"","","",null,null,null,null,null,null,null,null,null,null,40.625,0,760,1.47,15,23,28.1,1.3,100,0.4,55,43.7,null,2,null,34.375,null,760,2.04,27,23,27.3,1.1000000000000001,100,0.4,55,45.4,0,1,null,40.625,null,760,1.47,15,23,28.1,1.3,100,0.4,55,43.7,0,2,null,45,null,760,1.18,10,23,28.7,1.44,100,0.4,55,42.5,0,2,null,48.4375,null,760,1.01,7,23,29.1,1.55,100,0.4,55,41.5,0,2,null,760,1.01,7,23,29.1,1.55,100,0.4,55,41.5,0,2]
[null,770,40.415089986865439,0.99999999999999989,554.02439024390242,31.240763395180238,0.77299749685904984,770,40.415089986865439,0.99999999999999989,957.80487804878044,48.17991819020483,1.1921269556955802,"","","",null,null,null,null,null,null,null,null,null,null,40.625,0,770,1.49,15,23,28.1,1.3,100,0.4,55,43.7,null,2,null,34.375,null,770,2.0699999999999998,28,23,27.3,1.1000000000000001,100,0.4,55,45.4,0,1,null,40.625,null,770,1.49,15,23,28.1,1.3,100,0.4,55,43.7,0,2,null,45,null,770,1.2,10,23,28.6,1.44,100,0.4,55,42.4,0,2,null,48.4375,null,770,1.02,7,23,29.1,1.55,100,0.4,55,41.5,0,2,null,770,1.02,7,23,29.1,1.55,100,0.4,55,41.5,0,2]
[null,780,40.574273048545933,1,561.21951219512198,31.373303714846713,0.77323144341512839,780,40.574273048545933,1,970.2439024390244,48.273846525621934,1.189764915020503,"","","",null,null,null,null,null,null,null,null,null,null,40.9375,0,780,1.51,15,23,28,1.31,100,0.4,55,43.6,null,2,null,34.6875,null,780,2.1,28,23,27.3,1.1100000000000001,100,0.4,55,45.4,0,1,null,40.9375,null,780,1.51,15,23,28,1.31,100,0.4,55,43.6,0,2,null,45.3125,null,780,1.21,10,23,28.6,1.45,100,0.4,55,42.4,0,2,null,48.75,null,780,1.03,8,23,29,1.56,100,0.4,55,41.4,0,2,null,780,1.03,8,23,29,1.56,100,0.4,55,41.4,0,2]
[null,790,40.737210188297638,1,568.41463414634143,31.502146611851686,0.77330152129320673,790,40.737210188297638,1,982.68292682926824,48.315140570992412,1.1860198660553256,"","","",null,null,null,null,null,null,null,null,null,null,40.9375,0,790,1.53,16,23,28,1.31,100,0.4,55,43.6,null,2,null,34.6875,null,790,2.13,29,23,27.2,1.1100000000000001,100,0.4,55,45.3,0,1,null,40.9375,null,790,1.53,16,23,28,1.31,100,0.4,55,43.6,0,2,null,45.3125,null,790,1.23,11,23,28.5,1.45,100,0.4,55,42.3,0,2,null,48.75,null,790,1.04,8,23,28.9,1.56,100,0.4,55,41.4,0,2,null,790,1.04,8,23,28.9,1.56,100,0.4,55,41.4,0,2]
[null,800,40.904077186822491,1,575.60975609756099,31.627343830292062,0.77320761169698293,800,40.904077186822491,1,995.1219512195122,48.292403943380236,1.1806256799979329,"","","",null,null,null,null,null,null,null,null,null,null,40.9375,0,800,1.55,16,23,27.9,1.31,100,0.4,55,43.5,null,2,null,34.6875,null,800,2.15,30,23,27.2,1.1100000000000001,100,0.4,55,45.3,0,1,null,40.9375,null,800,1.55,16,23,27.9,1.31,100,0.4,55,43.5,0,2,null,45.625,null,800,1.24,11,23,28.5,1.46,100,0.4,55,42.3,0,2,null,49.0625,null,800,1.06,8,23,28.9,1.57,100,0.4,55,41.3,0,2,null,800,1.06,8,23,28.9,1.57,100,0.4,55,41.3,0,2]
[null,810,41.074907888325498,1,582.80487804878044,31.748964560931597,0.77295278780054033,810,41.074907888325498,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,41.25,0,810,1.57,16,23,27.9,1.32,100,0.4,55,43.5,null,2,null,35,null,810,2.1800000000000002,30,23,27.1,1.1200000000000001,100,0.4,55,45.3,0,1,null,41.25,null,810,1.57,16,23,27.9,1.32,100,0.4,55,43.5,0,2,null,45.625,null,810,1.26,11,23,28.4,1.46,100,0.4,55,42.2,0,2,null,49.375,null,810,1.07,8,23,28.8,1.58,100,0.4,55,41.3,0,2,null,810,1.07,8,23,28.8,1.58,100,0.4,55,41.3,0,2]
[null,820,41.249575343309488,1,590,31.867095294387326,0.77254359661077188,820,41.249575343309488,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,41.25,0,820,1.59,17,23,27.8,1.32,100,0.4,55,43.5,null,2,null,35,null,820,2.21,31,23,27.1,1.1200000000000001,100,0.4,55,45.2,0,1,null,41.25,null,820,1.59,17,23,27.8,1.32,100,0.4,55,43.5,0,2,null,45.9375,null,820,1.28,11,23,28.4,1.47,100,0.4,55,42.2,0,2,null,49.375,null,820,1.08,8,23,28.8,1.58,100,0.4,55,41.2,0,2,null,820,1.08,8,23,28.8,1.58,100,0.4,55,41.2,0,2]
[null,830,41.427772139743638,1,597.19512195121945,31.98183956809126,0.77199033199783285,830,41.427772139743638,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,41.5625,0,830,1.61,17,23,27.8,1.33,100,0.4,55,43.4,null,2,null,35.3125,null,830,2.23,32,23,27.1,1.1299999999999999,100,0.4,55,45.2,0,1,null,41.5625,null,830,1.61,17,23,27.8,1.33,100,0.4,55,43.4,0,2,null,45.9375,null,830,1.29,12,23,28.3,1.47,100,0.4,55,42.1,0,2,null,49.6875,null,830,1.1000000000000001,9,23,28.7,1.59,100,0.4,55,41.2,0,2,null,830,1.1000000000000001,9,23,28.7,1.59,100,0.4,55,41.2,0,2]
[null,840,41.608989922618491,1,604.39024390243901,32.093317607032986,0.77130729841598922,840,41.608989922618491,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,41.5625,0,840,1.63,18,23,27.8,1.33,100,0.4,55,43.4,null,2,null,35.3125,null,840,2.2599999999999998,32,23,27,1.1299999999999999,100,0.4,55,45.2,0,1,null,41.5625,null,840,1.63,18,23,27.8,1.33,100,0.4,55,43.4,0,2,null,46.25,null,840,1.31,12,23,28.3,1.48,100,0.4,55,42.1,0,2,null,49.6875,null,840,1.1100000000000001,9,23,28.7,1.59,100,0.4,55,41.1,0,2,null,840,1.1100000000000001,9,23,28.7,1.59,100,0.4,55,41.1,0,2]
[null,850,41.792498101873747,1,611.58536585365846,32.20166585827954,0.77051306623941185,850,41.792498101873747,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,41.875,0,850,1.65,18,23,27.7,1.34,100,0.4,55,43.3,null,2,null,35.3125,null,850,2.29,33,23,27,1.1299999999999999,100,0.4,55,45.1,0,1,null,41.875,null,850,1.65,18,23,27.7,1.34,100,0.4,55,43.3,0,2,null,46.5625,null,850,1.32,12,23,28.2,1.49,100,0.4,55,42.1,0,2,null,50,null,850,1.1200000000000001,9,23,28.6,1.6,100,0.4,55,41.1,0,2,null,850,1.1200000000000001,9,23,28.6,1.6,100,0.4,55,41.1,0,2]
[null,860,41.977321748707965,1,618.78048780487802,32.307036419272663,0.76963072138510247,860,41.977321748707965,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,41.875,0,860,1.66,18,23,27.7,1.34,100,0.4,55,43.3,null,2,null,35.625,null,860,2.31,34,23,27,1.1399999999999999,100,0.4,55,45.1,0,1,null,41.875,null,860,1.66,18,23,27.7,1.34,100,0.4,55,43.3,0,2,null,46.5625,null,860,1.34,12,23,28.2,1.49,100,0.4,55,42,0,2,null,50,null,860,1.1399999999999999,9,23,28.6,1.6,100,0.4,55,41,0,2,null,860,1.1399999999999999,9,23,28.6,1.6,100,0.4,55,41,0,2]
[null,870,42.162218680265909,1,625.97560975609758,32.409596359904441,0.76868811401222115,870,42.162218680265909,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,42.1875,0,870,1.68,19,23,27.6,1.35,100,0.4,55,43.3,null,2,null,35.625,null,870,2.34,35,23,26.9,1.1399999999999999,100,0.4,55,45,0,1,null,42.1875,null,870,1.68,19,23,27.6,1.35,100,0.4,55,43.3,0,2,null,46.875,null,870,1.35,13,23,28.2,1.5,100,0.4,55,42,0,2,null,50.3125,null,870,1.1499999999999999,9,23,28.6,1.61,100,0.4,55,41,0,2,null,870,1.1499999999999999,9,23,28.6,1.61,100,0.4,55,41,0,2]
[null,880,42.345655732705154,1,633.17073170731703,32.509526938372403,0.7677181136024791,880,42.345655732705154,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,42.1875,0,880,1.7,19,23,27.6,1.35,100,0.4,55,43.2,null,2,null,35.625,null,880,2.37,35,23,26.9,1.1399999999999999,100,0.4,55,45,0,1,null,42.1875,null,880,1.7,19,23,27.6,1.35,100,0.4,55,43.2,0,2,null,46.875,null,880,1.37,13,23,28.1,1.5,100,0.4,55,41.9,0,2,null,50.625,null,880,1.1599999999999999,9,23,28.5,1.62,100,0.4,55,40.9,0,2,null,880,1.1599999999999999,9,23,28.5,1.62,100,0.4,55,40.9,0,2]
[null,890,42.525784222639174,1,640.36585365853659,32.607022710810526,0.76675888068518527,890,42.525784222639174,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,42.5,0,890,1.72,20,23,27.6,1.36,100,0.4,55,43.2,null,2,null,35.9375,null,890,2.39,36,23,26.9,1.1499999999999999,100,0.4,55,45,0,1,null,42.5,null,890,1.72,20,23,27.6,1.36,100,0.4,55,43.2,0,2,null,46.875,null,890,1.38,13,23,28.1,1.5,100,0.4,55,41.9,0,2,null,50.625,null,890,1.18,10,23,28.5,1.62,100,0.4,55,40.9,0,2,null,890,1.18,10,23,28.5,1.62,100,0.4,55,40.9,0,2]
[null,900,42.70041459696688,1,647.56097560975604,32.70229053470004,0.7658541689434315,900,42.70041459696688,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,42.5,0,900,1.74,20,23,27.5,1.36,100,0.4,55,43.1,null,2,null,35.9375,null,900,2.42,37,23,26.8,1.1499999999999999,100,0.4,55,45,0,1,null,42.5,null,900,1.74,20,23,27.5,1.36,100,0.4,55,43.1,0,2,null,47.1875,null,900,1.4,13,23,28,1.51,100,0.4,55,41.8,0,2,null,50.9375,null,900,1.19,10,23,28.4,1.63,100,0.4,55,40.799999999999997,0,2,null,900,1.19,10,23,28.4,1.63,100,0.4,55,40.799999999999997,0,2]
[null,910,42.86699027107025,1,654.7560975609756,32.79554846605717,0.76505367553620818,910,42.86699027107025,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,42.8125,0,910,1.76,20,23,27.5,1.37,100,0.4,55,43.1,null,2,null,36.25,null,910,2.4500000000000002,38,23,26.8,1.1599999999999999,100,0.4,55,44.9,0,1,null,42.8125,null,910,1.76,20,23,27.5,1.37,100,0.4,55,43.1,0,2,null,47.1875,null,910,1.42,14,23,28,1.51,100,0.4,55,41.8,0,2,null,50.9375,null,910,1.2,10,23,28.4,1.63,100,0.4,55,40.799999999999997,0,2,null,910,1.2,10,23,28.4,1.63,100,0.4,55,40.799999999999997,0,2]
[null,920,43.022560655399928,1,661.95121951219505,32.887024550400469,0.76441346236495322,920,43.022560655399928,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,42.8125,0,920,1.78,21,23,27.5,1.37,100,0.4,55,43.1,null,2,null,36.25,null,920,2.48,38,23,26.8,1.1599999999999999,100,0.4,55,44.9,0,1,null,42.8125,null,920,1.78,21,23,27.5,1.37,100,0.4,55,43.1,0,2,null,47.5,null,920,1.43,14,23,28,1.52,100,0.4,55,41.8,0,2,null,51.25,null,920,1.22,10,23,28.3,1.64,100,0.4,55,40.799999999999997,0,2,null,920,1.22,10,23,28.3,1.64,100,0.4,55,40.799999999999997,0,2]
[null,930,43.163753370431579,0.99999999999999989,669.14634146341461,32.976955507493813,0.76399647696263551,930,43.163753370431579,0.99999999999999989,"","","","","","",null,null,null,null,null,null,null,null,null,null,{"$f":"IF($AA$13=$AP$13,AP110,IF($AA$13=$BE$13,BE110,IF($AA$13=$BT$13,BT110,IF($AA$13=$CI$13,CI110,\"-\"))))","v":42.8125},{"$f":"IF($AA$13=$AP$13,AQ110,IF($AA$13=$BE$13,BF110,IF($AA$13=$BT$13,BU110,IF($AA$13=$CI$13,CJ110,\"-\"))))","v":0},{"$f":"IF($AA$13=$AP$13,AR110,IF($AA$13=$BE$13,BG110,IF($AA$13=$BT$13,BV110,IF($AA$13=$CI$13,CK110,\"-\"))))","v":930},{"$f":"IF($AA$13=$AP$13,AS110,IF($AA$13=$BE$13,BH110,IF($AA$13=$BT$13,BW110,IF($AA$13=$CI$13,CL110,\"-\"))))","v":1.8},{"$f":"IF($AA$13=$AP$13,AT110,IF($AA$13=$BE$13,BI110,IF($AA$13=$BT$13,BX110,IF($AA$13=$CI$13,CM110,\"-\"))))","v":21},{"$f":"IF($AA$13=$AP$13,AU110,IF($AA$13=$BE$13,BJ110,IF($AA$13=$BT$13,BY110,IF($AA$13=$CI$13,CN110,\"-\"))))","v":23},{"$f":"IF($AA$13=$AP$13,AV110,IF($AA$13=$BE$13,BK110,IF($AA$13=$BT$13,BZ110,IF($AA$13=$CI$13,CO110,\"-\"))))","v":27.4},{"$f":"IF($AA$13=$AP$13,AW110,IF($AA$13=$BE$13,BL110,IF($AA$13=$BT$13,CA110,IF($AA$13=$CI$13,CP110,\"-\"))))","v":1.37},{"$f":"IF($AA$13=$AP$13,AX110,IF($AA$13=$BE$13,BM110,IF($AA$13=$BT$13,CB110,IF($AA$13=$CI$13,CQ110,\"-\"))))","v":100},{"$f":"IF($AA$13=$AP$13,AY110,IF($AA$13=$BE$13,BN110,IF($AA$13=$BT$13,CC110,IF($AA$13=$CI$13,CR110,\"-\"))))","v":0.4},{"$f":"IF($AA$13=$AP$13,AZ110,IF($AA$13=$BE$13,BO110,IF($AA$13=$BT$13,CD110,IF($AA$13=$CI$13,CS110,\"-\"))))","v":55},{"$f":"IF($AA$13=$AP$13,BA110,IF($AA$13=$BE$13,BP110,IF($AA$13=$BT$13,CE110,IF($AA$13=$CI$13,CT110,\"-\"))))","v":43},null,{"$f":"IF($AA$13=$AP$13,BC110,IF($AA$13=$BE$13,BR110,IF($AA$13=$BT$13,CG110,IF($AA$13=$CI$13,CV110,\"-\"))))","v":2},null,36.25,null,930,2.5,39,23,26.8,1.1599999999999999,100,0.4,55,44.9,0,1,null,42.8125,null,930,1.8,21,23,27.4,1.37,100,0.4,55,43,0,2,null,47.5,null,930,1.45,14,23,27.9,1.52,100,0.4,55,41.7,0,2,null,51.25,null,930,1.23,11,23,28.3,1.64,100,0.4,55,40.700000000000003,0,2,null,930,1.23,11,23,28.3,1.64,100,0.4,55,40.700000000000003,0,2]
[null,940,43.28674565001171,1,676.34146341463418,33.065585309871295,0.76387320906999978,940,43.28674565001171,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,43.125,0,940,1.82,22,23,27.4,1.38,100,0.4,55,43,null,2,null,36.5625,null,940,2.5299999999999998,40,23,26.7,1.17,100,0.4,55,44.8,0,1,null,43.125,null,940,1.82,22,23,27.4,1.38,100,0.4,55,43,0,2,null,47.8125,null,940,1.46,14,23,27.9,1.53,100,0.4,55,41.7,0,2,null,51.5625,null,940,1.24,11,23,28.3,1.65,100,0.4,55,40.700000000000003,0,2,null,940,1.24,11,23,28.3,1.65,100,0.4,55,40.700000000000003,0,2]
[null,950,43.38723493307009,1,683.53658536585363,33.153163655135472,0.76412252834913597,950,43.38723493307009,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,43.125,0,950,1.84,22,23,27.4,1.38,100,0.4,55,43,null,2,null,36.5625,null,950,2.56,41,23,26.7,1.17,100,0.4,55,44.8,0,1,null,43.125,null,950,1.84,22,23,27.4,1.38,100,0.4,55,43,0,2,null,47.8125,null,950,1.48,15,23,27.8,1.53,100,0.4,55,41.6,0,2,null,51.5625,null,950,1.26,11,23,28.2,1.65,100,0.4,55,40.6,0,2,null,950,1.26,11,23,28.2,1.65,100,0.4,55,40.6,0,2]
[null,960,43.460408643721564,1,690.73170731707319,33.239944332037823,0.76483276088200736,960,43.460408643721564,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,43.4375,0,960,1.86,23,23,27.3,1.39,100,0.4,55,42.9,null,2,null,36.5625,null,960,2.58,41,23,26.7,1.17,100,0.4,55,44.8,0,1,null,43.4375,null,960,1.86,23,23,27.3,1.39,100,0.4,55,42.9,0,2,null,48.125,null,960,1.49,15,23,27.8,1.54,100,0.4,55,41.6,0,2,null,51.875,null,960,1.27,11,23,28.2,1.66,100,0.4,55,40.6,0,2,null,960,1.27,11,23,28.2,1.66,100,0.4,55,40.6,0,2]
[null,970,{"$f":"$J$4*B114^6+$K$4*B114^5+$L$4*B114^4+$M$4*B114^3+$N$4*B114^2+$O$4*B114","v":43.500913159739412},1,697.92682926829264,33.326183480334436,0.76610307829533564,970,43.500913159739412,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,43.4375,0,970,1.88,23,23,27.3,1.39,100,0.4,55,42.9,null,2,null,36.875,null,970,2.61,42,23,26.6,1.18,100,0.4,55,44.7,0,1,null,43.4375,null,970,1.88,23,23,27.3,1.39,100,0.4,55,42.9,0,2,null,48.125,null,970,1.51,15,23,27.8,1.54,100,0.4,55,41.6,0,2,null,51.875,null,970,1.28,11,23,28.1,1.66,100,0.4,55,40.5,0,2,null,970,1.28,11,23,28.1,1.66,100,0.4,55,40.5,0,2]
[null,980,{"$f":"$J$4*B115^6+$K$4*B115^5+$L$4*B115^4+$M$4*B115^3+$N$4*B115^2+$O$4*B115","v":43.502821969409979},1,705.1219512195122,33.412137744422949,0.76804529526653398,980,43.502821969409979,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,43.4375,0,980,1.9,23,23,27.3,1.39,100,0.4,55,42.8,null,2,null,36.875,null,980,2.64,43,23,26.6,1.18,100,0.4,55,44.7,0,1,null,43.4375,null,980,1.9,23,23,27.3,1.39,100,0.4,55,42.8,0,2,null,48.4375,null,980,1.53,16,23,27.7,1.55,100,0.4,55,41.5,0,2,null,52.1875,null,980,1.3,12,23,28.1,1.67,100,0.4,55,40.5,0,2,null,980,1.3,12,23,28.1,1.67,100,0.4,55,40.5,0,2]
[null,990,{"$f":"$J$4*B116^6+$K$4*B116^5+$L$4*B116^4+$M$4*B116^3+$N$4*B116^2+$O$4*B116","v":43.459603016769563},1,712.31707317073165,33.498062320753689,0.77078620133340714,990,43.459603016769563,1,"","","","","","",null,null,null,null,null,null,null,null,null,null,43.75,0,990,1.92,24,23,27.2,1.4,100,0.4,55,42.8,null,2,null,36.875,null,990,2.66,44,23,26.6,1.18,100,0.4,55,44.7,0,1,null,43.75,null,990,1.92,24,23,27.2,1.4,100,0.4,55,42.8,0,2,null,48.4375,null,990,1.54,16,23,27.7,1.55,100,0.4,55,41.5,0,2,null,52.1875,null,990,1.31,12,23,28.1,1.67,100,0.4,55,40.5,0,2,null,990,1.31,12,23,28.1,1.67,100,0.4,55,40.5,0,2]
[null,1000,{"$f":"$J$4*B117^6+$K$4*B117^5+$L$4*B117^4+$M$4*B117^3+$N$4*B117^2+$O$4*B117","v":43.364085235214247},0.99999999999999989,719.51219512195121,33.584208899021348,0.77447059512162719,1000,43.364085235214247,0.99999999999999989,"","","","","","",null,null,null,null,null,null,null,null,null,null,43.75,0,1000,1.94,24,23,27.2,1.4,100,0.4,55,42.8,null,2,null,37.1875,null,1000,2.69,45,23,26.6,1.19,100,0.4,55,44.7,0,1,null,43.75,null,1000,1.94,24,23,27.2,1.4,100,0.4,55,42.8,0,2,null,48.75,null,1000,1.56,16,23,27.7,1.56,100,0.4,55,41.4,0,2,null,52.1875,null,1000,1.32,12,23,28,1.67,100,0.4,55,40.4,0,2,null,1000,1.32,12,23,28,1.67,100,0.4,55,40.4,0,2]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"q sensibel"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"W/K"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"DH18/(DE18-DA18)*1000","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"DH82/(DE82-DA82)*1000","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"DH114/(DE114-DA114)*1000","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"DH115/(DE115-DA115)*1000","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"DH116/(DE116-DA116)*1000","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"DH117/(DE117-DA117)*1000","v":0}]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"q sensibel"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"W/K"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"DX18/(DU18-DQ18)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"DX82/(DU82-DQ82)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"DX114/(DU114-DQ114)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"DX115/(DU115-DQ115)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"DX116/(DU116-DQ116)*1000","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"BL441/(BJ441-BO441)*1000","v":{"$error":"#DIV/0!"}}]

{"sheet":"Auslegung_BG800_kondensierend","index":8,"n_rows":80091,"n_cols":379,"rows_kept":4500,"cut":true,"hidden":true,"merged":[[62,48,62,51],[63,48,63,51],[117,13,117,14]],"bounds":{"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0}}
["T_VL",{"$f":"IF(ISERROR(D1),1,ROUND(D1,0))","v":6},"°C",{"$f":"Auslegetool!$J$8","v":6},"Vorlauf",null,null,"Volumenstrom","Wassermassenstrom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"T_VL",{"$f":"IF(ISERROR(AF1),1,ROUND(AF1,0))","v":6},"°C",{"$f":"$D$1","v":6},"Vorlauf",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"T_VL",{"$f":"IF(ISERROR(BE1),1,ROUND(BE1,0))","v":6},"°C",{"$f":"$D$1","v":6},"Vorlauf",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"T_VL",{"$f":"IF(ISERROR(CE1),1,ROUND(CE1,0))","v":6},"°C",{"$f":"$D$1","v":6},"Vorlauf",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"T_VL",{"$f":"IF(ISERROR(DE1),1,ROUND(DE1,0))","v":6},"°C",{"$f":"$D$1","v":6},"Vorlauf",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"T_VL",{"$f":"IF(ISERROR(ED1),1,ROUND(ED1,0))","v":6},"°C",{"$f":"D1","v":6},"Vorlauf",null,null,"Volumenstrom","Wassermassenstrom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"T_VL",{"$f":"IF(ISERROR(FF1),1,ROUND(FF1,0))","v":6},"°C",{"$f":"$D$1","v":6},"Vorlauf",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"T_VL",{"$f":"IF(ISERROR(GE1),1,ROUND(GE1,0))","v":6},"°C",{"$f":"$D$1","v":6},"Vorlauf",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"T_VL",{"$f":"IF(ISERROR(HE1),1,ROUND(HE1,0))","v":6},"°C",{"$f":"$D$1","v":6},"Vorlauf",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"T_VL",{"$f":"IF(ISERROR(IE1),1,ROUND(IE1,0))","v":6},"°C",{"$f":"$D$1","v":6},"Vorlauf",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"T_VL",{"$f":"IF(ISERROR(JE1),1,ROUND(JE1,0))","v":6},"°C",{"$f":"D1","v":6},"Vorlauf",null,null,"Volumenstrom","Wassermassenstrom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"T_VL",{"$f":"IF(ISERROR(KG1),1,ROUND(KG1,0))","v":6},"°C",{"$f":"$D$1","v":6},"Vorlauf",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"T_VL",{"$f":"IF(ISERROR(LF1),1,ROUND(LF1,0))","v":6},"°C",{"$f":"$D$1","v":6},"Vorlauf",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"T_VL",{"$f":"IF(ISERROR(MF1),1,ROUND(MF1,0))","v":6},"°C",{"$f":"$D$1","v":6},"Vorlauf",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"T_VL",{"$f":"IF(ISERROR(NF1),1,ROUND(NF1,0))","v":6},"°C",{"$f":"$D$1","v":6},"Vorlauf"]
["m_KW",{"$f":"IF(ISERROR(D2),1,D2)","v":100},"kg/h",{"$f":"I2","v":100},"Kühlwasser",null,null,100,100,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"m_KW",{"$f":"IF(ISERROR(AF2),1,AF2)","v":100},"kg/h",{"$f":"$D$2","v":100},"Kühlwasser",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"m_KW",{"$f":"IF(ISERROR(BE2),1,BE2)","v":100},"kg/h",{"$f":"$D$2","v":100},"Kühlwasser",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"m_KW",{"$f":"IF(ISERROR(CE2),1,CE2)","v":100},"kg/h",{"$f":"$D$2","v":100},"Kühlwasser",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"m_KW",{"$f":"IF(ISERROR(DE2),1,DE2)","v":100},"kg/h",{"$f":"$D$2","v":100},"Kühlwasser",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"m_KW",{"$f":"IF(ISERROR(ED2),1,ED2)","v":200},"kg/h",{"$f":"$EI$3","v":200},"Kühlwasser",null,null,{"$f":"H2","v":100},{"$f":"I2","v":100},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"m_KW",{"$f":"IF(ISERROR(FF2),1,FF2)","v":200},"kg/h",{"$f":"ED2","v":200},"Kühlwasser",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"m_KW",{"$f":"IF(ISERROR(GE2),1,GE2)","v":200},"kg/h",{"$f":"FF2","v":200},"Kühlwasser",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"m_KW",{"$f":"IF(ISERROR(HE2),1,HE2)","v":200},"kg/h",{"$f":"GE2","v":200},"Kühlwasser",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"m_KW",{"$f":"IF(ISERROR(IE2),1,IE2)","v":200},"kg/h",{"$f":"HE2","v":200},"Kühlwasser",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"m_KW",{"$f":"IF(ISERROR(JE2),1,JE2)","v":300},"kg/h",{"$f":"JJ4","v":300},"Kühlwasser",null,null,{"$f":"H2","v":100},{"$f":"I2","v":100},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"m_KW",{"$f":"IF(ISERROR(KG2),1,KG2)","v":300},"kg/h",{"$f":"JE2","v":300},"Kühlwasser",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"m_KW",{"$f":"IF(ISERROR(LF2),1,LF2)","v":300},"kg/h",{"$f":"KG2","v":300},"Kühlwasser",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"m_KW",{"$f":"IF(ISERROR(MF2),1,MF2)","v":300},"kg/h",{"$f":"LF2","v":300},"Kühlwasser",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"m_KW",{"$f":"IF(ISERROR(NF2),1,NF2)","v":300},"kg/h",{"$f":"MF2","v":300},"Kühlwasser"]
["V",{"$f":"IF(ISERROR(D3),1,ROUND(D3,0))","v":100},"m³/h",{"$f":"H2","v":100},"Volumenstrom",null,null,170,200,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"V",{"$f":"IF(ISERROR(AF3),1,ROUND(AF3,0))","v":170},"m³/h",{"$f":"H3","v":170},"Volumenstrom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"V",{"$f":"IF(ISERROR(BE3),1,ROUND(BE3,0))","v":240},"m³/h",{"$f":"H4","v":240},"Volumenstrom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"V",{"$f":"IF(ISERROR(CE3),1,ROUND(CE3,0))","v":310},"m³/h",{"$f":"H5","v":310},"Volumenstrom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"V",{"$f":"IF(ISERROR(DE3),1,ROUND(DE3,0))","v":380},"m³/h",{"$f":"H6","v":380},"Volumenstrom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"V",{"$f":"IF(ISERROR(ED3),1,ROUND(ED3,0))","v":100},"m³/h",{"$f":"EH2","v":100},"Volumenstrom",null,null,{"$f":"H3","v":170},200,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"V",{"$f":"IF(ISERROR(FF3),1,ROUND(FF3,0))","v":170},"m³/h",{"$f":"EH3","v":170},"Volumenstrom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"V",{"$f":"IF(ISERROR(GE3),1,ROUND(GE3,0))","v":240},"m³/h",{"$f":"EH4","v":240},"Volumenstrom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"V",{"$f":"IF(ISERROR(HE3),1,ROUND(HE3,0))","v":310},"m³/h",{"$f":"EH5","v":310},"Volumenstrom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"V",{"$f":"IF(ISERROR(IE3),1,ROUND(IE3,0))","v":380},"m³/h",{"$f":"EH6","v":380},"Volumenstrom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"V",{"$f":"IF(ISERROR(JE3),1,ROUND(JE3,0))","v":100},"m³/h",{"$f":"JI2","v":100},"Volumenstrom",null,null,{"$f":"H3","v":170},200,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"V",{"$f":"IF(ISERROR(KG3),1,ROUND(KG3,0))","v":170},"m³/h",{"$f":"JI3","v":170},"Volumenstrom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"V",{"$f":"IF(ISERROR(LF3),1,ROUND(LF3,0))","v":240},"m³/h",{"$f":"JI4","v":240},"Volumenstrom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"V",{"$f":"IF(ISERROR(MF3),1,ROUND(MF3,0))","v":310},"m³/h",{"$f":"JI5","v":310},"Volumenstrom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"V",{"$f":"IF(ISERROR(NF3),1,ROUND(NF3,0))","v":380},"m³/h",{"$f":"JI6","v":380},"Volumenstrom"]
["rel.Feuchte",1,"%",null,null,null,null,240,300,"rel Feuchte","korrektur totale Leistung",null,"korrektur sens. Leistung",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"rel.Feuchte",1,"%",null,null,null,null,null,4,"rel Feuchte","korrektur totale Leistung",null,"korrektur sens. Leistung",null,null,null,null,null,null,null,null,null,null,null,null,"rel.Feuchte",1,"%",null,null,null,null,null,4,"rel Feuchte","korrektur totale Leistung",null,"korrektur sens. Leistung",null,null,null,null,null,null,null,null,null,null,null,null,null,"rel.Feuchte",1,"%",null,null,null,null,null,4,"rel Feuchte","korrektur totale Leistung",null,"korrektur sens. Leistung",null,null,null,null,null,null,null,null,null,null,null,null,null,"rel.Feuchte",1,"%",null,null,null,null,null,4,"rel Feuchte","korrektur totale Leistung",null,"korrektur sens. Leistung",null,null,null,null,null,null,null,null,null,null,null,null,"rel.Feuchte",1,"%",null,null,null,null,240,300,"rel Feuchte","korrektur totale Leistung",null,"korrektur sens. Leistung",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"rel.Feuchte",1,"%",null,null,null,null,null,4,"rel Feuchte","korrektur totale Leistung",null,"korrektur sens. Leistung",null,null,null,null,null,null,null,null,null,null,null,null,"rel.Feuchte",1,"%",null,null,null,null,null,4,"rel Feuchte","korrektur totale Leistung",null,"korrektur sens. Leistung",null,null,null,null,null,null,null,null,null,null,null,null,null,"rel.Feuchte",1,"%",null,null,null,null,null,4,"rel Feuchte","korrektur totale Leistung",null,"korrektur sens. Leistung",null,null,null,null,null,null,null,null,null,null,null,null,null,"rel.Feuchte",1,"%",null,null,null,null,null,4,"rel Feuchte","korrektur totale Leistung",null,"korrektur sens. Leistung",null,null,null,null,null,null,null,null,null,null,null,null,null,"rel.Feuchte",1,"%",null,null,null,null,240,300,"rel Feuchte","korrektur totale Leistung",null,"korrektur sens. Leistung",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"rel.Feuchte",1,"%",null,null,null,null,null,4,"rel Feuchte","korrektur totale Leistung",null,"korrektur sens. Leistung",null,null,null,null,null,null,null,null,null,null,null,null,"rel.Feuchte",1,"%",null,null,null,null,null,4,"rel Feuchte","korrektur totale Leistung",null,"korrektur sens. Leistung",null,null,null,null,null,null,null,null,null,null,null,null,null,"rel.Feuchte",1,"%",null,null,null,null,null,4,"rel Feuchte","korrektur totale Leistung",null,"korrektur sens. Leistung",null,null,null,null,null,null,null,null,null,null,null,null,null,"rel.Feuchte",1,"%",null,null,null,null,null,4,"rel Feuchte","korrektur totale Leistung",null,"korrektur sens. Leistung"]
[null,50,"%",null,{"$f":"CONCATENATE(B1, \" \",C1, \" \",E1, \"; \")","v":"6 °C Vorlauf; "},null,null,310,null,null,null,{"$f":"J18*M5+K18","v":33.836814621409921},1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,50,"%",null,{"$f":"CONCATENATE(AD1, \" \",AE1, \" \",AG1, \"; \")","v":"6 °C Vorlauf; "},null,null,null,null,null,null,{"$f":"AL18*AO5+AM18","v":40.271098237517762},1,null,null,null,null,null,null,null,null,null,null,null,null,null,50,"%",null,{"$f":"CONCATENATE(BC1, \" \",BD1, \" \",BF1, \"; \")","v":"6 °C Vorlauf; "},null,null,null,null,null,null,{"$f":"BK18*BN5+BL18","v":45.098915807790121},1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,50,"%",null,{"$f":"CONCATENATE(CC1, \" \",CD1, \" \",CF1, \"; \")","v":"6 °C Vorlauf; "},null,null,null,null,null,null,{"$f":"CK18*CN5+CL18","v":49.335483027582903},1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,50,"%",null,{"$f":"CONCATENATE(DC1, \" \",DD1, \" \",DF1, \"; \")","v":"6 °C Vorlauf; "},null,null,null,null,null,null,{"$f":"DK18*DN5+DL18","v":52.840858937362071},1,null,null,null,null,null,null,null,null,null,null,null,null,null,50,"%",null,{"$f":"CONCATENATE(EB1, \" \",EC1, \" \",EE1, \"; \")","v":"6 °C Vorlauf; "},null,null,310,null,null,null,{"$f":"EJ18*EM5+EK18","v":29.884658217107649},1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,50,"%",null,{"$f":"CONCATENATE(FD1, \" \",FE1, \" \",FG1, \"; \")","v":"6 °C Vorlauf; "},null,null,null,null,null,null,{"$f":"FL18*FO5+FM18","v":32.318621931997328},1,null,null,null,null,null,null,null,null,null,null,null,null,null,50,"%",null,{"$f":"CONCATENATE(GC1, \" \",GD1, \" \",GF1, \"; \")","v":"6 °C Vorlauf; "},null,null,null,null,null,null,{"$f":"GK18*GN5+GL18","v":34.752446654901405},1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,50,"%",null,{"$f":"CONCATENATE(HC1, \" \",HD1, \" \",HF1, \"; \")","v":"6 °C Vorlauf; "},null,null,null,null,null,null,{"$f":"HK18*HN5+HL18","v":36.782502414292615},1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,50,"%",null,{"$f":"CONCATENATE(IC1, \" \",ID1, \" \",IF1, \"; \")","v":"6 °C Vorlauf; "},null,null,null,null,null,null,{"$f":"IK18*IN5+IL18","v":38.916164760095398},1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,50,"%",null,{"$f":"CONCATENATE(JC1, \" \",JD1, \" \",JF1, \"; \")","v":"6 °C Vorlauf; "},null,null,310,null,null,null,{"$f":"JK18*JN5+JL18","v":28.591527093596021},1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,50,"%",null,{"$f":"CONCATENATE(KE1, \" \",KF1, \" \",KH1, \"; \")","v":"6 °C Vorlauf; "},null,null,null,null,null,null,{"$f":"KM18*KP5+KN18","v":30.673792887683796},1,null,null,null,null,null,null,null,null,null,null,null,null,null,50,"%",null,{"$f":"CONCATENATE(LD1, \" \",LE1, \" \",LG1, \"; \")","v":"6 °C Vorlauf; "},null,null,null,null,null,null,{"$f":"LL18*LO5+LM18","v":31.955234725044075},1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,50,"%",null,{"$f":"CONCATENATE(MD1, \" \",ME1, \" \",MG1, \"; \")","v":"6 °C Vorlauf; "},null,null,null,null,null,null,{"$f":"ML18*MO5+MM18","v":33.584453678807158},1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,50,"%",null,{"$f":"CONCATENATE(ND1, \" \",NE1, \" \",NG1, \"; \")","v":"6 °C Vorlauf; "},null,null,null,null,null,null,{"$f":"NL18*NO5+NM18","v":34.713979973355123},1]
[null,60,"%",null,{"$f":"CONCATENATE(B2, \" \",C2, \" \",E2, \"; \")","v":"100 kg/h Kühlwasser; "},null,null,380,null,{"$f":"IF(C13=1,J7,B5)","v":60},{"$f":"IF(C13=1,K7,C13)","v":1.5932203389830508},{"$f":"IF(C14=1,L7,B5)","v":50},{"$f":"IF(C14=1,M7,C14)","v":0.89830508474576276},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,60,"%",null,{"$f":"CONCATENATE(AD2, \" \",AE2, \" \",AG2, \"; \")","v":"100 kg/h Kühlwasser; "},null,null,null,null,{"$f":"IF(AE13=1,AL7,AD5)","v":60},{"$f":"IF(AE13=1,AM7,AE13)","v":1.367816091954023},{"$f":"IF(AE14=1,AN7,AD5)","v":50},{"$f":"IF(AE14=1,AO7,AE14)","v":0.86206896551724144},null,null,null,null,null,null,null,null,null,null,null,null,null,60,"%",null,{"$f":"CONCATENATE(BC2, \" \",BD2, \" \",BF2, \"; \")","v":"100 kg/h Kühlwasser; "},null,null,null,null,{"$f":"IF(BD13=1,BK7,BC5)","v":60},{"$f":"IF(BD13=1,BL7,BD13)","v":1.2358490566037736},{"$f":"IF(BD14=1,BM7,BC5)","v":50},{"$f":"IF(BD14=1,BN7,BD14)","v":0.85849056603773588},null,null,null,null,null,null,null,null,null,null,null,null,null,null,60,"%",null,{"$f":"CONCATENATE(CC2, \" \",CD2, \" \",CF2, \"; \")","v":"100 kg/h Kühlwasser; "},null,null,null,null,{"$f":"IF(CD13=1,CK7,CC5)","v":60},{"$f":"IF(CD13=1,CL7,CD13)","v":1.1499999999999999},{"$f":"IF(CD14=1,CM7,CC5)","v":50},{"$f":"IF(CD14=1,CN7,CD14)","v":0.87500000000000011},null,null,null,null,null,null,null,null,null,null,null,null,null,null,60,"%",null,{"$f":"CONCATENATE(DC2, \" \",DD2, \" \",DF2, \"; \")","v":"100 kg/h Kühlwasser; "},null,null,null,null,{"$f":"IF(DD13=1,DK7,DC5)","v":60},{"$f":"IF(DD13=1,DL7,DD13)","v":1.0923076923076922},{"$f":"IF(DD14=1,DM7,DC5)","v":50},{"$f":"IF(DD14=1,DN7,DD14)","v":0.89999999999999991},null,null,null,null,null,null,null,null,null,null,null,null,null,60,"%",null,{"$f":"CONCATENATE(EB2, \" \",EC2, \" \",EE2, \"; \")","v":"200 kg/h Kühlwasser; "},null,null,380,null,{"$f":"IF(EC13=1,EJ7,EB5)","v":60},{"$f":"IF(EC13=1,EK7,EC13)","v":1.7460317460317463},{"$f":"IF(EC14=1,EL7,EB5)","v":50},{"$f":"IF(EC14=1,EM7,EC14)","v":0.95238095238095233},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,60,"%",null,{"$f":"CONCATENATE(FD2, \" \",FE2, \" \",FG2, \"; \")","v":"200 kg/h Kühlwasser; "},null,null,null,null,{"$f":"IF(FE13=1,FL7,FD5)","v":60},{"$f":"IF(FE13=1,FM7,FE13)","v":1.6494845360824744},{"$f":"IF(FE14=1,FN7,FD5)","v":50},{"$f":"IF(FE14=1,FO7,FE14)","v":0.91752577319587636},null,null,null,null,null,null,null,null,null,null,null,null,null,60,"%",null,{"$f":"CONCATENATE(GC2, \" \",GD2, \" \",GF2, \"; \")","v":"200 kg/h Kühlwasser; "},null,null,null,null,{"$f":"IF(GD13=1,GK7,GC5)","v":60},{"$f":"IF(GD13=1,GL7,GD13)","v":1.544},{"$f":"IF(GD14=1,GM7,GC5)","v":50},{"$f":"IF(GD14=1,GN7,GD14)","v":0.89600000000000013},null,null,null,null,null,null,null,null,null,null,null,null,null,null,60,"%",null,{"$f":"CONCATENATE(HC2, \" \",HD2, \" \",HF2, \"; \")","v":"200 kg/h Kühlwasser; "},null,null,null,null,{"$f":"IF(HD13=1,HK7,HC5)","v":60},{"$f":"IF(HD13=1,HL7,HD13)","v":1.4594594594594597},{"$f":"IF(HD14=1,HM7,HC5)","v":50},{"$f":"IF(HD14=1,HN7,HD14)","v":0.8783783783783784},null,null,null,null,null,null,null,null,null,null,null,null,null,null,60,"%",null,{"$f":"CONCATENATE(IC2, \" \",ID2, \" \",IF2, \"; \")","v":"200 kg/h Kühlwasser; "},null,null,null,null,{"$f":"IF(ID13=1,IK7,IC5)","v":60},{"$f":"IF(ID13=1,IL7,ID13)","v":1.3892215568862276},{"$f":"IF(ID14=1,IM7,IC5)","v":50},{"$f":"IF(ID14=1,IN7,ID14)","v":0.86826347305389218},null,null,null,null,null,null,null,null,null,null,null,null,null,null,60,"%",null,{"$f":"CONCATENATE(JC2, \" \",JD2, \" \",JF2, \"; \")","v":"300 kg/h Kühlwasser; "},null,null,380,null,{"$f":"IF(JD13=1,JK7,JC5)","v":60},{"$f":"IF(JD13=1,JL7,JD13)","v":1.8095238095238093},{"$f":"IF(JD14=1,JM7,JC5)","v":50},{"$f":"IF(JD14=1,JN7,JD14)","v":0.96825396825396826},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,60,"%",null,{"$f":"CONCATENATE(KE2, \" \",KF2, \" \",KH2, \"; \")","v":"300 kg/h Kühlwasser; "},null,null,null,null,{"$f":"IF(KF13=1,KM7,KE5)","v":60},{"$f":"IF(KF13=1,KN7,KF13)","v":1.73},{"$f":"IF(KF14=1,KO7,KE5)","v":50},{"$f":"IF(KF14=1,KP7,KF14)","v":0.94},null,null,null,null,null,null,null,null,null,null,null,null,null,60,"%",null,{"$f":"CONCATENATE(LD2, \" \",LE2, \" \",LG2, \"; \")","v":"300 kg/h Kühlwasser; "},null,null,null,null,{"$f":"IF(LE13=1,LL7,LD5)","v":60},{"$f":"IF(LE13=1,LM7,LE13)","v":1.6641221374045803},{"$f":"IF(LE14=1,LN7,LD5)","v":50},{"$f":"IF(LE14=1,LO7,LE14)","v":0.92366412213740456},null,null,null,null,null,null,null,null,null,null,null,null,null,null,60,"%",null,{"$f":"CONCATENATE(MD2, \" \",ME2, \" \",MG2, \"; \")","v":"300 kg/h Kühlwasser; "},null,null,null,null,{"$f":"IF(ME13=1,ML7,MD5)","v":60},{"$f":"IF(ME13=1,MM7,ME13)","v":1.5987261146496814},{"$f":"IF(ME14=1,MN7,MD5)","v":50},{"$f":"IF(ME14=1,MO7,ME14)","v":0.90445859872611456},null,null,null,null,null,null,null,null,null,null,null,null,null,null,60,"%",null,{"$f":"CONCATENATE(ND2, \" \",NE2, \" \",NG2, \"; \")","v":"300 kg/h Kühlwasser; "},null,null,null,null,{"$f":"IF(NE13=1,NL7,ND5)","v":60},{"$f":"IF(NE13=1,NM7,NE13)","v":1.5444444444444443},{"$f":"IF(NE14=1,NN7,ND5)","v":50},{"$f":"IF(NE14=1,NO7,NE14)","v":0.89444444444444449}]
[null,70,"%",null,{"$f":"CONCATENATE(B3, \" \",C3, \" \",E3, \"; \")","v":"100 m³/h Volumenstrom; "},null,null,null,null,{"$f":"IF(D13=1,J8,B6)","v":60},{"$f":"IF(D13=1,K8,D13)","v":1.5932203389830508},{"$f":"IF(D14=1,L8,B6)","v":60},{"$f":"IF(D14=1,M8,D14)","v":0.88135593220338992},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,70,"%",null,{"$f":"CONCATENATE(AD3, \" \",AE3, \" \",AG3, \"; \")","v":"170 m³/h Volumenstrom; "},null,null,null,null,{"$f":"IF(AF13=1,AL8,AD6)","v":60},{"$f":"IF(AF13=1,AM8,AF13)","v":1.367816091954023},{"$f":"IF(AF14=1,AN8,AD6)","v":60},{"$f":"IF(AF14=1,AO8,AF14)","v":0.80459770114942519},null,null,null,null,null,null,null,null,null,null,null,null,null,70,"%",null,{"$f":"CONCATENATE(BC3, \" \",BD3, \" \",BF3, \"; \")","v":"240 m³/h Volumenstrom; "},null,null,null,null,{"$f":"IF(BE13=1,BK8,BC6)","v":60},{"$f":"IF(BE13=1,BL8,BE13)","v":1.2358490566037736},{"$f":"IF(BE14=1,BM8,BC6)","v":60},{"$f":"IF(BE14=1,BN8,BE14)","v":0.78301886792452824},null,null,null,null,null,null,null,null,null,null,null,null,null,null,70,"%",null,{"$f":"CONCATENATE(CC3, \" \",CD3, \" \",CF3, \"; \")","v":"310 m³/h Volumenstrom; "},null,null,null,null,{"$f":"IF(CE13=1,CK8,CC6)","v":60},{"$f":"IF(CE13=1,CL8,CE13)","v":1.1499999999999999},{"$f":"IF(CE14=1,CM8,CC6)","v":60},{"$f":"IF(CE14=1,CN8,CE14)","v":0.78333333333333333},null,null,null,null,null,null,null,null,null,null,null,null,null,null,70,"%",null,{"$f":"CONCATENATE(DC3, \" \",DD3, \" \",DF3, \"; \")","v":"380 m³/h Volumenstrom; "},null,null,null,null,{"$f":"IF(DE13=1,DK8,DC6)","v":60},{"$f":"IF(DE13=1,DL8,DE13)","v":1.0923076923076922},{"$f":"IF(DE14=1,DM8,DC6)","v":60},{"$f":"IF(DE14=1,DN8,DE14)","v":0.8},null,null,null,null,null,null,null,null,null,null,null,null,null,70,"%",null,{"$f":"CONCATENATE(EB3, \" \",EC3, \" \",EE3, \"; \")","v":"100 m³/h Volumenstrom; "},null,null,null,null,{"$f":"IF(ED13=1,EJ8,EB6)","v":60},{"$f":"IF(ED13=1,EK8,ED13)","v":1.7460317460317463},{"$f":"IF(ED14=1,EL8,EB6)","v":60},{"$f":"IF(ED14=1,EM8,ED14)","v":0.9365079365079364},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,70,"%",null,{"$f":"CONCATENATE(FD3, \" \",FE3, \" \",FG3, \"; \")","v":"170 m³/h Volumenstrom; "},null,null,null,null,{"$f":"IF(FF13=1,FL8,FD6)","v":60},{"$f":"IF(FF13=1,FM8,FF13)","v":1.6494845360824744},{"$f":"IF(FF14=1,FN8,FD6)","v":60},{"$f":"IF(FF14=1,FO8,FF14)","v":0.89690721649484539},null,null,null,null,null,null,null,null,null,null,null,null,null,70,"%",null,{"$f":"CONCATENATE(GC3, \" \",GD3, \" \",GF3, \"; \")","v":"240 m³/h Volumenstrom; "},null,null,null,null,{"$f":"IF(GE13=1,GK8,GC6)","v":60},{"$f":"IF(GE13=1,GL8,GE13)","v":1.544},{"$f":"IF(GE14=1,GM8,GC6)","v":60},{"$f":"IF(GE14=1,GN8,GE14)","v":0.85600000000000009},null,null,null,null,null,null,null,null,null,null,null,null,null,null,70,"%",null,{"$f":"CONCATENATE(HC3, \" \",HD3, \" \",HF3, \"; \")","v":"310 m³/h Volumenstrom; "},null,null,null,null,{"$f":"IF(HE13=1,HK8,HC6)","v":60},{"$f":"IF(HE13=1,HL8,HE13)","v":1.4594594594594597},{"$f":"IF(HE14=1,HM8,HC6)","v":60},{"$f":"IF(HE14=1,HN8,HE14)","v":0.82432432432432434},null,null,null,null,null,null,null,null,null,null,null,null,null,null,70,"%",null,{"$f":"CONCATENATE(IC3, \" \",ID3, \" \",IF3, \"; \")","v":"380 m³/h Volumenstrom; "},null,null,null,null,{"$f":"IF(IE13=1,IK8,IC6)","v":60},{"$f":"IF(IE13=1,IL8,IE13)","v":1.3892215568862276},{"$f":"IF(IE14=1,IM8,IC6)","v":60},{"$f":"IF(IE14=1,IN8,IE14)","v":0.80838323353293418},null,null,null,null,null,null,null,null,null,null,null,null,null,null,70,"%",null,{"$f":"CONCATENATE(JC3, \" \",JD3, \" \",JF3, \"; \")","v":"100 m³/h Volumenstrom; "},null,null,null,null,{"$f":"IF(JE13=1,JK8,JC6)","v":60},{"$f":"IF(JE13=1,JL8,JE13)","v":1.8095238095238093},{"$f":"IF(JE14=1,JM8,JC6)","v":60},{"$f":"IF(JE14=1,JN8,JE14)","v":0.96825396825396826},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,70,"%",null,{"$f":"CONCATENATE(KE3, \" \",KF3, \" \",KH3, \"; \")","v":"170 m³/h Volumenstrom; "},null,null,null,null,{"$f":"IF(KG13=1,KM8,KE6)","v":60},{"$f":"IF(KG13=1,KN8,KG13)","v":1.73},{"$f":"IF(KG14=1,KO8,KE6)","v":60},{"$f":"IF(KG14=1,KP8,KG14)","v":0.93},null,null,null,null,null,null,null,null,null,null,null,null,null,70,"%",null,{"$f":"CONCATENATE(LD3, \" \",LE3, \" \",LG3, \"; \")","v":"240 m³/h Volumenstrom; "},null,null,null,null,{"$f":"IF(LF13=1,LL8,LD6)","v":60},{"$f":"IF(LF13=1,LM8,LF13)","v":1.6641221374045803},{"$f":"IF(LF14=1,LN8,LD6)","v":60},{"$f":"IF(LF14=1,LO8,LF14)","v":0.89312977099236635},null,null,null,null,null,null,null,null,null,null,null,null,null,null,70,"%",null,{"$f":"CONCATENATE(MD3, \" \",ME3, \" \",MG3, \"; \")","v":"310 m³/h Volumenstrom; "},null,null,null,null,{"$f":"IF(MF13=1,ML8,MD6)","v":60},{"$f":"IF(MF13=1,MM8,MF13)","v":1.5987261146496814},{"$f":"IF(MF14=1,MN8,MD6)","v":60},{"$f":"IF(MF14=1,MO8,MF14)","v":0.87261146496815289},null,null,null,null,null,null,null,null,null,null,null,null,null,null,70,"%",null,{"$f":"CONCATENATE(ND3, \" \",NE3, \" \",NG3, \"; \")","v":"380 m³/h Volumenstrom; "},null,null,null,null,{"$f":"IF(NF13=1,NL8,ND6)","v":60},{"$f":"IF(NF13=1,NM8,NF13)","v":1.5444444444444443},{"$f":"IF(NF14=1,NN8,ND6)","v":60},{"$f":"IF(NF14=1,NO8,NF14)","v":0.85}]
[null,80,"%",null,{"$f":"CONCATENATE(B12, \" \",C12, \" \",A12, \"; \")","v":"26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(E13=1,J9,B7)","v":70},{"$f":"IF(E13=1,K9,E13)","v":1.8135593220338986},{"$f":"IF(E14=1,L9,B7)","v":70},{"$f":"IF(E14=1,M9,E14)","v":0.84745762711864414},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,80,"%",null,{"$f":"CONCATENATE(AD12, \" \",AE12, \" \",AC12, \"; \")","v":"26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(AG13=1,AL9,AD7)","v":70},{"$f":"IF(AG13=1,AM9,AG13)","v":1.5517241379310347},{"$f":"IF(AG14=1,AN9,AD7)","v":70},{"$f":"IF(AG14=1,AO9,AG14)","v":0.74712643678160917},null,null,null,null,null,null,null,null,null,null,null,null,null,80,"%",null,{"$f":"CONCATENATE(BC12, \" \",BD12, \" \",BB12, \"; \")","v":"26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(BF13=1,BK9,BC7)","v":70},{"$f":"IF(BF13=1,BL9,BF13)","v":1.4056603773584906},{"$f":"IF(BF14=1,BM9,BC7)","v":70},{"$f":"IF(BF14=1,BN9,BF14)","v":0.70754716981132071},null,null,null,null,null,null,null,null,null,null,null,null,null,null,80,"%",null,{"$f":"CONCATENATE(CC12, \" \",CD12, \" \",CB12, \"; \")","v":"26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(CF13=1,CK9,CC7)","v":70},{"$f":"IF(CF13=1,CL9,CF13)","v":1.3},{"$f":"IF(CF14=1,CM9,CC7)","v":70},{"$f":"IF(CF14=1,CN9,CF14)","v":0.69166666666666665},null,null,null,null,null,null,null,null,null,null,null,null,null,null,80,"%",null,{"$f":"CONCATENATE(DC12, \" \",DD12, \" \",DB12, \"; \")","v":"26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(DF13=1,DK9,DC7)","v":70},{"$f":"IF(DF13=1,DL9,DF13)","v":1.2384615384615385},{"$f":"IF(DF14=1,DM9,DC7)","v":70},{"$f":"IF(DF14=1,DN9,DF14)","v":0.7},null,null,null,null,null,null,null,null,null,null,null,null,null,80,"%",null,{"$f":"CONCATENATE(EB12, \" \",EC12, \" \",EA12, \"; \")","v":"26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(EE13=1,EJ9,EB7)","v":70},{"$f":"IF(EE13=1,EK9,EE13)","v":2},{"$f":"IF(EE14=1,EL9,EB7)","v":70},{"$f":"IF(EE14=1,EM9,EE14)","v":0.92063492063492058},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,80,"%",null,{"$f":"CONCATENATE(FD12, \" \",FE12, \" \",FC12, \"; \")","v":"26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(FG13=1,FL9,FD7)","v":70},{"$f":"IF(FG13=1,FM9,FG13)","v":1.8865979381443301},{"$f":"IF(FG14=1,FN9,FD7)","v":70},{"$f":"IF(FG14=1,FO9,FG14)","v":0.865979381443299},null,null,null,null,null,null,null,null,null,null,null,null,null,80,"%",null,{"$f":"CONCATENATE(GC12, \" \",GD12, \" \",GB12, \"; \")","v":"26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(GF13=1,GK9,GC7)","v":70},{"$f":"IF(GF13=1,GL9,GF13)","v":1.7600000000000002},{"$f":"IF(GF14=1,GM9,GC7)","v":70},{"$f":"IF(GF14=1,GN9,GF14)","v":0.81600000000000006},null,null,null,null,null,null,null,null,null,null,null,null,null,null,80,"%",null,{"$f":"CONCATENATE(HC12, \" \",HD12, \" \",HB12, \"; \")","v":"26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(HF13=1,HK9,HC7)","v":70},{"$f":"IF(HF13=1,HL9,HF13)","v":1.6554054054054055},{"$f":"IF(HF14=1,HM9,HC7)","v":70},{"$f":"IF(HF14=1,HN9,HF14)","v":0.77702702702702697},null,null,null,null,null,null,null,null,null,null,null,null,null,null,80,"%",null,{"$f":"CONCATENATE(IC12, \" \",ID12, \" \",IB12, \"; \")","v":"26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(IF13=1,IK9,IC7)","v":70},{"$f":"IF(IF13=1,IL9,IF13)","v":1.5808383233532937},{"$f":"IF(IF14=1,IM9,IC7)","v":70},{"$f":"IF(IF14=1,IN9,IF14)","v":0.75449101796407192},null,null,null,null,null,null,null,null,null,null,null,null,null,null,80,"%",null,{"$f":"CONCATENATE(JC12, \" \",JD12, \" \",JB12, \"; \")","v":"26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(JF13=1,JK9,JC7)","v":70},{"$f":"IF(JF13=1,JL9,JF13)","v":2.0634920634920637},{"$f":"IF(JF14=1,JM9,JC7)","v":70},{"$f":"IF(JF14=1,JN9,JF14)","v":0.95238095238095233},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,80,"%",null,{"$f":"CONCATENATE(KE12, \" \",KF12, \" \",KD12, \"; \")","v":"26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(KH13=1,KM9,KE7)","v":70},{"$f":"IF(KH13=1,KN9,KH13)","v":1.98},{"$f":"IF(KH14=1,KO9,KE7)","v":70},{"$f":"IF(KH14=1,KP9,KH14)","v":0.91},null,null,null,null,null,null,null,null,null,null,null,null,null,80,"%",null,{"$f":"CONCATENATE(LD12, \" \",LE12, \" \",LC12, \"; \")","v":"26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(LG13=1,LL9,LD7)","v":70},{"$f":"IF(LG13=1,LM9,LG13)","v":1.9007633587786261},{"$f":"IF(LG14=1,LN9,LD7)","v":70},{"$f":"IF(LG14=1,LO9,LG14)","v":0.86259541984732813},null,null,null,null,null,null,null,null,null,null,null,null,null,null,80,"%",null,{"$f":"CONCATENATE(MD12, \" \",ME12, \" \",MC12, \"; \")","v":"26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(MG13=1,ML9,MD7)","v":70},{"$f":"IF(MG13=1,MM9,MG13)","v":1.8280254777070064},{"$f":"IF(MG14=1,MN9,MD7)","v":70},{"$f":"IF(MG14=1,MO9,MG14)","v":0.83439490445859876},null,null,null,null,null,null,null,null,null,null,null,null,null,null,80,"%",null,{"$f":"CONCATENATE(ND12, \" \",NE12, \" \",NC12, \"; \")","v":"26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(NG13=1,NL9,ND7)","v":70},{"$f":"IF(NG13=1,NM9,NG13)","v":1.7611111111111111},{"$f":"IF(NG14=1,NN9,ND7)","v":70},{"$f":"IF(NG14=1,NO9,NG14)","v":0.80555555555555547}]
[null,90,"%",null,{"$f":"CONCATENATE(E5,E6,E7,E8)","v":"6 °C Vorlauf; 100 kg/h Kühlwasser; 100 m³/h Volumenstrom; 26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(F13=1,J10,B8)","v":80},{"$f":"IF(F13=1,K10,F13)","v":2.0508474576271185},{"$f":"IF(F14=1,L10,B8)","v":80},{"$f":"IF(F14=1,M10,F14)","v":0.81355932203389836},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,90,"%",null,{"$f":"CONCATENATE(AG5,AG6,AG7,AG8)","v":"6 °C Vorlauf; 100 kg/h Kühlwasser; 170 m³/h Volumenstrom; 26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(AH13=1,AL10,AD8)","v":80},{"$f":"IF(AH13=1,AM10,AH13)","v":1.7471264367816093},{"$f":"IF(AH14=1,AN10,AD8)","v":80},{"$f":"IF(AH14=1,AO10,AH14)","v":0.68965517241379304},null,null,null,null,null,null,null,null,null,null,null,null,null,90,"%",null,{"$f":"CONCATENATE(BF5,BF6,BF7,BF8)","v":"6 °C Vorlauf; 100 kg/h Kühlwasser; 240 m³/h Volumenstrom; 26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(BG13=1,BK10,BC8)","v":80},{"$f":"IF(BG13=1,BL10,BG13)","v":1.5660377358490565},{"$f":"IF(BG14=1,BM10,BC8)","v":80},{"$f":"IF(BG14=1,BN10,BG14)","v":0.64150943396226412},null,null,null,null,null,null,null,null,null,null,null,null,null,null,90,"%",null,{"$f":"CONCATENATE(CF5,CF6,CF7,CF8)","v":"6 °C Vorlauf; 100 kg/h Kühlwasser; 310 m³/h Volumenstrom; 26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(CG13=1,CK10,CC8)","v":80},{"$f":"IF(CG13=1,CL10,CG13)","v":1.45},{"$f":"IF(CG14=1,CM10,CC8)","v":80},{"$f":"IF(CG14=1,CN10,CG14)","v":0.60833333333333339},null,null,null,null,null,null,null,null,null,null,null,null,null,null,90,"%",null,{"$f":"CONCATENATE(DF5,DF6,DF7,DF8)","v":"6 °C Vorlauf; 100 kg/h Kühlwasser; 380 m³/h Volumenstrom; 26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(DG13=1,DK10,DC8)","v":80},{"$f":"IF(DG13=1,DL10,DG13)","v":1.3692307692307693},{"$f":"IF(DG14=1,DM10,DC8)","v":80},{"$f":"IF(DG14=1,DN10,DG14)","v":0.6},null,null,null,null,null,null,null,null,null,null,null,null,null,90,"%",null,{"$f":"CONCATENATE(EE5,EE6,EE7,EE8)","v":"6 °C Vorlauf; 200 kg/h Kühlwasser; 100 m³/h Volumenstrom; 26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(EF13=1,EJ10,EB8)","v":80},{"$f":"IF(EF13=1,EK10,EF13)","v":2.2380952380952381},{"$f":"IF(EF14=1,EL10,EB8)","v":80},{"$f":"IF(EF14=1,EM10,EF14)","v":0.90476190476190466},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,90,"%",null,{"$f":"CONCATENATE(FG5,FG6,FG7,FG8)","v":"6 °C Vorlauf; 200 kg/h Kühlwasser; 170 m³/h Volumenstrom; 26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(FH13=1,FL10,FD8)","v":80},{"$f":"IF(FH13=1,FM10,FH13)","v":2.1134020618556701},{"$f":"IF(FH14=1,FN10,FD8)","v":80},{"$f":"IF(FH14=1,FO10,FH14)","v":0.83505154639175261},null,null,null,null,null,null,null,null,null,null,null,null,null,90,"%",null,{"$f":"CONCATENATE(GF5,GF6,GF7,GF8)","v":"6 °C Vorlauf; 200 kg/h Kühlwasser; 240 m³/h Volumenstrom; 26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(GG13=1,GK10,GC8)","v":80},{"$f":"IF(GG13=1,GL10,GG13)","v":1.9760000000000002},{"$f":"IF(GG14=1,GM10,GC8)","v":80},{"$f":"IF(GG14=1,GN10,GG14)","v":0.77600000000000002},null,null,null,null,null,null,null,null,null,null,null,null,null,null,90,"%",null,{"$f":"CONCATENATE(HF5,HF6,HF7,HF8)","v":"6 °C Vorlauf; 200 kg/h Kühlwasser; 310 m³/h Volumenstrom; 26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(HG13=1,HK10,HC8)","v":80},{"$f":"IF(HG13=1,HL10,HG13)","v":1.8581081081081081},{"$f":"IF(HG14=1,HM10,HC8)","v":80},{"$f":"IF(HG14=1,HN10,HG14)","v":0.72972972972972983},null,null,null,null,null,null,null,null,null,null,null,null,null,null,90,"%",null,{"$f":"CONCATENATE(IF5,IF6,IF7,IF8)","v":"6 °C Vorlauf; 200 kg/h Kühlwasser; 380 m³/h Volumenstrom; 26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(IG13=1,IK10,IC8)","v":80},{"$f":"IF(IG13=1,IL10,IG13)","v":1.7664670658682637},{"$f":"IF(IG14=1,IM10,IC8)","v":80},{"$f":"IF(IG14=1,IN10,IG14)","v":0.69461077844311381},null,null,null,null,null,null,null,null,null,null,null,null,null,null,90,"%",null,{"$f":"CONCATENATE(JF5,JF6,JF7,JF8)","v":"6 °C Vorlauf; 300 kg/h Kühlwasser; 100 m³/h Volumenstrom; 26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(JG13=1,JK10,JC8)","v":80},{"$f":"IF(JG13=1,JL10,JG13)","v":2.3174603174603172},{"$f":"IF(JG14=1,JM10,JC8)","v":80},{"$f":"IF(JG14=1,JN10,JG14)","v":0.9365079365079364},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,90,"%",null,{"$f":"CONCATENATE(KH5,KH6,KH7,KH8)","v":"6 °C Vorlauf; 300 kg/h Kühlwasser; 170 m³/h Volumenstrom; 26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(KI13=1,KM10,KE8)","v":80},{"$f":"IF(KI13=1,KN10,KI13)","v":2.23},{"$f":"IF(KI14=1,KO10,KE8)","v":80},{"$f":"IF(KI14=1,KP10,KI14)","v":0.89},null,null,null,null,null,null,null,null,null,null,null,null,null,90,"%",null,{"$f":"CONCATENATE(LG5,LG6,LG7,LG8)","v":"6 °C Vorlauf; 300 kg/h Kühlwasser; 240 m³/h Volumenstrom; 26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(LH13=1,LL10,LD8)","v":80},{"$f":"IF(LH13=1,LM10,LH13)","v":2.1374045801526713},{"$f":"IF(LH14=1,LN10,LD8)","v":80},{"$f":"IF(LH14=1,LO10,LH14)","v":0.83969465648854968},null,null,null,null,null,null,null,null,null,null,null,null,null,null,90,"%",null,{"$f":"CONCATENATE(MG5,MG6,MG7,MG8)","v":"6 °C Vorlauf; 300 kg/h Kühlwasser; 310 m³/h Volumenstrom; 26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(MH13=1,ML10,MD8)","v":80},{"$f":"IF(MH13=1,MM10,MH13)","v":2.057324840764331},{"$f":"IF(MH14=1,MN10,MD8)","v":80},{"$f":"IF(MH14=1,MO10,MH14)","v":0.79617834394904452},null,null,null,null,null,null,null,null,null,null,null,null,null,null,90,"%",null,{"$f":"CONCATENATE(NG5,NG6,NG7,NG8)","v":"6 °C Vorlauf; 300 kg/h Kühlwasser; 380 m³/h Volumenstrom; 26 °C Ansaugtemp; "},null,null,null,null,{"$f":"IF(NH13=1,NL10,ND8)","v":80},{"$f":"IF(NH13=1,NM10,NH13)","v":1.9777777777777779},{"$f":"IF(NH14=1,NN10,ND8)","v":80},{"$f":"IF(NH14=1,NO10,NH14)","v":0.76666666666666661}]
[null,99,"%",null,null,null,null,null,null,{"$f":"IF(G13=1,J11,B9)","v":90},{"$f":"IF(G13=1,K11,G13)","v":2.2711864406779663},{"$f":"IF(G14=1,L11,B9)","v":90},{"$f":"IF(G14=1,M11,G14)","v":0.77966101694915257},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,99,"%",null,null,null,null,null,null,{"$f":"IF(AI13=1,AL11,AD9)","v":90},{"$f":"IF(AI13=1,AM11,AI13)","v":1.9310344827586206},{"$f":"IF(AI14=1,AN11,AD9)","v":90},{"$f":"IF(AI14=1,AO11,AI14)","v":0.64367816091954033},null,null,null,null,null,null,null,null,null,null,null,null,null,99,"%",null,null,null,null,null,null,{"$f":"IF(BH13=1,BK11,BC9)","v":90},{"$f":"IF(BH13=1,BL11,BH13)","v":1.7264150943396226},{"$f":"IF(BH14=1,BM11,BC9)","v":90},{"$f":"IF(BH14=1,BN11,BH14)","v":0.56603773584905659},null,null,null,null,null,null,null,null,null,null,null,null,null,null,99,"%",null,null,null,null,null,null,{"$f":"IF(CH13=1,CK11,CC9)","v":90},{"$f":"IF(CH13=1,CL11,CH13)","v":1.5833333333333333},{"$f":"IF(CH14=1,CM11,CC9)","v":90},{"$f":"IF(CH14=1,CN11,CH14)","v":0.52500000000000002},null,null,null,null,null,null,null,null,null,null,null,null,null,null,99,"%",null,null,null,null,null,null,{"$f":"IF(DH13=1,DK11,DC9)","v":90},{"$f":"IF(DH13=1,DL11,DH13)","v":1.5},{"$f":"IF(DH14=1,DM11,DC9)","v":90},{"$f":"IF(DH14=1,DN11,DH14)","v":0.50769230769230766},null,null,null,null,null,null,null,null,null,null,null,null,null,99,"%",null,null,null,null,null,null,{"$f":"IF(EG13=1,EJ11,EB9)","v":90},{"$f":"IF(EG13=1,EK11,EG13)","v":2.4920634920634921},{"$f":"IF(EG14=1,EL11,EB9)","v":90},{"$f":"IF(EG14=1,EM11,EG14)","v":0.88888888888888895},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,99,"%",null,null,null,null,null,null,{"$f":"IF(FI13=1,FL11,FD9)","v":90},{"$f":"IF(FI13=1,FM11,FI13)","v":2.3505154639175254},{"$f":"IF(FI14=1,FN11,FD9)","v":90},{"$f":"IF(FI14=1,FO11,FI14)","v":0.81443298969072175},null,null,null,null,null,null,null,null,null,null,null,null,null,99,"%",null,null,null,null,null,null,{"$f":"IF(GH13=1,GK11,GC9)","v":90},{"$f":"IF(GH13=1,GL11,GH13)","v":2.1920000000000002},{"$f":"IF(GH14=1,GM11,GC9)","v":90},{"$f":"IF(GH14=1,GN11,GH14)","v":0.73599999999999999},null,null,null,null,null,null,null,null,null,null,null,null,null,null,99,"%",null,null,null,null,null,null,{"$f":"IF(HH13=1,HK11,HC9)","v":90},{"$f":"IF(HH13=1,HL11,HH13)","v":2.0540540540540539},{"$f":"IF(HH14=1,HM11,HC9)","v":90},{"$f":"IF(HH14=1,HN11,HH14)","v":0.67567567567567566},null,null,null,null,null,null,null,null,null,null,null,null,null,null,99,"%",null,null,null,null,null,null,{"$f":"IF(IH13=1,IK11,IC9)","v":90},{"$f":"IF(IH13=1,IL11,IH13)","v":1.9461077844311379},{"$f":"IF(IH14=1,IM11,IC9)","v":90},{"$f":"IF(IH14=1,IN11,IH14)","v":0.6347305389221557},null,null,null,null,null,null,null,null,null,null,null,null,null,null,99,"%",null,null,null,null,null,null,{"$f":"IF(JH13=1,JK11,JC9)","v":90},{"$f":"IF(JH13=1,JL11,JH13)","v":2.587301587301587},{"$f":"IF(JH14=1,JM11,JC9)","v":90},{"$f":"IF(JH14=1,JN11,JH14)","v":0.9365079365079364},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,99,"%",null,null,null,null,null,null,{"$f":"IF(KJ13=1,KM11,KE9)","v":90},{"$f":"IF(KJ13=1,KN11,KJ13)","v":2.48},{"$f":"IF(KJ14=1,KO11,KE9)","v":90},{"$f":"IF(KJ14=1,KP11,KJ14)","v":0.87},null,null,null,null,null,null,null,null,null,null,null,null,null,99,"%",null,null,null,null,null,null,{"$f":"IF(LI13=1,LL11,LD9)","v":90},{"$f":"IF(LI13=1,LM11,LI13)","v":2.3740458015267172},{"$f":"IF(LI14=1,LN11,LD9)","v":90},{"$f":"IF(LI14=1,LO11,LI14)","v":0.80916030534351147},null,null,null,null,null,null,null,null,null,null,null,null,null,null,99,"%",null,null,null,null,null,null,{"$f":"IF(MI13=1,ML11,MD9)","v":90},{"$f":"IF(MI13=1,MM11,MI13)","v":2.2802547770700636},{"$f":"IF(MI14=1,MN11,MD9)","v":90},{"$f":"IF(MI14=1,MO11,MI14)","v":0.76433121019108274},null,null,null,null,null,null,null,null,null,null,null,null,null,null,99,"%",null,null,null,null,null,null,{"$f":"IF(NI13=1,NL11,ND9)","v":90},{"$f":"IF(NI13=1,NM11,NI13)","v":2.1944444444444446},{"$f":"IF(NI14=1,NN11,ND9)","v":90},{"$f":"IF(NI14=1,NO11,NI14)","v":0.72222222222222221}]
[null,{"$f":"ROUND(D11,0)","v":50},"%",{"$f":"Auslegetool!$J$9","v":50},"rel Feuchte",null,null,null,null,{"$f":"IF(H13=1,J12,B10)","v":99},{"$f":"IF(H13=1,K12,H13)","v":2.4745762711864407},{"$f":"IF(H14=1,L12,B10)","v":99},{"$f":"IF(H14=1,M12,H14)","v":0.76271186440677974},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"ROUND(AF11,0)","v":50},"%",{"$f":"$D$11","v":50},"rel Feuchte",null,null,null,null,{"$f":"IF(AJ13=1,AL12,AD10)","v":99},{"$f":"IF(AJ13=1,AM12,AJ13)","v":2.0919540229885056},{"$f":"IF(AJ14=1,AN12,AD10)","v":99},{"$f":"IF(AJ14=1,AO12,AJ14)","v":0.5977011494252874},null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"ROUND(BE11,0)","v":50},"%",{"$f":"$D$11","v":50},"rel Feuchte",null,null,null,null,{"$f":"IF(BI13=1,BK12,BC10)","v":99},{"$f":"IF(BI13=1,BL12,BI13)","v":1.8584905660377358},{"$f":"IF(BI14=1,BM12,BC10)","v":99},{"$f":"IF(BI14=1,BN12,BI14)","v":0.50943396226415094},null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"ROUND(CE11,0)","v":50},"%",{"$f":"$D$11","v":50},"rel Feuchte",null,null,null,null,{"$f":"IF(CI13=1,CK12,CC10)","v":99},{"$f":"IF(CI13=1,CL12,CI13)","v":1.7083333333333333},{"$f":"IF(CI14=1,CM12,CC10)","v":99},{"$f":"IF(CI14=1,CN12,CI14)","v":0.45000000000000007},null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"ROUND(DE11,0)","v":50},"%",{"$f":"$D$11","v":50},"rel Feuchte",null,null,null,null,{"$f":"IF(DI13=1,DK12,DC10)","v":99},{"$f":"IF(DI13=1,DL12,DI13)","v":1.6153846153846154},{"$f":"IF(DI14=1,DM12,DC10)","v":99},{"$f":"IF(DI14=1,DN12,DI14)","v":0.42307692307692307},null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"ROUND(ED11,0)","v":50},"%",{"$f":"D11","v":50},"rel Feuchte",null,null,null,null,{"$f":"IF(EH13=1,EJ12,EB10)","v":99},{"$f":"IF(EH13=1,EK12,EH13)","v":2.7142857142857144},{"$f":"IF(EH14=1,EL12,EB10)","v":99},{"$f":"IF(EH14=1,EM12,EH14)","v":0.88888888888888895},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"ROUND(FF11,0)","v":50},"%",{"$f":"$D$11","v":50},"rel Feuchte",null,null,null,null,{"$f":"IF(FJ13=1,FL12,FD10)","v":99},{"$f":"IF(FJ13=1,FM12,FJ13)","v":2.5670103092783507},{"$f":"IF(FJ14=1,FN12,FD10)","v":99},{"$f":"IF(FJ14=1,FO12,FJ14)","v":0.78350515463917525},null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"ROUND(GE11,0)","v":50},"%",{"$f":"$D$11","v":50},"rel Feuchte",null,null,null,null,{"$f":"IF(GI13=1,GK12,GC10)","v":99},{"$f":"IF(GI13=1,GL12,GI13)","v":2.3839999999999999},{"$f":"IF(GI14=1,GM12,GC10)","v":99},{"$f":"IF(GI14=1,GN12,GI14)","v":0.69599999999999995},null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"ROUND(HE11,0)","v":50},"%",{"$f":"$D$11","v":50},"rel Feuchte",null,null,null,null,{"$f":"IF(HI13=1,HK12,HC10)","v":99},{"$f":"IF(HI13=1,HL12,HI13)","v":2.2297297297297298},{"$f":"IF(HI14=1,HM12,HC10)","v":99},{"$f":"IF(HI14=1,HN12,HI14)","v":0.63513513513513509},null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"ROUND(IE11,0)","v":50},"%",{"$f":"$D$11","v":50},"rel Feuchte",null,null,null,null,{"$f":"IF(II13=1,IK12,IC10)","v":99},{"$f":"IF(II13=1,IL12,II13)","v":2.1137724550898205},{"$f":"IF(II14=1,IM12,IC10)","v":99},{"$f":"IF(II14=1,IN12,II14)","v":0.58682634730538918},null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"ROUND(JE11,0)","v":50},"%",{"$f":"D11","v":50},"rel Feuchte",null,null,null,null,{"$f":"IF(JI13=1,JK12,JC10)","v":99},{"$f":"IF(JI13=1,JL12,JI13)","v":2.8095238095238093},{"$f":"IF(JI14=1,JM12,JC10)","v":99},{"$f":"IF(JI14=1,JN12,JI14)","v":0.92063492063492058},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"ROUND(KG11,0)","v":50},"%",{"$f":"$D$11","v":50},"rel Feuchte",null,null,null,null,{"$f":"IF(KK13=1,KM12,KE10)","v":99},{"$f":"IF(KK13=1,KN12,KK13)","v":2.7},{"$f":"IF(KK14=1,KO12,KE10)","v":99},{"$f":"IF(KK14=1,KP12,KK14)","v":0.85},null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"ROUND(LF11,0)","v":50},"%",{"$f":"$D$11","v":50},"rel Feuchte",null,null,null,null,{"$f":"IF(LJ13=1,LL12,LD10)","v":99},{"$f":"IF(LJ13=1,LM12,LJ13)","v":2.5877862595419847},{"$f":"IF(LJ14=1,LN12,LD10)","v":99},{"$f":"IF(LJ14=1,LO12,LJ14)","v":0.7862595419847328},null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"ROUND(MF11,0)","v":50},"%",{"$f":"$D$11","v":50},"rel Feuchte",null,null,null,null,{"$f":"IF(MJ13=1,ML12,MD10)","v":99},{"$f":"IF(MJ13=1,MM12,MJ13)","v":2.484076433121019},{"$f":"IF(MJ14=1,MN12,MD10)","v":99},{"$f":"IF(MJ14=1,MO12,MJ14)","v":0.73248407643312097},null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"ROUND(NF11,0)","v":50},"%",{"$f":"$D$11","v":50},"rel Feuchte",null,null,null,null,{"$f":"IF(NJ13=1,NL12,ND10)","v":99},{"$f":"IF(NJ13=1,NM12,NJ13)","v":2.3833333333333333},{"$f":"IF(NJ14=1,NN12,ND10)","v":99},{"$f":"IF(NJ14=1,NO12,NJ14)","v":0.68333333333333335}]
["Ansaugtemp",{"$f":"ROUND(D12,0)","v":26},"°C",{"$f":"Auslegetool!$J$6","v":26},"Ansaugtemperatur",null,null,null,null,null,null,100,1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Ansaugtemp",{"$f":"ROUND(AF12,0)","v":26},"°C",{"$f":"$D$12","v":26},"Ansaugtemperatur",null,null,null,null,null,null,100,1,null,null,null,null,null,null,null,null,null,null,null,null,"Ansaugtemp",{"$f":"ROUND(BE12,0)","v":26},"°C",{"$f":"$D$12","v":26},"Ansaugtemperatur",null,null,null,null,null,null,100,1,null,null,null,null,null,null,null,null,null,null,null,null,null,"Ansaugtemp",{"$f":"ROUND(CE12,0)","v":26},"°C",{"$f":"$D$12","v":26},"Ansaugtemperatur",null,null,null,null,null,null,100,1,null,null,null,null,null,null,null,null,null,null,null,null,null,"Ansaugtemp",{"$f":"ROUND(DE12,0)","v":26},"°C",{"$f":"$D$12","v":26},"Ansaugtemperatur",null,null,null,null,null,null,100,1,null,null,null,null,null,null,null,null,null,null,null,null,"Ansaugtemp",{"$f":"ROUND(ED12,0)","v":26},"°C",{"$f":"D12","v":26},"Ansaugtemperatur",null,null,null,null,null,null,100,1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Ansaugtemp",{"$f":"ROUND(FF12,0)","v":26},"°C",{"$f":"$D$12","v":26},"Ansaugtemperatur",null,null,null,null,null,null,100,1,null,null,null,null,null,null,null,null,null,null,null,null,"Ansaugtemp",{"$f":"ROUND(GE12,0)","v":26},"°C",{"$f":"$D$12","v":26},"Ansaugtemperatur",null,null,null,null,null,null,100,1,null,null,null,null,null,null,null,null,null,null,null,null,null,"Ansaugtemp",{"$f":"ROUND(HE12,0)","v":26},"°C",{"$f":"$D$12","v":26},"Ansaugtemperatur",null,null,null,null,null,null,100,1,null,null,null,null,null,null,null,null,null,null,null,null,null,"Ansaugtemp",{"$f":"ROUND(IE12,0)","v":26},"°C",{"$f":"$D$12","v":26},"Ansaugtemperatur",null,null,null,null,null,null,100,1,null,null,null,null,null,null,null,null,null,null,null,null,null,"Ansaugtemp",{"$f":"ROUND(JE12,0)","v":26},"°C",{"$f":"D12","v":26},"Ansaugtemperatur",null,null,null,null,null,null,100,1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Ansaugtemp",{"$f":"ROUND(KG12,0)","v":26},"°C",{"$f":"$D$12","v":26},"Ansaugtemperatur",null,null,null,null,null,null,100,1,null,null,null,null,null,null,null,null,null,null,null,null,"Ansaugtemp",{"$f":"ROUND(LF12,0)","v":26},"°C",{"$f":"$D$12","v":26},"Ansaugtemperatur",null,null,null,null,null,null,100,1,null,null,null,null,null,null,null,null,null,null,null,null,null,"Ansaugtemp",{"$f":"ROUND(MF12,0)","v":26},"°C",{"$f":"$D$12","v":26},"Ansaugtemperatur",null,null,null,null,null,null,100,1,null,null,null,null,null,null,null,null,null,null,null,null,null,"Ansaugtemp",{"$f":"ROUND(NF12,0)","v":26},"°C",{"$f":"$D$12","v":26},"Ansaugtemperatur",null,null,null,null,null,null,100,1]
["Korrekturfaktor\n totale Leistung",{"$f":"INDEX($K$22:$K$12516,MATCH(B1&B2&B3&B4&B12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(B1&B2&B3&B4&B12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(B1&B2&B3&B6&B12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.5932203389830508},{"$f":"INDEX($K$22:$K$12516,MATCH(B1&B2&B3&B7&B12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.8135593220338986},{"$f":"INDEX($K$22:$K$12516,MATCH(B1&B2&B3&B8&B12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.0508474576271185},{"$f":"INDEX($K$22:$K$12516,MATCH(B1&B2&B3&B9&B12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.2711864406779663},{"$f":"INDEX($K$22:$K$12516,MATCH(B1&B2&B3&B10&B12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.4745762711864407},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"INDEX($K$22:$K$12516,MATCH(AD1&AD2&AD3&AD4&AD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(AD1&AD2&AD3&AD4&AD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(AD1&AD2&AD3&AD6&AD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.367816091954023},{"$f":"INDEX($K$22:$K$12516,MATCH(AD1&AD2&AD3&AD7&AD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.5517241379310347},{"$f":"INDEX($K$22:$K$12516,MATCH(AD1&AD2&AD3&AD8&AD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.7471264367816093},{"$f":"INDEX($K$22:$K$12516,MATCH(AD1&AD2&AD3&AD9&AD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.9310344827586206},{"$f":"INDEX($K$22:$K$12516,MATCH(AD1&AD2&AD3&AD10&AD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.0919540229885056},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"INDEX($K$22:$K$12516,MATCH(BC1&BC2&BC3&BC4&BC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(BC1&BC2&BC3&BC4&BC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(BC1&BC2&BC3&BC6&BC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.2358490566037736},{"$f":"INDEX($K$22:$K$12516,MATCH(BC1&BC2&BC3&BC7&BC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.4056603773584906},{"$f":"INDEX($K$22:$K$12516,MATCH(BC1&BC2&BC3&BC8&BC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.5660377358490565},{"$f":"INDEX($K$22:$K$12516,MATCH(BC1&BC2&BC3&BC9&BC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.7264150943396226},{"$f":"INDEX($K$22:$K$12516,MATCH(BC1&BC2&BC3&BC10&BC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.8584905660377358},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"INDEX($K$22:$K$12516,MATCH(CC1&CC2&CC3&CC4&CC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(CC1&CC2&CC3&CC4&CC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(CC1&CC2&CC3&CC6&CC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.1499999999999999},{"$f":"INDEX($K$22:$K$12516,MATCH(CC1&CC2&CC3&CC7&CC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.3},{"$f":"INDEX($K$22:$K$12516,MATCH(CC1&CC2&CC3&CC8&CC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.45},{"$f":"INDEX($K$22:$K$12516,MATCH(CC1&CC2&CC3&CC9&CC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.5833333333333333},{"$f":"INDEX($K$22:$K$12516,MATCH(CC1&CC2&CC3&CC10&CC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.7083333333333333},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"INDEX($K$22:$K$12516,MATCH(DC1&DC2&DC3&DC4&DC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(DC1&DC2&DC3&DC4&DC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(DC1&DC2&DC3&DC6&DC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.0923076923076922},{"$f":"INDEX($K$22:$K$12516,MATCH(DC1&DC2&DC3&DC7&DC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.2384615384615385},{"$f":"INDEX($K$22:$K$12516,MATCH(DC1&DC2&DC3&DC8&DC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.3692307692307693},{"$f":"INDEX($K$22:$K$12516,MATCH(DC1&DC2&DC3&DC9&DC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.5},{"$f":"INDEX($K$22:$K$12516,MATCH(DC1&DC2&DC3&DC10&DC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.6153846153846154},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"INDEX($K$22:$K$12516,MATCH(EB1&EB2&EB3&EB4&EB12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(EB1&EB2&EB3&EB4&EB12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(EB1&EB2&EB3&EB6&EB12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.7460317460317463},{"$f":"INDEX($K$22:$K$12516,MATCH(EB1&EB2&EB3&EB7&EB12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2},{"$f":"INDEX($K$22:$K$12516,MATCH(EB1&EB2&EB3&EB8&EB12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.2380952380952381},{"$f":"INDEX($K$22:$K$12516,MATCH(EB1&EB2&EB3&EB9&EB12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.4920634920634921},{"$f":"INDEX($K$22:$K$12516,MATCH(EB1&EB2&EB3&EB10&EB12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.7142857142857144},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"INDEX($K$22:$K$12516,MATCH(FD1&FD2&FD3&FD4&FD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(FD1&FD2&FD3&FD4&FD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(FD1&FD2&FD3&FD6&FD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.6494845360824744},{"$f":"INDEX($K$22:$K$12516,MATCH(FD1&FD2&FD3&FD7&FD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.8865979381443301},{"$f":"INDEX($K$22:$K$12516,MATCH(FD1&FD2&FD3&FD8&FD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.1134020618556701},{"$f":"INDEX($K$22:$K$12516,MATCH(FD1&FD2&FD3&FD9&FD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.3505154639175254},{"$f":"INDEX($K$22:$K$12516,MATCH(FD1&FD2&FD3&FD10&FD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.5670103092783507},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"INDEX($K$22:$K$12516,MATCH(GC1&GC2&GC3&GC4&GC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(GC1&GC2&GC3&GC4&GC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(GC1&GC2&GC3&GC6&GC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.544},{"$f":"INDEX($K$22:$K$12516,MATCH(GC1&GC2&GC3&GC7&GC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.7600000000000002},{"$f":"INDEX($K$22:$K$12516,MATCH(GC1&GC2&GC3&GC8&GC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.9760000000000002},{"$f":"INDEX($K$22:$K$12516,MATCH(GC1&GC2&GC3&GC9&GC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.1920000000000002},{"$f":"INDEX($K$22:$K$12516,MATCH(GC1&GC2&GC3&GC10&GC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.3839999999999999},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"INDEX($K$22:$K$12516,MATCH(HC1&HC2&HC3&HC4&HC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(HC1&HC2&HC3&HC4&HC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(HC1&HC2&HC3&HC6&HC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.4594594594594597},{"$f":"INDEX($K$22:$K$12516,MATCH(HC1&HC2&HC3&HC7&HC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.6554054054054055},{"$f":"INDEX($K$22:$K$12516,MATCH(HC1&HC2&HC3&HC8&HC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.8581081081081081},{"$f":"INDEX($K$22:$K$12516,MATCH(HC1&HC2&HC3&HC9&HC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.0540540540540539},{"$f":"INDEX($K$22:$K$12516,MATCH(HC1&HC2&HC3&HC10&HC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.2297297297297298},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"INDEX($K$22:$K$12516,MATCH(IC1&IC2&IC3&IC4&IC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(IC1&IC2&IC3&IC4&IC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(IC1&IC2&IC3&IC6&IC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.3892215568862276},{"$f":"INDEX($K$22:$K$12516,MATCH(IC1&IC2&IC3&IC7&IC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.5808383233532937},{"$f":"INDEX($K$22:$K$12516,MATCH(IC1&IC2&IC3&IC8&IC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.7664670658682637},{"$f":"INDEX($K$22:$K$12516,MATCH(IC1&IC2&IC3&IC9&IC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.9461077844311379},{"$f":"INDEX($K$22:$K$12516,MATCH(IC1&IC2&IC3&IC10&IC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.1137724550898205},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"INDEX($K$22:$K$12516,MATCH(JC1&JC2&JC3&JC4&JC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(JC1&JC2&JC3&JC4&JC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(JC1&JC2&JC3&JC6&JC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.8095238095238093},{"$f":"INDEX($K$22:$K$12516,MATCH(JC1&JC2&JC3&JC7&JC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.0634920634920637},{"$f":"INDEX($K$22:$K$12516,MATCH(JC1&JC2&JC3&JC8&JC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.3174603174603172},{"$f":"INDEX($K$22:$K$12516,MATCH(JC1&JC2&JC3&JC9&JC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.587301587301587},{"$f":"INDEX($K$22:$K$12516,MATCH(JC1&JC2&JC3&JC10&JC12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.8095238095238093},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"INDEX($K$22:$K$12516,MATCH(KE1&KE2&KE3&KE4&KE12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(KE1&KE2&KE3&KE4&KE12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(KE1&KE2&KE3&KE6&KE12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.73},{"$f":"INDEX($K$22:$K$12516,MATCH(KE1&KE2&KE3&KE7&KE12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.98},{"$f":"INDEX($K$22:$K$12516,MATCH(KE1&KE2&KE3&KE8&KE12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.23},{"$f":"INDEX($K$22:$K$12516,MATCH(KE1&KE2&KE3&KE9&KE12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.48},{"$f":"INDEX($K$22:$K$12516,MATCH(KE1&KE2&KE3&KE10&KE12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.7},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"INDEX($K$22:$K$12516,MATCH(LD1&LD2&LD3&LD4&LD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(LD1&LD2&LD3&LD4&LD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(LD1&LD2&LD3&LD6&LD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.6641221374045803},{"$f":"INDEX($K$22:$K$12516,MATCH(LD1&LD2&LD3&LD7&LD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.9007633587786261},{"$f":"INDEX($K$22:$K$12516,MATCH(LD1&LD2&LD3&LD8&LD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.1374045801526713},{"$f":"INDEX($K$22:$K$12516,MATCH(LD1&LD2&LD3&LD9&LD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.3740458015267172},{"$f":"INDEX($K$22:$K$12516,MATCH(LD1&LD2&LD3&LD10&LD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.5877862595419847},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"INDEX($K$22:$K$12516,MATCH(MD1&MD2&MD3&MD4&MD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(MD1&MD2&MD3&MD4&MD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(MD1&MD2&MD3&MD6&MD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.5987261146496814},{"$f":"INDEX($K$22:$K$12516,MATCH(MD1&MD2&MD3&MD7&MD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.8280254777070064},{"$f":"INDEX($K$22:$K$12516,MATCH(MD1&MD2&MD3&MD8&MD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.057324840764331},{"$f":"INDEX($K$22:$K$12516,MATCH(MD1&MD2&MD3&MD9&MD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.2802547770700636},{"$f":"INDEX($K$22:$K$12516,MATCH(MD1&MD2&MD3&MD10&MD12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.484076433121019},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"INDEX($K$22:$K$12516,MATCH(ND1&ND2&ND3&ND4&ND12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(ND1&ND2&ND3&ND4&ND12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1},{"$f":"INDEX($K$22:$K$12516,MATCH(ND1&ND2&ND3&ND6&ND12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.5444444444444443},{"$f":"INDEX($K$22:$K$12516,MATCH(ND1&ND2&ND3&ND7&ND12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.7611111111111111},{"$f":"INDEX($K$22:$K$12516,MATCH(ND1&ND2&ND3&ND8&ND12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":1.9777777777777779},{"$f":"INDEX($K$22:$K$12516,MATCH(ND1&ND2&ND3&ND9&ND12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.1944444444444446},{"$f":"INDEX($K$22:$K$12516,MATCH(ND1&ND2&ND3&ND10&ND12,$A$22:$A$12516&$H$22:$H$12516&$C$22:$C$12516&$E$22:$E$12516&$D$22:$D$12516,0))","v":2.3833333333333333}]
["Korrekturfaktor\nsensible Leistung",{"$f":"INDEX($L$19:$L$12516,MATCH(B1&B2&B3&B4&B12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":1},{"$f":"INDEX($L$19:$L$12516,MATCH(B1&B2&B3&B5&B12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.89830508474576276},{"$f":"INDEX($L$19:$L$12516,MATCH(B1&B2&B3&B6&B12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.88135593220338992},{"$f":"INDEX($L$19:$L$12516,MATCH(B1&B2&B3&B7&B12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.84745762711864414},{"$f":"INDEX($L$19:$L$12516,MATCH(B1&B2&B3&B8&B12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.81355932203389836},{"$f":"INDEX($L$19:$L$12516,MATCH(B1&B2&B3&B9&B12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.77966101694915257},{"$f":"INDEX($L$19:$L$12516,MATCH(B1&B2&B3&B10&B12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.76271186440677974},null,"Polynom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"INDEX($L$19:$L$12516,MATCH(AD1&AD2&AD3&AD4&AD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":1},{"$f":"INDEX($L$19:$L$12516,MATCH(AD1&AD2&AD3&AD5&AD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.86206896551724144},{"$f":"INDEX($L$19:$L$12516,MATCH(AD1&AD2&AD3&AD6&AD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.80459770114942519},{"$f":"INDEX($L$19:$L$12516,MATCH(AD1&AD2&AD3&AD7&AD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.74712643678160917},{"$f":"INDEX($L$19:$L$12516,MATCH(AD1&AD2&AD3&AD8&AD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.68965517241379304},{"$f":"INDEX($L$19:$L$12516,MATCH(AD1&AD2&AD3&AD9&AD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.64367816091954033},{"$f":"INDEX($L$19:$L$12516,MATCH(AD1&AD2&AD3&AD10&AD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.5977011494252874},null,"Polynom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"INDEX($L$19:$L$12516,MATCH(BC1&BC2&BC3&BC4&BC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":1},{"$f":"INDEX($L$19:$L$12516,MATCH(BC1&BC2&BC3&BC5&BC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.85849056603773588},{"$f":"INDEX($L$19:$L$12516,MATCH(BC1&BC2&BC3&BC6&BC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.78301886792452824},{"$f":"INDEX($L$19:$L$12516,MATCH(BC1&BC2&BC3&BC7&BC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.70754716981132071},{"$f":"INDEX($L$19:$L$12516,MATCH(BC1&BC2&BC3&BC8&BC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.64150943396226412},{"$f":"INDEX($L$19:$L$12516,MATCH(BC1&BC2&BC3&BC9&BC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.56603773584905659},{"$f":"INDEX($L$19:$L$12516,MATCH(BC1&BC2&BC3&BC10&BC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.50943396226415094},null,"Polynom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"INDEX($L$19:$L$12516,MATCH(CC1&CC2&CC3&CC4&CC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":1},{"$f":"INDEX($L$19:$L$12516,MATCH(CC1&CC2&CC3&CC5&CC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.87500000000000011},{"$f":"INDEX($L$19:$L$12516,MATCH(CC1&CC2&CC3&CC6&CC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.78333333333333333},{"$f":"INDEX($L$19:$L$12516,MATCH(CC1&CC2&CC3&CC7&CC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.69166666666666665},{"$f":"INDEX($L$19:$L$12516,MATCH(CC1&CC2&CC3&CC8&CC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.60833333333333339},{"$f":"INDEX($L$19:$L$12516,MATCH(CC1&CC2&CC3&CC9&CC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.52500000000000002},{"$f":"INDEX($L$19:$L$12516,MATCH(CC1&CC2&CC3&CC10&CC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.45000000000000007},null,"Polynom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"INDEX($L$19:$L$12516,MATCH(DC1&DC2&DC3&DC4&DC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":1},{"$f":"INDEX($L$19:$L$12516,MATCH(DC1&DC2&DC3&DC5&DC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.89999999999999991},{"$f":"INDEX($L$19:$L$12516,MATCH(DC1&DC2&DC3&DC6&DC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.8},{"$f":"INDEX($L$19:$L$12516,MATCH(DC1&DC2&DC3&DC7&DC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.7},{"$f":"INDEX($L$19:$L$12516,MATCH(DC1&DC2&DC3&DC8&DC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.6},{"$f":"INDEX($L$19:$L$12516,MATCH(DC1&DC2&DC3&DC9&DC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.50769230769230766},{"$f":"INDEX($L$19:$L$12516,MATCH(DC1&DC2&DC3&DC10&DC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.42307692307692307},null,"Polynom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"INDEX($L$19:$L$12516,MATCH(EB1&EB2&EB3&EB4&EB12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":1},{"$f":"INDEX($L$19:$L$12516,MATCH(EB1&EB2&EB3&EB5&EB12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.95238095238095233},{"$f":"INDEX($L$19:$L$12516,MATCH(EB1&EB2&EB3&EB6&EB12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.9365079365079364},{"$f":"INDEX($L$19:$L$12516,MATCH(EB1&EB2&EB3&EB7&EB12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.92063492063492058},{"$f":"INDEX($L$19:$L$12516,MATCH(EB1&EB2&EB3&EB8&EB12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.90476190476190466},{"$f":"INDEX($L$19:$L$12516,MATCH(EB1&EB2&EB3&EB9&EB12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.88888888888888895},{"$f":"INDEX($L$19:$L$12516,MATCH(EB1&EB2&EB3&EB10&EB12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.88888888888888895},null,"Polynom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"INDEX($L$19:$L$12516,MATCH(FD1&FD2&FD3&FD4&FD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":1},{"$f":"INDEX($L$19:$L$12516,MATCH(FD1&FD2&FD3&FD5&FD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.91752577319587636},{"$f":"INDEX($L$19:$L$12516,MATCH(FD1&FD2&FD3&FD6&FD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.89690721649484539},{"$f":"INDEX($L$19:$L$12516,MATCH(FD1&FD2&FD3&FD7&FD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.865979381443299},{"$f":"INDEX($L$19:$L$12516,MATCH(FD1&FD2&FD3&FD8&FD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.83505154639175261},{"$f":"INDEX($L$19:$L$12516,MATCH(FD1&FD2&FD3&FD9&FD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.81443298969072175},{"$f":"INDEX($L$19:$L$12516,MATCH(FD1&FD2&FD3&FD10&FD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.78350515463917525},null,"Polynom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"INDEX($L$19:$L$12516,MATCH(GC1&GC2&GC3&GC4&GC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":1},{"$f":"INDEX($L$19:$L$12516,MATCH(GC1&GC2&GC3&GC5&GC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.89600000000000013},{"$f":"INDEX($L$19:$L$12516,MATCH(GC1&GC2&GC3&GC6&GC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.85600000000000009},{"$f":"INDEX($L$19:$L$12516,MATCH(GC1&GC2&GC3&GC7&GC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.81600000000000006},{"$f":"INDEX($L$19:$L$12516,MATCH(GC1&GC2&GC3&GC8&GC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.77600000000000002},{"$f":"INDEX($L$19:$L$12516,MATCH(GC1&GC2&GC3&GC9&GC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.73599999999999999},{"$f":"INDEX($L$19:$L$12516,MATCH(GC1&GC2&GC3&GC10&GC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.69599999999999995},null,"Polynom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"INDEX($L$19:$L$12516,MATCH(HC1&HC2&HC3&HC4&HC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":1},{"$f":"INDEX($L$19:$L$12516,MATCH(HC1&HC2&HC3&HC5&HC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.8783783783783784},{"$f":"INDEX($L$19:$L$12516,MATCH(HC1&HC2&HC3&HC6&HC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.82432432432432434},{"$f":"INDEX($L$19:$L$12516,MATCH(HC1&HC2&HC3&HC7&HC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.77702702702702697},{"$f":"INDEX($L$19:$L$12516,MATCH(HC1&HC2&HC3&HC8&HC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.72972972972972983},{"$f":"INDEX($L$19:$L$12516,MATCH(HC1&HC2&HC3&HC9&HC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.67567567567567566},{"$f":"INDEX($L$19:$L$12516,MATCH(HC1&HC2&HC3&HC10&HC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.63513513513513509},null,"Polynom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"INDEX($L$19:$L$12516,MATCH(IC1&IC2&IC3&IC4&IC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":1},{"$f":"INDEX($L$19:$L$12516,MATCH(IC1&IC2&IC3&IC5&IC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.86826347305389218},{"$f":"INDEX($L$19:$L$12516,MATCH(IC1&IC2&IC3&IC6&IC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.80838323353293418},{"$f":"INDEX($L$19:$L$12516,MATCH(IC1&IC2&IC3&IC7&IC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.75449101796407192},{"$f":"INDEX($L$19:$L$12516,MATCH(IC1&IC2&IC3&IC8&IC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.69461077844311381},{"$f":"INDEX($L$19:$L$12516,MATCH(IC1&IC2&IC3&IC9&IC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.6347305389221557},{"$f":"INDEX($L$19:$L$12516,MATCH(IC1&IC2&IC3&IC10&IC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.58682634730538918},null,"Polynom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"INDEX($L$19:$L$12516,MATCH(JC1&JC2&JC3&JC4&JC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":1},{"$f":"INDEX($L$19:$L$12516,MATCH(JC1&JC2&JC3&JC5&JC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.96825396825396826},{"$f":"INDEX($L$19:$L$12516,MATCH(JC1&JC2&JC3&JC6&JC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.96825396825396826},{"$f":"INDEX($L$19:$L$12516,MATCH(JC1&JC2&JC3&JC7&JC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.95238095238095233},{"$f":"INDEX($L$19:$L$12516,MATCH(JC1&JC2&JC3&JC8&JC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.9365079365079364},{"$f":"INDEX($L$19:$L$12516,MATCH(JC1&JC2&JC3&JC9&JC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.9365079365079364},{"$f":"INDEX($L$19:$L$12516,MATCH(JC1&JC2&JC3&JC10&JC12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.92063492063492058},null,"Polynom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"INDEX($L$19:$L$12516,MATCH(KE1&KE2&KE3&KE4&KE12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":1},{"$f":"INDEX($L$19:$L$12516,MATCH(KE1&KE2&KE3&KE5&KE12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.94},{"$f":"INDEX($L$19:$L$12516,MATCH(KE1&KE2&KE3&KE6&KE12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.93},{"$f":"INDEX($L$19:$L$12516,MATCH(KE1&KE2&KE3&KE7&KE12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.91},{"$f":"INDEX($L$19:$L$12516,MATCH(KE1&KE2&KE3&KE8&KE12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.89},{"$f":"INDEX($L$19:$L$12516,MATCH(KE1&KE2&KE3&KE9&KE12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.87},{"$f":"INDEX($L$19:$L$12516,MATCH(KE1&KE2&KE3&KE10&KE12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.85},null,"Polynom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"INDEX($L$19:$L$12516,MATCH(LD1&LD2&LD3&LD4&LD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":1},{"$f":"INDEX($L$19:$L$12516,MATCH(LD1&LD2&LD3&LD5&LD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.92366412213740456},{"$f":"INDEX($L$19:$L$12516,MATCH(LD1&LD2&LD3&LD6&LD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.89312977099236635},{"$f":"INDEX($L$19:$L$12516,MATCH(LD1&LD2&LD3&LD7&LD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.86259541984732813},{"$f":"INDEX($L$19:$L$12516,MATCH(LD1&LD2&LD3&LD8&LD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.83969465648854968},{"$f":"INDEX($L$19:$L$12516,MATCH(LD1&LD2&LD3&LD9&LD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.80916030534351147},{"$f":"INDEX($L$19:$L$12516,MATCH(LD1&LD2&LD3&LD10&LD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.7862595419847328},null,"Polynom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"INDEX($L$19:$L$12516,MATCH(MD1&MD2&MD3&MD4&MD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":1},{"$f":"INDEX($L$19:$L$12516,MATCH(MD1&MD2&MD3&MD5&MD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.90445859872611456},{"$f":"INDEX($L$19:$L$12516,MATCH(MD1&MD2&MD3&MD6&MD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.87261146496815289},{"$f":"INDEX($L$19:$L$12516,MATCH(MD1&MD2&MD3&MD7&MD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.83439490445859876},{"$f":"INDEX($L$19:$L$12516,MATCH(MD1&MD2&MD3&MD8&MD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.79617834394904452},{"$f":"INDEX($L$19:$L$12516,MATCH(MD1&MD2&MD3&MD9&MD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.76433121019108274},{"$f":"INDEX($L$19:$L$12516,MATCH(MD1&MD2&MD3&MD10&MD12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.73248407643312097},null,"Polynom",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"INDEX($L$19:$L$12516,MATCH(ND1&ND2&ND3&ND4&ND12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":1},{"$f":"INDEX($L$19:$L$12516,MATCH(ND1&ND2&ND3&ND5&ND12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.89444444444444449},{"$f":"INDEX($L$19:$L$12516,MATCH(ND1&ND2&ND3&ND6&ND12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.85},{"$f":"INDEX($L$19:$L$12516,MATCH(ND1&ND2&ND3&ND7&ND12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.80555555555555547},{"$f":"INDEX($L$19:$L$12516,MATCH(ND1&ND2&ND3&ND8&ND12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.76666666666666661},{"$f":"INDEX($L$19:$L$12516,MATCH(ND1&ND2&ND3&ND9&ND12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.72222222222222221},{"$f":"INDEX($L$19:$L$12516,MATCH(ND1&ND2&ND3&ND10&ND12,$A$19:$A$12516&$H$19:$H$12516&$C$19:$C$12516&$E$19:$E$12516&$D$19:$D$12516,0))","v":0.68333333333333335},null,"Polynom"]
[null,null,null,null,null,null,null,null,"x=rel.Feuchte y=Korrektur Total",{"$f":"LINEST(K6:K11,J6:J11^{0,1},0,0)","v":2.2642751357577751E-2},0.23393121606055631,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"x=rel.Feuchte y=Korrektur Total",{"$f":"LINEST(AM6:AM11,AL6:AL11^{0,1},0,0)","v":1.8663095636647697E-2},0.24851839452442021,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"x=rel.Feuchte y=Korrektur Total",{"$f":"LINEST(BL6:BL11,BK6:BK11^{0,1},0,0)","v":1.6065213409049272E-2},0.27572815533980655,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"x=rel.Feuchte y=Korrektur Total",{"$f":"LINEST(CL6:CL11,CK6:CK11^{0,1},0,0)","v":1.4359223300970874E-2},0.29179719525350584,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"x=rel.Feuchte y=Korrektur Total",{"$f":"LINEST(DL6:DL11,DK6:DK11^{0,1},0,0)","v":1.3430918595967147E-2},0.29048344535723131,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"x=rel.Feuchte y=Korrektur Total",{"$f":"LINEST(EK6:EK11,EJ6:EJ11^{0,1},0,0)","v":2.4798890429958389E-2},0.25896953819283991,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"x=rel.Feuchte y=Korrektur Total",{"$f":"LINEST(FM6:FM11,FL6:FL11^{0,1},0,0)","v":2.3449104193774398E-2},0.24222600340306244,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"x=rel.Feuchte y=Korrektur Total",{"$f":"LINEST(GL6:GL11,GK6:GK11^{0,1},0,0)","v":2.1558058252427178E-2},0.2508085436893211,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"x=rel.Feuchte y=Korrektur Total",{"$f":"LINEST(HL6:HL11,HK6:HK11^{0,1},0,0)","v":1.9790081343479395E-2},0.2720948132598624,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"x=rel.Feuchte y=Korrektur Total",{"$f":"LINEST(IL6:IL11,IK6:IK11^{0,1},0,0)","v":1.8559386082204515E-2},0.27781175513051637,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"x=rel.Feuchte y=Korrektur Total",{"$f":"LINEST(JL6:JL11,JK6:JK11^{0,1},0,0)","v":2.5729696409308053E-2},0.2644824574921667,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"x=rel.Feuchte y=Korrektur Total",{"$f":"LINEST(KN6:KN11,KM6:KM11^{0,1},0,0)","v":2.4912621359223303E-2},0.23585113268608363,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"x=rel.Feuchte y=Korrektur Total",{"$f":"LINEST(LM6:LM11,LL6:LL11^{0,1},0,0)","v":2.3677462387904837E-2},0.24338150646013998,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"x=rel.Feuchte y=Korrektur Total",{"$f":"LINEST(MM6:MM11,ML6:ML11^{0,1},0,0)","v":2.2707315564900136E-2},0.23741265227877018,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"x=rel.Feuchte y=Korrektur Total",{"$f":"LINEST(NM6:NM11,NL6:NL11^{0,1},0,0)","v":2.1559870550161821E-2},0.2515958288385472]
[null,null,null,null,null,null,null,null,"exponent",2,1,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"exponent",2,1,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"exponent",2,1,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,0,0]
["Korrekturfaktor\n totale Leistung",{"$f":"IF(ISNA(B13),1,IF(J15*B11+K15<1,1,J15*B11+K15))","v":1.3660687839394439},{"$f":"IF(B17<1,1,B17)","v":1.3660687839394439},null,null,null,null,null,"x=rel.Feuchte y=Korrektur Sensibel",{"$f":"LINEST(M5:M11,L5:L11^{0,1,2},0,0)","v":2.4485421464862393E-5},-6.7674830450028221E-3,1.1940352638002047,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"IF(ISNA(AD13),1,IF(AL15*AD11+AM15<1,1,AL15*AD11+AM15))","v":1.1816731763568051},{"$f":"IF(AD17<1,1,AD17)","v":1.1816731763568051},null,null,null,null,null,"x=rel.Feuchte y=Korrektur Sensibel",{"$f":"LINEST(AO5:AO11,AN5:AN11^{0,1,2},0,0)","v":6.1914812155148381E-5},-1.5001569937970754E-2,1.4855137645155103,0,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"IF(ISNA(BC13),1,IF(BK15*BC11+BL15<1,1,BK15*BC11+BL15))","v":1.0789888257922702},{"$f":"IF(BC17<1,1,BC17)","v":1.0789888257922702},null,null,null,null,null,"x=rel.Feuchte y=Korrektur Sensibel",{"$f":"LINEST(BN5:BN11,BM5:BM11^{0,1,2},0,0)","v":7.6909694235813088E-5},-1.928235866418361E-2,1.6745733662678424,0,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"IF(ISNA(CC13),1,IF(CK15*CC11+CL15<1,1,CK15*CC11+CL15))","v":1.0097583603020495},{"$f":"IF(CC17<1,1,CC17)","v":1.0097583603020495},null,null,null,null,null,"x=rel.Feuchte y=Korrektur Sensibel",{"$f":"LINEST(CN5:CN11,CM5:CM11^{0,1,2},0,0)","v":7.8093100567095666E-5},-2.122650150232842E-2,1.7949156932071604,0,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"IF(ISNA(DC13),1,IF(DK15*DC11+DL15<1,1,DK15*DC11+DL15))","v":1},{"$f":"IF(DC17<1,1,DC17)","v":1},null,null,null,null,null,"x=rel.Feuchte y=Korrektur Sensibel",{"$f":"LINEST(DN5:DN11,DM5:DM11^{0,1,2},0,0)","v":5.6518708925250246E-5},-1.9241619579582227E-2,1.7762891586899496,0,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"IF(ISNA(EB13),1,IF(EJ15*EB11+EK15<1,1,EJ15*EB11+EK15))","v":1.4989140596907593},{"$f":"IF(EB17<1,1,EB17)","v":1.4989140596907593},null,null,null,null,null,"x=rel.Feuchte y=Korrektur Sensibel",{"$f":"LINEST(EM5:EM11,EL5:EL11^{0,1,2},0,0)","v":1.3113502851237918E-5},-3.3394788665494493E-3,1.0880939069437265,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"IF(ISNA(FD13),1,IF(FL15*FD11+FM15<1,1,FL15*FD11+FM15))","v":1.4146812130917823},{"$f":"IF(FD17<1,1,FD17)","v":1.4146812130917823},null,null,null,null,null,"x=rel.Feuchte y=Korrektur Sensibel",{"$f":"LINEST(FO5:FO11,FN5:FN11^{0,1,2},0,0)","v":1.431238109405595E-5},-4.9880867642595229E-3,1.1420100796868156,0,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"IF(ISNA(GC13),1,IF(GK15*GC11+GL15<1,1,GK15*GC11+GL15))","v":1.3287114563106799},{"$f":"IF(GC17<1,1,GC17)","v":1.3287114563106799},null,null,null,null,null,"x=rel.Feuchte y=Korrektur Sensibel",{"$f":"LINEST(GN5:GN11,GM5:GM11^{0,1,2},0,0)","v":2.1222080227398558E-5},-7.3752157391501968E-3,1.2241410581823864,0,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"IF(ISNA(HC13),1,IF(HK15*HC11+HL15<1,1,HK15*HC11+HL15))","v":1.2615988804338323},{"$f":"IF(HC17<1,1,HC17)","v":1.2615988804338323},null,null,null,null,null,"x=rel.Feuchte y=Korrektur Sensibel",{"$f":"LINEST(HN5:HN11,HM5:HM11^{0,1,2},0,0)","v":3.424017728815603E-5},-1.0270927501843575E-2,1.3220956146960994,0,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"IF(ISNA(IC13),1,IF(IK15*IC11+IL15<1,1,IK15*IC11+IL15))","v":1.2057810592407421},{"$f":"IF(IC17<1,1,IC17)","v":1.2057810592407421},null,null,null,null,null,"x=rel.Feuchte y=Korrektur Sensibel",{"$f":"LINEST(IN5:IN11,IM5:IM11^{0,1,2},0,0)","v":4.1889084305576434E-5},-1.2306814921244535E-2,1.4014047268926058,0,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"IF(ISNA(JC13),1,IF(JK15*JC11+JL15<1,1,JK15*JC11+JL15))","v":1.5509672779575694},{"$f":"IF(JC17<1,1,JC17)","v":1.5509672779575694},null,null,null,null,null,"x=rel.Feuchte y=Korrektur Sensibel",{"$f":"LINEST(JN5:JN11,JM5:JM11^{0,1,2},0,0)","v":1.9466640307289643E-6},-1.3304262775082935E-3,1.0353756375932039,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"IF(ISNA(KE13),1,IF(KM15*KE11+KN15<1,1,KM15*KE11+KN15))","v":1.4814822006472488},{"$f":"IF(KE17<1,1,KE17)","v":1.4814822006472488},null,null,null,null,null,"x=rel.Feuchte y=Korrektur Sensibel",{"$f":"LINEST(KP5:KP11,KO5:KO11^{0,1,2},0,0)","v":6.1976986746753114E-6},-2.9004158463714507E-3,1.0795196012293835,0,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"IF(ISNA(LD13),1,IF(LL15*LD11+LM15<1,1,LL15*LD11+LM15))","v":1.4272546258553818},{"$f":"IF(LD17<1,1,LD17)","v":1.4272546258553818},null,null,null,null,null,"x=rel.Feuchte y=Korrektur Sensibel",{"$f":"LINEST(LO5:LO11,LN5:LN11^{0,1,2},0,0)","v":1.4907123051235945E-5},-5.0695830241262174E-3,1.1444696777121748,0,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"IF(ISNA(MD13),1,IF(ML15*MD11+MM15<1,1,ML15*MD11+MM15))","v":1.3727784305237769},{"$f":"IF(MD17<1,1,MD17)","v":1.3727784305237769},null,null,null,null,null,"x=rel.Feuchte y=Korrektur Sensibel",{"$f":"LINEST(MO5:MO11,MN5:MN11^{0,1,2},0,0)","v":1.9272146280604039E-5},-6.5247997431940631E-3,1.1930231613203195,0,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\n totale Leistung",{"$f":"IF(ISNA(ND13),1,IF(NL15*ND11+NM15<1,1,NL15*ND11+NM15))","v":1.3295893563466381},{"$f":"IF(ND17<1,1,ND17)","v":1.3295893563466381},null,null,null,null,null,"x=rel.Feuchte y=Korrektur Sensibel",{"$f":"LINEST(NO5:NO11,NN5:NN11^{0,1,2},0,0)","v":2.2522845629637439E-5},-7.772884886183341E-3,1.2371221347616244,0]
["Korrekturfaktor\nsensible Leistung",{"$f":"IF(ISNA(B14),1,IF(J17*B11^J16+K17*B11^K16+L17*B11^L16+M17>1,1,J17*B11^J16+K17*B11^K16+L17*B11^L16+M17))","v":0.91687466521221961},{"$f":"IF(OR(B18>1,B17=1),1,B18)","v":0.91687466521221961},"wenn B17 größer 1 oder \nB16 =1 dann C17 = 1 sonst B17",null,null,null,null,"x=KorrekturTotal; y=rel.Feuchte",{"$f":"LINEST(J6:J11,K6:K11^{0,1},0,0)","v":44.160139251523056},-10.323324630113135,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"IF(ISNA(AD14),1,IF(AL17*AD11^AL16+AM17*AD11^AM16+AN17*AD11^AN16+AO17>1,1,AL17*AD11^AL16+AM17*AD11^AM16+AN17*AD11^AN16+AO17))","v":0.89022229800484354},{"$f":"IF(OR(AD18>1,AD17=1),1,AD18)","v":0.89022229800484354},"wenn B17 größer 1 oder \nB16 =1 dann C17 = 1 sonst B17",null,null,null,null,"x=KorrekturTotal; y=rel.Feuchte",{"$f":"LINEST(AL6:AL11,AM6:AM11^{0,1},0,0)","v":53.573616770582781},-13.302518533065015,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"IF(ISNA(BC14),1,IF(BK17*BC11^BK16+BL17*BC11^BL16+BM17*BC11^BM16+BN17>1,1,BK17*BC11^BK16+BL17*BC11^BL16+BM17*BC11^BM16+BN17))","v":0.90272966864819459},{"$f":"IF(OR(BC18>1,BC17=1),1,BC18)","v":0.90272966864819459},"wenn B17 größer 1 oder \nB16 =1 dann C17 = 1 sonst B17",null,null,null,null,"x=KorrekturTotal; y=rel.Feuchte",{"$f":"LINEST(BK6:BK11,BL6:BL11^{0,1},0,0)","v":62.215232231294344},-17.116316423504223,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"IF(ISNA(CC14),1,IF(CK17*CC11^CK16+CL17*CC11^CL16+CM17*CC11^CM16+CN17>1,1,CK17*CC11^CK16+CL17*CC11^CL16+CM17*CC11^CM16+CN17))","v":0.92882336950847866},{"$f":"IF(OR(CC18>1,CC17=1),1,CC18)","v":0.92882336950847866},"wenn B17 größer 1 oder \nB16 =1 dann C17 = 1 sonst B17",null,null,null,null,"x=KorrekturTotal; y=rel.Feuchte",{"$f":"LINEST(CK6:CK11,CL6:CL11^{0,1},0,0)","v":69.603032811887246},-20.267549784304343,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"IF(ISNA(DC14),1,IF(DK17*DC11^DK16+DL17*DC11^DL16+DM17*DC11^DM16+DN17>1,1,DK17*DC11^DK16+DL17*DC11^DL16+DM17*DC11^DM16+DN17))","v":0.9555049520239639},{"$f":"IF(OR(DC18>1,DC17=1),1,DC18)","v":1},"wenn B17 größer 1 oder \nB16 =1 dann C17 = 1 sonst B17",null,null,null,null,"x=KorrekturTotal; y=rel.Feuchte",{"$f":"LINEST(DK6:DK11,DL6:DL11^{0,1},0,0)","v":74.41181463249022},-21.570955695128145,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"IF(ISNA(EB14),1,IF(EJ17*EB11^EJ16+EK17*EB11^EK16+EL17*EB11^EL16+EM17>1,1,EJ17*EB11^EJ16+EK17*EB11^EK16+EL17*EB11^EL16+EM17))","v":0.95390372074434882},{"$f":"IF(OR(EB18>1,EB17=1),1,EB18)","v":0.95390372074434882},"wenn B17 größer 1 oder \nB16 =1 dann C17 = 1 sonst B17",null,null,null,null,"x=KorrekturTotal; y=rel.Feuchte",{"$f":"LINEST(EJ6:EJ11,EK6:EK11^{0,1},0,0)","v":40.321737285888553},-10.437079068780905,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"IF(ISNA(FD14),1,IF(FL17*FD11^FL16+FM17*FD11^FM16+FN17*FD11^FN16+FO17>1,1,FL17*FD11^FL16+FM17*FD11^FM16+FN17*FD11^FN16+FO17))","v":0.92838669420897935},{"$f":"IF(OR(FD18>1,FD17=1),1,FD18)","v":0.92838669420897935},"wenn B17 größer 1 oder \nB16 =1 dann C17 = 1 sonst B17",null,null,null,null,"x=KorrekturTotal; y=rel.Feuchte",{"$f":"LINEST(FL6:FL11,FM6:FM11^{0,1},0,0)","v":42.642723110410557},-10.324101178413228,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"IF(ISNA(GC14),1,IF(GK17*GC11^GK16+GL17*GC11^GL16+GM17*GC11^GM16+GN17>1,1,GK17*GC11^GK16+GL17*GC11^GL16+GM17*GC11^GM16+GN17))","v":0.90843547179337292},{"$f":"IF(OR(GC18>1,GC17=1),1,GC18)","v":0.90843547179337292},"wenn B17 größer 1 oder \nB16 =1 dann C17 = 1 sonst B17",null,null,null,null,"x=KorrekturTotal; y=rel.Feuchte",{"$f":"LINEST(GK6:GK11,GL6:GL11^{0,1},0,0)","v":46.386170383442931},-11.633723728541526,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"IF(ISNA(HC14),1,IF(HK17*HC11^HK16+HL17*HC11^HL16+HM17*HC11^HM16+HN17>1,1,HK17*HC11^HK16+HL17*HC11^HL16+HM17*HC11^HM16+HN17))","v":0.89414968282431073},{"$f":"IF(OR(HC18>1,HC17=1),1,HC18)","v":0.89414968282431073},"wenn B17 größer 1 oder \nB16 =1 dann C17 = 1 sonst B17",null,null,null,null,"x=KorrekturTotal; y=rel.Feuchte",{"$f":"LINEST(HK6:HK11,HL6:HL11^{0,1},0,0)","v":50.528850796716561},-13.746348382423944,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"IF(ISNA(IC14),1,IF(IK17*IC11^IK16+IL17*IC11^IL16+IM17*IC11^IM16+IN17>1,1,IK17*IC11^IK16+IL17*IC11^IL16+IM17*IC11^IM16+IN17))","v":0.89078669159432011},{"$f":"IF(OR(IC18>1,IC17=1),1,IC18)","v":0.89078669159432011},"wenn B17 größer 1 oder \nB16 =1 dann C17 = 1 sonst B17",null,null,null,null,"x=KorrekturTotal; y=rel.Feuchte",{"$f":"LINEST(IK6:IK11,IL6:IL11^{0,1},0,0)","v":53.875540644326762},-14.959375884231365,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"IF(ISNA(JC14),1,IF(JK17*JC11^JK16+JL17*JC11^JL16+JM17*JC11^JM16+JN17>1,1,JK17*JC11^JK16+JL17*JC11^JL16+JM17*JC11^JM16+JN17))","v":0.97372098379461169},{"$f":"IF(OR(JC18>1,JC17=1),1,JC18)","v":0.97372098379461169},"wenn B17 größer 1 oder \nB16 =1 dann C17 = 1 sonst B17",null,null,null,null,"x=KorrekturTotal; y=rel.Feuchte",{"$f":"LINEST(JK6:JK11,JL6:JL11^{0,1},0,0)","v":38.861379310344844},-10.269852216748825,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"IF(ISNA(KE14),1,IF(KM17*KE11^KM16+KN17*KE11^KN16+KO17*KE11^KO16+KP17>1,1,KM17*KE11^KM16+KN17*KE11^KN16+KO17*KE11^KO16+KP17))","v":0.94999305559749925},{"$f":"IF(OR(KE18>1,KE17=1),1,KE18)","v":0.94999305559749925},"wenn B17 größer 1 oder \nB16 =1 dann C17 = 1 sonst B17",null,null,null,null,"x=KorrekturTotal; y=rel.Feuchte",{"$f":"LINEST(KM6:KM11,KN6:KN11^{0,1},0,0)","v":40.139743456043384},-9.4659505683595899,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"IF(ISNA(LD14),1,IF(LL17*LD11^LL16+LM17*LD11^LM16+LN17*LD11^LN16+LO17>1,1,LL17*LD11^LL16+LM17*LD11^LM16+LN17*LD11^LN16+LO17))","v":0.92825833413395376},{"$f":"IF(OR(LD18>1,LD17=1),1,LD18)","v":0.92825833413395376},"wenn B17 größer 1 oder \nB16 =1 dann C17 = 1 sonst B17",null,null,null,null,"x=KorrekturTotal; y=rel.Feuchte",{"$f":"LINEST(LL6:LL11,LM6:LM11^{0,1},0,0)","v":42.234240658764016},-10.27900593371994,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"IF(ISNA(MD14),1,IF(ML17*MD11^ML16+MM17*MD11^MM16+MN17*MD11^MN16+MO17>1,1,ML17*MD11^ML16+MM17*MD11^MM16+MN17*MD11^MN16+MO17))","v":0.91496353986212642},{"$f":"IF(OR(MD18>1,MD17=1),1,MD18)","v":0.91496353986212642},"wenn B17 größer 1 oder \nB16 =1 dann C17 = 1 sonst B17",null,null,null,null,"x=KorrekturTotal; y=rel.Feuchte",{"$f":"LINEST(ML6:ML11,MM6:MM11^{0,1},0,0)","v":44.037521388413587},-10.453067709606431,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korrekturfaktor\nsensible Leistung",{"$f":"IF(ISNA(ND14),1,IF(NL17*ND11^NL16+NM17*ND11^NM16+NN17*ND11^NN16+NO17>1,1,NL17*ND11^NL16+NM17*ND11^NM16+NN17*ND11^NN16+NO17))","v":0.90478500452655086},{"$f":"IF(OR(ND18>1,ND17=1),1,ND18)","v":0.90478500452655086},"wenn B17 größer 1 oder \nB16 =1 dann C17 = 1 sonst B17",null,null,null,null,"x=KorrekturTotal; y=rel.Feuchte",{"$f":"LINEST(NL6:NL11,NM6:NM11^{0,1},0,0)","v":46.381193863079631},-11.667213889724511]
[]
[]
["TWI [°C]","TWO [°C]","QA [m³/h]","TAI [°C]","UR [%]","PT [kW]","PS [kW]","m [kg/h]","Kondensat ja/nein","Total Basis (trocken)","Faktor Total","Faktor Sensibel"]
[3,7.6,100,21,1,0.54,0.54,100,{"$f":"IF(F22<>G22,1,0)","v":0},{"$f":"IF(F22/G22=1,F22,J21)","v":0.54},{"$f":"F22/J22","v":1},{"$f":"G22/J22","v":1},null,"Volumenstrom","Korrekturfaktor\n totale Leistung","Korrekturfaktor\nsensible Leistung","Koeffizienten \nTotal","exponent","Koeffizienten \nSensibel","exponent",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Volumenstrom","Korrekturfaktor\n totale Leistung","Korrekturfaktor\nsensible Leistung","Koeffizienten \nTotal","exponent","Koeffizienten \nSensibel","exponent",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Volumenstrom","Korrekturfaktor\n totale Leistung","Korrekturfaktor\nsensible Leistung","Koeffizienten \nTotal","exponent","Koeffizienten \nSensibel","exponent"]
[3,8.6999999999999993,100,21,50,0.67,0.49,100,1,{"$f":"IF(F23/G23=1,F23,J22)","v":0.54},1.2407407407407407,{"$f":"G23/J23","v":0.90740740740740733},null,{"$f":"B3","v":100},{"$f":"C17","v":1.3660687839394439},{"$f":"C18","v":0.91687466521221961},{"$f":"TRANSPOSE(LINEST(O23:O27,N23:N27^{0,1,2,3},0,0))","v":-5.4030981122289094E-9},3,{"$f":"TRANSPOSE(LINEST(P23:P27,N23:N27^{0,1,2,3},0,0))","v":1.4390650584327849E-9},3,"a",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"EB3","v":100},{"$f":"EC17","v":1.4989140596907593},{"$f":"EC18","v":0.95390372074434882},{"$f":"TRANSPOSE(LINEST(EO23:EO27,EN23:EN27^{0,1,2,3},0,0))","v":3.1660993357339008E-9},3,{"$f":"TRANSPOSE(LINEST(EP23:EP27,EN23:EN27^{0,1,2,3},0,0))","v":1.3015047665957573E-9},3,"a",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"JC3","v":100},{"$f":"JD17","v":1.5509672779575694},{"$f":"JD18","v":0.97372098379461169},{"$f":"TRANSPOSE(LINEST(JP23:JP27,JO23:JO27^{0,1,2,3},0,0))","v":-9.6462132264044552E-10},3,{"$f":"TRANSPOSE(LINEST(JQ23:JQ27,JO23:JO27^{0,1,2,3},0,0))","v":2.7285038937901869E-10},3,"a"]
[3,9.6,100,21,60,0.77,0.48,100,1,{"$f":"IF(F24/G24=1,F24,J23)","v":0.54},1.4259259259259258,0.88888888888888884,null,{"$f":"AD3","v":170},{"$f":"AE17","v":1.1816731763568051},{"$f":"AE18","v":0.89022229800484354},9.4693615392813825E-6,2,2.014081986131429E-6,2,"b",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"FD3","v":170},{"$f":"FE17","v":1.4146812130917823},{"$f":"FE18","v":0.92838669420897935},-1.1762791060428553E-6,2,-2.0860669641979294E-7,2,"b",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"KE3","v":170},{"$f":"KF17","v":1.4814822006472488},{"$f":"KF18","v":0.94999305559749925},1.4575504678495836E-6,2,3.2160475922128357E-7,2,"b"]
[3,10.4,100,21,70,0.87,0.47,100,1,{"$f":"IF(F25/G25=1,F25,J24)","v":0.54},1.6111111111111109,0.87037037037037024,null,{"$f":"BC3","v":240},{"$f":"BD17","v":1.0789888257922702},{"$f":"BD18","v":0.90272966864819459},-4.8131259761316665E-3,1,-9.4675927491491259E-4,1,"c",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"GC3","v":240},{"$f":"GD17","v":1.3287114563106799},{"$f":"GD18","v":0.90843547179337292},-1.0914471143304114E-3,1,-3.7569626406162854E-4,1,"c",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"LD3","v":240},{"$f":"LE17","v":1.4272546258553818},{"$f":"LE18","v":0.92825833413395376},-1.3046665164165368E-3,1,-4.5306662530010197E-4,1,"c"]
[3,11.3,100,21,80,0.97,0.45,100,1,0.54,1.7962962962962961,0.83333333333333326,null,{"$f":"CC3","v":310},{"$f":"CD17","v":1.0097583603020495},{"$f":"CD18","v":0.92882336950847866},1.7570297843854885,0,0.98915542196899187,0,"d",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"HC3","v":310},{"$f":"HD17","v":1.2615988804338323},{"$f":"HD18","v":0.89414968282431073},1.6170576988100227,0,0.99218422742003187,0,"d",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"MD3","v":310},{"$f":"ME17","v":1.3727784305237769},{"$f":"ME18","v":0.91496353986212642},1.6674367338897629,0,1.0157068967532243,0,"d"]
[3,12.2,100,21,90,1.07,0.44,100,1,0.54,1.9814814814814814,0.81481481481481477,null,{"$f":"DC3","v":380},{"$f":"DD17","v":1},{"$f":"DD18","v":1},0,0,0,0,"e",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IC3","v":380},{"$f":"ID17","v":1.2057810592407421},{"$f":"ID18","v":0.89078669159432011},0,0,0,0,"e",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"ND3","v":380},{"$f":"NE17","v":1.3295893563466381},{"$f":"NE18","v":0.90478500452655086},0,0,0,0,"e"]
[3,13,100,21,99,1.1599999999999999,0.43,100,1,{"$f":"IF(F28/G28=1,F28,J27)","v":0.54},2.1481481481481479,0.79629629629629628]
[3,5.4,100,21,1,0.56999999999999995,0.56999999999999995,200,0,0.56999999999999995,1,1,null,null,null,null,null,null,null,null,null,null,null,"Wassermassenstrom wk","Korrektur"]
[3,6.3,100,21,50,0.77,0.55000000000000004,200,1,0.56999999999999995,{"$f":"F30/J30","v":1.3508771929824563},0.9649122807017545,null,null,null,null,null,null,null,null,null,null,null,null,"Total","Total","Total","Sensibel","Sensibel","Sensibel","Koeffizienten Total",null,null,"Korrektur Total \nbei wk","Koeffizienten Total",null,null,"Korrektur Sensibel\nbei wk"]
[3,6.8,100,21,60,0.89,0.54,200,1,{"$f":"IF(F31/G31=1,F31,J30)","v":0.56999999999999995},{"$f":"F31/J31","v":1.56140350877193},0.94736842105263175,null,"x = Volumenstrom",null,null,"y = Total",null,"y = Sensibel",null,null,null,null,null,{"$f":"I2","v":100},{"$f":"I3","v":200},{"$f":"I4","v":300},{"$f":"I2","v":100},{"$f":"I3","v":200},{"$f":"I4","v":300},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"x = Volumenstrom",null,null,"y = Total",null,"y = Sensibel",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"x = Volumenstrom",null,null,"y = Total",null,"y = Sensibel"]
[3,7.3,100,21,70,1.01,0.54,200,1,0.56999999999999995,{"$f":"F32/J32","v":1.7719298245614037},0.94736842105263175,null,{"$f":"Auswertung_Leistung!J276","v":164.02443076580053},null,null,{"$f":"IF(Q$23*$N32^R$23+Q$24*$N32^R$24+Q$25*$N32^R$25+Q$26*$N32^R$26+Q$27*$N32^R$27<1,1,Q$23*$N32^R$23+Q$24*$N32^R$24+Q$25*$N32^R$25+Q$26*$N32^R$26+Q$27*$N32^R$27)","v":1.198479954560647},null,{"$f":"IF(S$23*$N32^T$23+S$24*$N32^T$24+S$25*$N32^T$25+S$26*$N32^T$26+S$27*$N32^T$27>1,1,S$23*$N32^T$23+S$24*$N32^T$24+S$25*$N32^T$25+S$26*$N32^T$26+S$27*$N32^T$27)","v":0.89440113314833414},null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},{"$f":"Q32","v":1.198479954560647},{"$f":"EQ32","v":1.4203588067994268},{"$f":"JR32","v":1.4883967167775192},{"$f":"S32","v":0.89440113314833414},{"$f":"ES32","v":0.93069193474908996},{"$f":"JT32","v":0.95124942607768725},{"$f":"LINEST(TRANSPOSE(Y32:AA32),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-7.6920471130343755E-6},4.5264026562981102E-3,0.8227601600611798,{"$f":"AE32*X32^2+AF32*X32+AG32","v":1.4203588067994268},{"$f":"LINEST(TRANSPOSE(AB32:AD32),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-7.8666551360793171E-7},5.9890767008994022E-4,0.84237702127541914,{"$f":"AI32*X32^2+AJ32*X32+AK32","v":0.93069193474908996},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"$N32","v":164.02443076580053},null,null,{"$f":"IF(EQ$23*$N32^ER$23+EQ$24*$N32^ER$24+EQ$25*$N32^ER$25+EQ$26*$N32^ER$26+EQ$27*$N32^ER$27<1,1,EQ$23*$N32^ER$23+EQ$24*$N32^ER$24+EQ$25*$N32^ER$25+EQ$26*$N32^ER$26+EQ$27*$N32^ER$27)","v":1.4203588067994268},null,{"$f":"IF(ES$23*$N32^ET$23+ES$24*$N32^ET$24+ES$25*$N32^ET$25+ES$26*$N32^ET$26+ES$27*$N32^ET$27>1,1,ES$23*$N32^ET$23+ES$24*$N32^ET$24+ES$25*$N32^ET$25+ES$26*$N32^ET$26+ES$27*$N32^ET$27)","v":0.93069193474908996},null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"$N32","v":164.02443076580053},null,null,{"$f":"IF(JR$23*$N32^JS$23+JR$24*$N32^JS$24+JR$25*$N32^JS$25+JR$26*$N32^JS$26+JR$27*$N32^JS$27<1,1,JR$23*$N32^JS$23+JR$24*$N32^JS$24+JR$25*$N32^JS$25+JR$26*$N32^JS$26+JR$27*$N32^JS$27)","v":1.4883967167775192},null,{"$f":"IF(JT$23*$N32^JU$23+JT$24*$N32^JU$24+JT$25*$N32^JU$25+JT$26*$N32^JU$26+JT$27*$N32^JU$27>1,1,JT$23*$N32^JU$23+JT$24*$N32^JU$24+JT$25*$N32^JU$25+JT$26*$N32^JU$26+JT$27*$N32^JU$27)","v":0.95124942607768725},null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"}]
[3,7.8,100,21,80,1.1299999999999999,0.53,200,1,0.56999999999999995,1.9824561403508771,0.92982456140350889,null,{"$f":"Auswertung_Leistung!J277","v":154.89530616677845},null,null,1.2186136297276982,null,0.89617787561759632,null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},{"$f":"Q33","v":1.2186136297276982},{"$f":"EQ33","v":1.431542005216897},{"$f":"JR33","v":1.4967355201248755},{"$f":"S33","v":0.89617787561759632},{"$f":"ES33","v":0.93382245854282897},{"$f":"JT33","v":0.95425912652532729},{"$f":"LINEST(TRANSPOSE(Y33:AA33),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-7.3867430290609873E-6},4.3453066636102832E-3,0.85795039365727988,1.431542005216897,{"$f":"LINEST(TRANSPOSE(AB33:AD33),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-8.6039574713674657E-7},6.345645533933548E-4,0.84132537774962801,0.93382245854282908,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"$N33","v":154.89530616677845},null,null,1.431542005216897,null,0.93382245854282897,null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"$N33","v":154.89530616677845},null,null,1.4967355201248755,null,0.95425912652532729,null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"}]
[3,8.3000000000000007,100,21,90,1.25,0.52,200,1,0.56999999999999995,2.192982456140351,0.91228070175438603,null,{"$f":"Auswertung_Leistung!J278","v":98.926386288835431},null,null,1.3683249331773524,null,0.91659983129294642,null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.3683249331773524,1.500638422150776,1.5517011208252574,0.91659983129294642,0.95423647266969269,0.97429817152133258,{"$f":"LINEST(TRANSPOSE(Y34:AA34),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-4.0625395149470943E-6},2.5418967442183619E-3,1.1547606539049873,1.500638422150776,{"$f":"LINEST(TRANSPOSE(AB34:AD34),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-8.7874712625533724E-7},6.3999055164406539E-4,0.86138824739109299,0.95423647266969258,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,98.926386288835431,null,null,1.500638422150776,null,0.95423647266969269,null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,98.926386288835431,null,null,1.5517011208252574,null,0.97429817152133258,null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"}]
[3,8.8000000000000007,100,21,99,1.35,0.52,200,1,0.56999999999999995,2.3684210526315792,0.91228070175438603,null,{"$f":"Auswertung_Leistung!J279","v":81.627063125975369},null,null,1.4243039556453481,null,0.92607670336274373,null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.4243039556453481,1.5218505309956356,1.5701276261228143,0.92607670336274373,0.96083516452126305,0.98101564165635269,{"$f":"LINEST(TRANSPOSE(Y35:AA35),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-2.4634740111554738E-6},1.714507956849524E-3,1.2774879000719497,1.5218505309956356,{"$f":"LINEST(TRANSPOSE(AB35:AD35),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-7.2889920117149123E-7},5.6625437193664194E-4,0.87674025818079415,0.96083516452126294,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,81.627063125975369,null,null,1.5218505309956356,null,0.96083516452126305,null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,81.627063125975369,null,null,1.5701276261228143,null,0.98101564165635269,null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"}]
[3,4.5999999999999996,100,21,1,0.57999999999999996,0.57999999999999996,300,0,0.57999999999999996,1,1,null,{"$f":"Auswertung_Leistung!J280","v":86.350933922726639},null,null,1.408541085846214,null,0.92334642112330967,null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.408541085846214,1.5160778851913601,1.5650246682586422,0.92334642112330967,0.95902503721811327,0.97915789256715047,{"$f":"LINEST(TRANSPOSE(Y36:AA36),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-2.9295008138931805E-6},1.9542182376194122E-3,1.2424142702232046,1.5160778851913599,{"$f":"LINEST(TRANSPOSE(AB36:AD36),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-7.7728803728833919E-7},5.8997257213453996E-4,0.87212204428273898,0.95902503721811339,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,86.350933922726639,null,null,1.5160778851913601,null,0.95902503721811327,null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,86.350933922726639,null,null,1.5650246682586422,null,0.97915789256715047,null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"}]
[3,5.3,100,21,50,0.8,0.56000000000000005,300,1,0.57999999999999996,1.3793103448275863,0.9655172413793105,null,{"$f":"Auswertung_Leistung!J281","v":79.802348196225324},null,null,{"$f":"IF(Q$23*$N37^R$23+Q$24*$N37^R$24+Q$25*$N37^R$25+Q$26*$N37^R$26+Q$27*$N37^R$27<1,1,Q$23*$N37^R$23+Q$24*$N37^R$24+Q$25*$N37^R$25+Q$26*$N37^R$26+Q$27*$N37^R$27)","v":1.430489918732885},null,{"$f":"IF(S$23*$N37^T$23+S$24*$N37^T$24+S$25*$N37^T$25+S$26*$N37^T$26+S$27*$N37^T$27>1,1,S$23*$N37^T$23+S$24*$N37^T$24+S$25*$N37^T$25+S$26*$N37^T$26+S$27*$N37^T$27)","v":0.92715967180035075},null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.430489918732885,1.5240756803566906,1.5721133337069699,0.92715967180035075,0.96153573290491057,0.98173789517765542,{"$f":"LINEST(TRANSPOSE(Y37:AA37),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-2.2774054136763626E-6},1.6190792403409711E-3,1.2913560488355509,{"$f":"AE37*X37^2+AF37*X37+AG37","v":1.5240756803566906},{"$f":"LINEST(TRANSPOSE(AB37:AD37),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-7.0869494159075122E-7},5.5636909352282525E-4,0.87860971186397552,{"$f":"AI37*X37^2+AJ37*X37+AK37","v":0.96153573290491057},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,79.802348196225324,null,null,1.5240756803566906,null,0.96153573290491057,null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,79.802348196225324,null,null,1.5721133337069699,null,0.98173789517765542,null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"}]
[3,5.6,100,21,60,0.92,0.56000000000000005,300,1,0.57999999999999996,1.5862068965517244,0.9655172413793105,null,{"$f":"Auswertung_Leistung!J282","v":63.7559727987841},null,null,1.4872552945776636,null,0.93735369583548767,null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.4872552945776636,1.5435105748695774,1.5899311489915455,0.93735369583548767,0.96772069093466062,0.9881991711173157,{"$f":"LINEST(TRANSPOSE(Y38:AA38),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-4.9173530849726102E-7},7.1007339546831345E-4,1.4211653081158049,1.5435105748695772,{"$f":"LINEST(TRANSPOSE(AB38:AD38),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-4.9442574582591449E-7},4.5199767473950715E-4,0.89709818581979572,0.96772069093466051,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.7559727987841,null,null,1.5435105748695774,null,0.96772069093466062,null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.7559727987841,null,null,1.5899311489915455,null,0.9881991711173157,null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"}]
[3,6,100,21,70,1.04,0.55000000000000004,300,1,0.57999999999999996,1.7931034482758623,0.94827586206896564,null,{"$f":"Auswertung_Leistung!J283","v":63.7559727987841},null,null,1.4872552945776636,null,0.93735369583548767,null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.4872552945776636,1.5435105748695774,1.5899311489915455,0.93735369583548767,0.96772069093466062,0.9881991711173157,{"$f":"LINEST(TRANSPOSE(Y39:AA39),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-4.9173530849726102E-7},7.1007339546831345E-4,1.4211653081158049,1.5435105748695772,{"$f":"LINEST(TRANSPOSE(AB39:AD39),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-4.9442574582591449E-7},4.5199767473950715E-4,0.89709818581979572,0.96772069093466051,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.7559727987841,null,null,1.5435105748695774,null,0.96772069093466062,null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.7559727987841,null,null,1.5899311489915455,null,0.9881991711173157,null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"}]
[3,6.3,100,21,80,1.1599999999999999,0.55000000000000004,300,1,0.57999999999999996,2,0.94827586206896564,null,{"$f":"Auswertung_Leistung!J284","v":63.7559727987841},null,null,1.4872552945776636,null,0.93735369583548767,null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.4872552945776636,1.5435105748695774,1.5899311489915455,0.93735369583548767,0.96772069093466062,0.9881991711173157,{"$f":"LINEST(TRANSPOSE(Y40:AA40),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-4.9173530849726102E-7},7.1007339546831345E-4,1.4211653081158049,1.5435105748695772,{"$f":"LINEST(TRANSPOSE(AB40:AD40),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-4.9442574582591449E-7},4.5199767473950715E-4,0.89709818581979572,0.96772069093466051,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.7559727987841,null,null,1.5435105748695774,null,0.96772069093466062,null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.7559727987841,null,null,1.5899311489915455,null,0.9881991711173157,null,null,{"$f":"Auswertung_Leistung!$A$271","v":"Baugröße 630"}]
[3,6.7,100,21,90,1.29,0.54,300,1,0.57999999999999996,2.2241379310344831,0.93103448275862077]
[3,7,100,21,99,1.4,0.54,300,1,0.57999999999999996,2.4137931034482758,0.93103448275862077]
[3,7.9,100,22,1,0.56999999999999995,0.56999999999999995,100,0,0.56999999999999995,1,1]
[3,9.1999999999999993,100,22,50,0.72,0.52,100,1,0.56999999999999995,1.2631578947368423,0.91228070175438603]
[3,10.1,100,22,60,0.83,0.5,100,1,0.56999999999999995,1.4561403508771931,0.87719298245614041]
[3,11,100,22,70,0.94,0.49,100,1,0.56999999999999995,1.6491228070175439,0.85964912280701755]
[3,12,100,22,80,1.05,0.47,100,1,0.56999999999999995,1.8421052631578949,0.82456140350877194]
[3,12.9,100,22,90,1.1499999999999999,0.46,100,1,0.56999999999999995,2.0175438596491229,0.80701754385964919]
[3,13.7,100,22,99,1.25,0.45,100,1,0.56999999999999995,2.192982456140351,0.78947368421052644]
[3,5.6,100,22,1,0.6,0.6,200,0,0.6,1,1]
[3,6.6,100,22,50,0.84,0.57999999999999996,200,1,0.6,1.4,0.96666666666666667,null,{"$f":"Auswertung_Leistung!J295","v":164.02443076580053},null,null,{"$f":"IF(Q$23*$N51^R$23+Q$24*$N51^R$24+Q$25*$N51^R$25+Q$26*$N51^R$26+Q$27*$N51^R$27<1,1,Q$23*$N51^R$23+Q$24*$N51^R$24+Q$25*$N51^R$25+Q$26*$N51^R$26+Q$27*$N51^R$27)","v":1.198479954560647},null,{"$f":"IF(S$23*$N51^T$23+S$24*$N51^T$24+S$25*$N51^T$25+S$26*$N51^T$26+S$27*$N51^T$27>1,1,S$23*$N51^T$23+S$24*$N51^T$24+S$25*$N51^T$25+S$26*$N51^T$26+S$27*$N51^T$27)","v":0.89440113314833414},null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.198479954560647,1.4203588067994268,1.4883967167775192,{"$f":"S51","v":0.89440113314833414},{"$f":"ES51","v":0.93069193474908996},0.95124942607768725,{"$f":"LINEST(TRANSPOSE(Y51:AA51),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-7.6920471130343755E-6},4.5264026562981102E-3,0.8227601600611798,{"$f":"AE51*X51^2+AF51*X51+AG51","v":1.4203588067994268},{"$f":"LINEST(TRANSPOSE(AB51:AD51),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-7.8666551360793171E-7},5.9890767008994022E-4,0.84237702127541914,{"$f":"AI51*X51^2+AJ51*X51+AK51","v":0.93069193474908996},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,164.02443076580053,null,null,{"$f":"IF(EQ$23*$N51^ER$23+EQ$24*$N51^ER$24+EQ$25*$N51^ER$25+EQ$26*$N51^ER$26+EQ$27*$N51^ER$27<1,1,EQ$23*$N51^ER$23+EQ$24*$N51^ER$24+EQ$25*$N51^ER$25+EQ$26*$N51^ER$26+EQ$27*$N51^ER$27)","v":1.4203588067994268},null,{"$f":"IF(ES$23*$N51^ET$23+ES$24*$N51^ET$24+ES$25*$N51^ET$25+ES$26*$N51^ET$26+ES$27*$N51^ET$27>1,1,ES$23*$N51^ET$23+ES$24*$N51^ET$24+ES$25*$N51^ET$25+ES$26*$N51^ET$26+ES$27*$N51^ET$27)","v":0.93069193474908996},null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,164.02443076580053,null,null,{"$f":"IF(JR$23*$N51^JS$23+JR$24*$N51^JS$24+JR$25*$N51^JS$25+JR$26*$N51^JS$26+JR$27*$N51^JS$27<1,1,JR$23*$N51^JS$23+JR$24*$N51^JS$24+JR$25*$N51^JS$25+JR$26*$N51^JS$26+JR$27*$N51^JS$27)","v":1.4883967167775192},null,{"$f":"IF(JT$23*$N51^JU$23+JT$24*$N51^JU$24+JT$25*$N51^JU$25+JT$26*$N51^JU$26+JT$27*$N51^JU$27>1,1,JT$23*$N51^JU$23+JT$24*$N51^JU$24+JT$25*$N51^JU$25+JT$26*$N51^JU$26+JT$27*$N51^JU$27)","v":0.95124942607768725},null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"}]
[3,7.1,100,22,60,0.96,0.56999999999999995,200,1,0.6,1.6,0.95,null,{"$f":"Auswertung_Leistung!J296","v":154.89530616677845},null,null,{"$f":"IF(Q$23*$N52^R$23+Q$24*$N52^R$24+Q$25*$N52^R$25+Q$26*$N52^R$26+Q$27*$N52^R$27<1,1,Q$23*$N52^R$23+Q$24*$N52^R$24+Q$25*$N52^R$25+Q$26*$N52^R$26+Q$27*$N52^R$27)","v":1.2186136297276982},null,{"$f":"IF(S$23*$N52^T$23+S$24*$N52^T$24+S$25*$N52^T$25+S$26*$N52^T$26+S$27*$N52^T$27>1,1,S$23*$N52^T$23+S$24*$N52^T$24+S$25*$N52^T$25+S$26*$N52^T$26+S$27*$N52^T$27)","v":0.89617787561759632},null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.2186136297276982,1.431542005216897,1.4967355201248755,0.89617787561759632,0.93382245854282897,0.95425912652532729,{"$f":"LINEST(TRANSPOSE(Y52:AA52),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-7.3867430290609873E-6},4.3453066636102832E-3,0.85795039365727988,1.431542005216897,{"$f":"LINEST(TRANSPOSE(AB52:AD52),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-8.6039574713674657E-7},6.345645533933548E-4,0.84132537774962801,{"$f":"AI52*X52^2+AJ52*X52+AK52","v":0.93382245854282908},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,154.89530616677845,null,null,{"$f":"IF(EQ$23*$N52^ER$23+EQ$24*$N52^ER$24+EQ$25*$N52^ER$25+EQ$26*$N52^ER$26+EQ$27*$N52^ER$27<1,1,EQ$23*$N52^ER$23+EQ$24*$N52^ER$24+EQ$25*$N52^ER$25+EQ$26*$N52^ER$26+EQ$27*$N52^ER$27)","v":1.431542005216897},null,{"$f":"IF(ES$23*$N52^ET$23+ES$24*$N52^ET$24+ES$25*$N52^ET$25+ES$26*$N52^ET$26+ES$27*$N52^ET$27>1,1,ES$23*$N52^ET$23+ES$24*$N52^ET$24+ES$25*$N52^ET$25+ES$26*$N52^ET$26+ES$27*$N52^ET$27)","v":0.93382245854282897},null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,154.89530616677845,null,null,{"$f":"IF(JR$23*$N52^JS$23+JR$24*$N52^JS$24+JR$25*$N52^JS$25+JR$26*$N52^JS$26+JR$27*$N52^JS$27<1,1,JR$23*$N52^JS$23+JR$24*$N52^JS$24+JR$25*$N52^JS$25+JR$26*$N52^JS$26+JR$27*$N52^JS$27)","v":1.4967355201248755},null,{"$f":"IF(JT$23*$N52^JU$23+JT$24*$N52^JU$24+JT$25*$N52^JU$25+JT$26*$N52^JU$26+JT$27*$N52^JU$27>1,1,JT$23*$N52^JU$23+JT$24*$N52^JU$24+JT$25*$N52^JU$25+JT$26*$N52^JU$26+JT$27*$N52^JU$27)","v":0.95425912652532729},null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"}]
[3,7.7,100,22,70,1.0900000000000001,0.56000000000000005,200,1,0.6,1.8166666666666669,0.93333333333333346,null,{"$f":"Auswertung_Leistung!J297","v":98.926386288835431},null,null,{"$f":"IF(Q$23*$N53^R$23+Q$24*$N53^R$24+Q$25*$N53^R$25+Q$26*$N53^R$26+Q$27*$N53^R$27<1,1,Q$23*$N53^R$23+Q$24*$N53^R$24+Q$25*$N53^R$25+Q$26*$N53^R$26+Q$27*$N53^R$27)","v":1.3683249331773524},null,{"$f":"IF(S$23*$N53^T$23+S$24*$N53^T$24+S$25*$N53^T$25+S$26*$N53^T$26+S$27*$N53^T$27>1,1,S$23*$N53^T$23+S$24*$N53^T$24+S$25*$N53^T$25+S$26*$N53^T$26+S$27*$N53^T$27)","v":0.91659983129294642},null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.3683249331773524,1.500638422150776,1.5517011208252574,0.91659983129294642,0.95423647266969269,0.97429817152133258,{"$f":"LINEST(TRANSPOSE(Y53:AA53),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-4.0625395149470943E-6},2.5418967442183619E-3,1.1547606539049873,1.500638422150776,{"$f":"LINEST(TRANSPOSE(AB53:AD53),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-8.7874712625533724E-7},6.3999055164406539E-4,0.86138824739109299,0.95423647266969258,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,98.926386288835431,null,null,{"$f":"IF(EQ$23*$N53^ER$23+EQ$24*$N53^ER$24+EQ$25*$N53^ER$25+EQ$26*$N53^ER$26+EQ$27*$N53^ER$27<1,1,EQ$23*$N53^ER$23+EQ$24*$N53^ER$24+EQ$25*$N53^ER$25+EQ$26*$N53^ER$26+EQ$27*$N53^ER$27)","v":1.500638422150776},null,{"$f":"IF(ES$23*$N53^ET$23+ES$24*$N53^ET$24+ES$25*$N53^ET$25+ES$26*$N53^ET$26+ES$27*$N53^ET$27>1,1,ES$23*$N53^ET$23+ES$24*$N53^ET$24+ES$25*$N53^ET$25+ES$26*$N53^ET$26+ES$27*$N53^ET$27)","v":0.95423647266969269},null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,98.926386288835431,null,null,{"$f":"IF(JR$23*$N53^JS$23+JR$24*$N53^JS$24+JR$25*$N53^JS$25+JR$26*$N53^JS$26+JR$27*$N53^JS$27<1,1,JR$23*$N53^JS$23+JR$24*$N53^JS$24+JR$25*$N53^JS$25+JR$26*$N53^JS$26+JR$27*$N53^JS$27)","v":1.5517011208252574},null,{"$f":"IF(JT$23*$N53^JU$23+JT$24*$N53^JU$24+JT$25*$N53^JU$25+JT$26*$N53^JU$26+JT$27*$N53^JU$27>1,1,JT$23*$N53^JU$23+JT$24*$N53^JU$24+JT$25*$N53^JU$25+JT$26*$N53^JU$26+JT$27*$N53^JU$27)","v":0.97429817152133258},null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"}]
[3,8.1999999999999993,100,22,80,1.21,0.56000000000000005,200,1,0.6,2.0166666666666666,0.93333333333333346,null,{"$f":"Auswertung_Leistung!J298","v":81.627063125975369},null,null,{"$f":"IF(Q$23*$N54^R$23+Q$24*$N54^R$24+Q$25*$N54^R$25+Q$26*$N54^R$26+Q$27*$N54^R$27<1,1,Q$23*$N54^R$23+Q$24*$N54^R$24+Q$25*$N54^R$25+Q$26*$N54^R$26+Q$27*$N54^R$27)","v":1.4243039556453481},null,{"$f":"IF(S$23*$N54^T$23+S$24*$N54^T$24+S$25*$N54^T$25+S$26*$N54^T$26+S$27*$N54^T$27>1,1,S$23*$N54^T$23+S$24*$N54^T$24+S$25*$N54^T$25+S$26*$N54^T$26+S$27*$N54^T$27)","v":0.92607670336274373},null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.4243039556453481,1.5218505309956356,1.5701276261228143,0.92607670336274373,0.96083516452126305,0.98101564165635269,{"$f":"LINEST(TRANSPOSE(Y54:AA54),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-2.4634740111554738E-6},1.714507956849524E-3,1.2774879000719497,1.5218505309956356,{"$f":"LINEST(TRANSPOSE(AB54:AD54),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-7.2889920117149123E-7},5.6625437193664194E-4,0.87674025818079415,0.96083516452126294,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,81.627063125975369,null,null,{"$f":"IF(EQ$23*$N54^ER$23+EQ$24*$N54^ER$24+EQ$25*$N54^ER$25+EQ$26*$N54^ER$26+EQ$27*$N54^ER$27<1,1,EQ$23*$N54^ER$23+EQ$24*$N54^ER$24+EQ$25*$N54^ER$25+EQ$26*$N54^ER$26+EQ$27*$N54^ER$27)","v":1.5218505309956356},null,{"$f":"IF(ES$23*$N54^ET$23+ES$24*$N54^ET$24+ES$25*$N54^ET$25+ES$26*$N54^ET$26+ES$27*$N54^ET$27>1,1,ES$23*$N54^ET$23+ES$24*$N54^ET$24+ES$25*$N54^ET$25+ES$26*$N54^ET$26+ES$27*$N54^ET$27)","v":0.96083516452126305},null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,81.627063125975369,null,null,{"$f":"IF(JR$23*$N54^JS$23+JR$24*$N54^JS$24+JR$25*$N54^JS$25+JR$26*$N54^JS$26+JR$27*$N54^JS$27<1,1,JR$23*$N54^JS$23+JR$24*$N54^JS$24+JR$25*$N54^JS$25+JR$26*$N54^JS$26+JR$27*$N54^JS$27)","v":1.5701276261228143},null,{"$f":"IF(JT$23*$N54^JU$23+JT$24*$N54^JU$24+JT$25*$N54^JU$25+JT$26*$N54^JU$26+JT$27*$N54^JU$27>1,1,JT$23*$N54^JU$23+JT$24*$N54^JU$24+JT$25*$N54^JU$25+JT$26*$N54^JU$26+JT$27*$N54^JU$27)","v":0.98101564165635269},null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"}]
[3,8.6999999999999993,100,22,90,1.34,0.55000000000000004,200,1,0.6,2.2333333333333334,0.91666666666666674,null,{"$f":"Auswertung_Leistung!J299","v":86.350933922726639},null,null,{"$f":"IF(Q$23*$N55^R$23+Q$24*$N55^R$24+Q$25*$N55^R$25+Q$26*$N55^R$26+Q$27*$N55^R$27<1,1,Q$23*$N55^R$23+Q$24*$N55^R$24+Q$25*$N55^R$25+Q$26*$N55^R$26+Q$27*$N55^R$27)","v":1.408541085846214},null,{"$f":"IF(S$23*$N55^T$23+S$24*$N55^T$24+S$25*$N55^T$25+S$26*$N55^T$26+S$27*$N55^T$27>1,1,S$23*$N55^T$23+S$24*$N55^T$24+S$25*$N55^T$25+S$26*$N55^T$26+S$27*$N55^T$27)","v":0.92334642112330967},null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.408541085846214,1.5160778851913601,1.5650246682586422,0.92334642112330967,0.95902503721811327,0.97915789256715047,{"$f":"LINEST(TRANSPOSE(Y55:AA55),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-2.9295008138931805E-6},1.9542182376194122E-3,1.2424142702232046,{"$f":"AE55*X55^2+AF55*X55+AG55","v":1.5160778851913599},{"$f":"LINEST(TRANSPOSE(AB55:AD55),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-7.7728803728833919E-7},5.8997257213453996E-4,0.87212204428273898,{"$f":"AI55*X55^2+AJ55*X55+AK55","v":0.95902503721811339},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,86.350933922726639,null,null,{"$f":"IF(EQ$23*$N55^ER$23+EQ$24*$N55^ER$24+EQ$25*$N55^ER$25+EQ$26*$N55^ER$26+EQ$27*$N55^ER$27<1,1,EQ$23*$N55^ER$23+EQ$24*$N55^ER$24+EQ$25*$N55^ER$25+EQ$26*$N55^ER$26+EQ$27*$N55^ER$27)","v":1.5160778851913601},null,{"$f":"IF(ES$23*$N55^ET$23+ES$24*$N55^ET$24+ES$25*$N55^ET$25+ES$26*$N55^ET$26+ES$27*$N55^ET$27>1,1,ES$23*$N55^ET$23+ES$24*$N55^ET$24+ES$25*$N55^ET$25+ES$26*$N55^ET$26+ES$27*$N55^ET$27)","v":0.95902503721811327},null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,86.350933922726639,null,null,{"$f":"IF(JR$23*$N55^JS$23+JR$24*$N55^JS$24+JR$25*$N55^JS$25+JR$26*$N55^JS$26+JR$27*$N55^JS$27<1,1,JR$23*$N55^JS$23+JR$24*$N55^JS$24+JR$25*$N55^JS$25+JR$26*$N55^JS$26+JR$27*$N55^JS$27)","v":1.5650246682586422},null,{"$f":"IF(JT$23*$N55^JU$23+JT$24*$N55^JU$24+JT$25*$N55^JU$25+JT$26*$N55^JU$26+JT$27*$N55^JU$27>1,1,JT$23*$N55^JU$23+JT$24*$N55^JU$24+JT$25*$N55^JU$25+JT$26*$N55^JU$26+JT$27*$N55^JU$27)","v":0.97915789256715047},null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"}]
[3,9.1999999999999993,100,22,99,1.45,0.54,200,1,0.6,2.4166666666666665,0.90000000000000013,null,{"$f":"Auswertung_Leistung!J300","v":79.802348196225324},null,null,1.430489918732885,null,0.92715967180035075,null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.430489918732885,1.5240756803566906,1.5721133337069699,0.92715967180035075,0.96153573290491057,0.98173789517765542,{"$f":"LINEST(TRANSPOSE(Y56:AA56),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-2.2774054136763626E-6},1.6190792403409711E-3,1.2913560488355509,1.5240756803566906,{"$f":"LINEST(TRANSPOSE(AB56:AD56),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-7.0869494159075122E-7},5.5636909352282525E-4,0.87860971186397552,0.96153573290491057,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,79.802348196225324,null,null,1.5240756803566906,null,0.96153573290491057,null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,79.802348196225324,null,null,1.5721133337069699,null,0.98173789517765542,null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"}]
[3,4.7,100,22,1,0.61,0.61,300,0,0.61,1,1,null,{"$f":"Auswertung_Leistung!J301","v":63.7559727987841},null,null,1.4872552945776636,null,0.93735369583548767,null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.4872552945776636,1.5435105748695774,1.5899311489915455,0.93735369583548767,0.96772069093466062,0.9881991711173157,{"$f":"LINEST(TRANSPOSE(Y57:AA57),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-4.9173530849726102E-7},7.1007339546831345E-4,1.4211653081158049,1.5435105748695772,{"$f":"LINEST(TRANSPOSE(AB57:AD57),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-4.9442574582591449E-7},4.5199767473950715E-4,0.89709818581979572,0.96772069093466051,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.7559727987841,null,null,1.5435105748695774,null,0.96772069093466062,null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.7559727987841,null,null,1.5899311489915455,null,0.9881991711173157,null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"}]
[3,5.5,100,22,50,0.87,0.59,300,1,0.61,1.4262295081967213,0.96721311475409832,null,{"$f":"Auswertung_Leistung!J302","v":63.7559727987841},null,null,1.4872552945776636,null,0.93735369583548767,null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.4872552945776636,1.5435105748695774,1.5899311489915455,0.93735369583548767,0.96772069093466062,0.9881991711173157,{"$f":"LINEST(TRANSPOSE(Y58:AA58),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-4.9173530849726102E-7},7.1007339546831345E-4,1.4211653081158049,1.5435105748695772,{"$f":"LINEST(TRANSPOSE(AB58:AD58),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-4.9442574582591449E-7},4.5199767473950715E-4,0.89709818581979572,0.96772069093466051,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.7559727987841,null,null,1.5435105748695774,null,0.96772069093466062,null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.7559727987841,null,null,1.5899311489915455,null,0.9881991711173157,null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"}]
[3,5.8,100,22,60,0.99,0.59,300,1,0.61,1.6229508196721312,0.96721311475409832,null,{"$f":"Auswertung_Leistung!J303","v":63.7559727987841},null,null,1.4872552945776636,null,0.93735369583548767,null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.4872552945776636,1.5435105748695774,1.5899311489915455,0.93735369583548767,0.96772069093466062,0.9881991711173157,{"$f":"LINEST(TRANSPOSE(Y59:AA59),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-4.9173530849726102E-7},7.1007339546831345E-4,1.4211653081158049,1.5435105748695772,{"$f":"LINEST(TRANSPOSE(AB59:AD59),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-4.9442574582591449E-7},4.5199767473950715E-4,0.89709818581979572,0.96772069093466051,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.7559727987841,null,null,1.5435105748695774,null,0.96772069093466062,null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.7559727987841,null,null,1.5899311489915455,null,0.9881991711173157,null,null,{"$f":"Auswertung_Leistung!$A$290","v":"Baugröße 800"}]
[3,6.2,100,22,70,1.1200000000000001,0.57999999999999996,300,1,0.61,1.8360655737704921,0.95081967213114749,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,3,2,1,0]
[3,6.6,100,22,80,1.25,0.57999999999999996,300,1,0.61,2.0491803278688523,0.95081967213114749,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.3098985833020001E-8,-6.07620718899582E-6,5.7406363346773604E-4,-1.2212985053876601E-3,0.61172223999672903,null,"y = 0,00000002309898583302x4 - 0,00000607620718899582x3 + 0,00057406363346773600x2 - 0,00122129850538766000x + 0,61172223999672900000\nR² = 0,99999798376960600000",null,null,null,null,"R² = 0,99999798376960600000"]
[3,6.9,100,22,90,1.38,0.56999999999999995,300,1,0.61,2.262295081967213,0.93442622950819665,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,3,2,1,0,null,"y = 0,00000000219901325220x4 - 0,00000229974268309632x3 + 0,00052359233017303100x2 - 0,04991694757763310000x + 2,09643715232244000000\nR² = 0,99999052809959700000",null,null,null,null,"R² = 0,99999052809959700000"]
[3,7.3,100,22,99,1.5,0.56999999999999995,300,1,0.61,2.459016393442623,0.93442622950819665,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.1990132522000002E-9,-2.2997426830963201E-6,5.2359233017303098E-4,-4.9916947577633097E-2,2.0964371523224399]
[3,8.1,100,23,1,0.6,0.6,100,0,0.6,1,1]
[3,9.6999999999999993,100,23,50,0.78,0.54,100,1,0.6,1.3,0.90000000000000013]
[3,10.7,100,23,60,0.9,0.53,100,1,0.6,1.5,0.88333333333333341]
[3,11.7,100,23,70,1.01,0.51,100,1,0.6,1.6833333333333333,0.85000000000000009]
[3,12.6,100,23,80,1.1200000000000001,0.49,100,1,0.6,1.8666666666666669,0.81666666666666665]
[3,13.6,100,23,90,1.24,0.48,100,1,0.6,2.0666666666666669,0.8]
[3,14.5,100,23,99,1.34,0.47,100,1,0.6,2.2333333333333334,0.78333333333333333,null,{"$f":"Auswertung_Leistung!J314","v":164.02443076580053},null,null,{"$f":"IF(Q$23*$N70^R$23+Q$24*$N70^R$24+Q$25*$N70^R$25+Q$26*$N70^R$26+Q$27*$N70^R$27<1,1,Q$23*$N70^R$23+Q$24*$N70^R$24+Q$25*$N70^R$25+Q$26*$N70^R$26+Q$27*$N70^R$27)","v":1.198479954560647},null,{"$f":"IF(S$23*$N70^T$23+S$24*$N70^T$24+S$25*$N70^T$25+S$26*$N70^T$26+S$27*$N70^T$27>1,1,S$23*$N70^T$23+S$24*$N70^T$24+S$25*$N70^T$25+S$26*$N70^T$26+S$27*$N70^T$27)","v":0.89440113314833414},null,null,{"$f":"Auswertung_Leistung!A309","v":"Baugröße 1000"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.198479954560647,1.4203588067994268,1.4883967167775192,0.89440113314833414,0.93069193474908996,0.95124942607768725,{"$f":"LINEST(TRANSPOSE(Y70:AA70),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-7.6920471130343755E-6},4.5264026562981102E-3,0.8227601600611798,{"$f":"AE70*X70^2+AF70*X70+AG70","v":1.4203588067994268},{"$f":"LINEST(TRANSPOSE(AB70:AD70),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-7.8666551360793171E-7},5.9890767008994022E-4,0.84237702127541914,{"$f":"AI70*X70^2+AJ70*X70+AK70","v":0.93069193474908996},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,164.02443076580053,null,null,{"$f":"IF(EQ$23*$N70^ER$23+EQ$24*$N70^ER$24+EQ$25*$N70^ER$25+EQ$26*$N70^ER$26+EQ$27*$N70^ER$27<1,1,EQ$23*$N70^ER$23+EQ$24*$N70^ER$24+EQ$25*$N70^ER$25+EQ$26*$N70^ER$26+EQ$27*$N70^ER$27)","v":1.4203588067994268},null,{"$f":"IF(ES$23*$N70^ET$23+ES$24*$N70^ET$24+ES$25*$N70^ET$25+ES$26*$N70^ET$26+ES$27*$N70^ET$27>1,1,ES$23*$N70^ET$23+ES$24*$N70^ET$24+ES$25*$N70^ET$25+ES$26*$N70^ET$26+ES$27*$N70^ET$27)","v":0.93069193474908996},null,null,{"$f":"Auswertung_Leistung!EA309","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,164.02443076580053,null,null,{"$f":"IF(JR$23*$N70^JS$23+JR$24*$N70^JS$24+JR$25*$N70^JS$25+JR$26*$N70^JS$26+JR$27*$N70^JS$27<1,1,JR$23*$N70^JS$23+JR$24*$N70^JS$24+JR$25*$N70^JS$25+JR$26*$N70^JS$26+JR$27*$N70^JS$27)","v":1.4883967167775192},null,{"$f":"IF(JT$23*$N70^JU$23+JT$24*$N70^JU$24+JT$25*$N70^JU$25+JT$26*$N70^JU$26+JT$27*$N70^JU$27>1,1,JT$23*$N70^JU$23+JT$24*$N70^JU$24+JT$25*$N70^JU$25+JT$26*$N70^JU$26+JT$27*$N70^JU$27)","v":0.95124942607768725},null,null,{"$f":"Auswertung_Leistung!JB309","v":0}]
[3,5.7,100,23,1,0.63,0.63,200,0,0.63,1,1,null,{"$f":"Auswertung_Leistung!J315","v":154.89530616677845},null,null,{"$f":"IF(Q$23*$N71^R$23+Q$24*$N71^R$24+Q$25*$N71^R$25+Q$26*$N71^R$26+Q$27*$N71^R$27<1,1,Q$23*$N71^R$23+Q$24*$N71^R$24+Q$25*$N71^R$25+Q$26*$N71^R$26+Q$27*$N71^R$27)","v":1.2186136297276982},null,{"$f":"IF(S$23*$N71^T$23+S$24*$N71^T$24+S$25*$N71^T$25+S$26*$N71^T$26+S$27*$N71^T$27>1,1,S$23*$N71^T$23+S$24*$N71^T$24+S$25*$N71^T$25+S$26*$N71^T$26+S$27*$N71^T$27)","v":0.89617787561759632},null,null,{"$f":"#REF!","v":{"$error":"#REF!"}},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.2186136297276982,1.431542005216897,1.4967355201248755,0.89617787561759632,0.93382245854282897,0.95425912652532729,{"$f":"LINEST(TRANSPOSE(Y71:AA71),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-7.3867430290609873E-6},4.3453066636102832E-3,0.85795039365727988,{"$f":"AE71*X71^2+AF71*X71+AG71","v":1.431542005216897},{"$f":"LINEST(TRANSPOSE(AB71:AD71),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-8.6039574713674657E-7},6.345645533933548E-4,0.84132537774962801,{"$f":"AI71*X71^2+AJ71*X71+AK71","v":0.93382245854282908},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,154.89530616677845,null,null,{"$f":"IF(EQ$23*$N71^ER$23+EQ$24*$N71^ER$24+EQ$25*$N71^ER$25+EQ$26*$N71^ER$26+EQ$27*$N71^ER$27<1,1,EQ$23*$N71^ER$23+EQ$24*$N71^ER$24+EQ$25*$N71^ER$25+EQ$26*$N71^ER$26+EQ$27*$N71^ER$27)","v":1.431542005216897},null,{"$f":"IF(ES$23*$N71^ET$23+ES$24*$N71^ET$24+ES$25*$N71^ET$25+ES$26*$N71^ET$26+ES$27*$N71^ET$27>1,1,ES$23*$N71^ET$23+ES$24*$N71^ET$24+ES$25*$N71^ET$25+ES$26*$N71^ET$26+ES$27*$N71^ET$27)","v":0.93382245854282897},null,null,{"$f":"#REF!","v":{"$error":"#REF!"}},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,154.89530616677845,null,null,{"$f":"IF(JR$23*$N71^JS$23+JR$24*$N71^JS$24+JR$25*$N71^JS$25+JR$26*$N71^JS$26+JR$27*$N71^JS$27<1,1,JR$23*$N71^JS$23+JR$24*$N71^JS$24+JR$25*$N71^JS$25+JR$26*$N71^JS$26+JR$27*$N71^JS$27)","v":1.4967355201248755},null,{"$f":"IF(JT$23*$N71^JU$23+JT$24*$N71^JU$24+JT$25*$N71^JU$25+JT$26*$N71^JU$26+JT$27*$N71^JU$27>1,1,JT$23*$N71^JU$23+JT$24*$N71^JU$24+JT$25*$N71^JU$25+JT$26*$N71^JU$26+JT$27*$N71^JU$27)","v":0.95425912652532729},null,null,{"$f":"#REF!","v":{"$error":"#REF!"}}]
[3,6.9,100,23,50,0.91,0.6,200,1,0.63,1.4444444444444444,0.95238095238095233,null,{"$f":"Auswertung_Leistung!J316","v":98.926386288835431},null,null,{"$f":"IF(Q$23*$N72^R$23+Q$24*$N72^R$24+Q$25*$N72^R$25+Q$26*$N72^R$26+Q$27*$N72^R$27<1,1,Q$23*$N72^R$23+Q$24*$N72^R$24+Q$25*$N72^R$25+Q$26*$N72^R$26+Q$27*$N72^R$27)","v":1.3683249331773524},null,{"$f":"IF(S$23*$N72^T$23+S$24*$N72^T$24+S$25*$N72^T$25+S$26*$N72^T$26+S$27*$N72^T$27>1,1,S$23*$N72^T$23+S$24*$N72^T$24+S$25*$N72^T$25+S$26*$N72^T$26+S$27*$N72^T$27)","v":0.91659983129294642},null,null,{"$f":"#REF!","v":{"$error":"#REF!"}},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.3683249331773524,1.500638422150776,1.5517011208252574,0.91659983129294642,0.95423647266969269,0.97429817152133258,{"$f":"LINEST(TRANSPOSE(Y72:AA72),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-4.0625395149470943E-6},2.5418967442183619E-3,1.1547606539049873,{"$f":"AE72*X72^2+AF72*X72+AG72","v":1.500638422150776},{"$f":"LINEST(TRANSPOSE(AB72:AD72),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-8.7874712625533724E-7},6.3999055164406539E-4,0.86138824739109299,{"$f":"AI72*X72^2+AJ72*X72+AK72","v":0.95423647266969258},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,98.926386288835431,null,null,{"$f":"IF(EQ$23*$N72^ER$23+EQ$24*$N72^ER$24+EQ$25*$N72^ER$25+EQ$26*$N72^ER$26+EQ$27*$N72^ER$27<1,1,EQ$23*$N72^ER$23+EQ$24*$N72^ER$24+EQ$25*$N72^ER$25+EQ$26*$N72^ER$26+EQ$27*$N72^ER$27)","v":1.500638422150776},null,{"$f":"IF(ES$23*$N72^ET$23+ES$24*$N72^ET$24+ES$25*$N72^ET$25+ES$26*$N72^ET$26+ES$27*$N72^ET$27>1,1,ES$23*$N72^ET$23+ES$24*$N72^ET$24+ES$25*$N72^ET$25+ES$26*$N72^ET$26+ES$27*$N72^ET$27)","v":0.95423647266969269},null,null,{"$f":"#REF!","v":{"$error":"#REF!"}},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,98.926386288835431,null,null,{"$f":"IF(JR$23*$N72^JS$23+JR$24*$N72^JS$24+JR$25*$N72^JS$25+JR$26*$N72^JS$26+JR$27*$N72^JS$27<1,1,JR$23*$N72^JS$23+JR$24*$N72^JS$24+JR$25*$N72^JS$25+JR$26*$N72^JS$26+JR$27*$N72^JS$27)","v":1.5517011208252574},null,{"$f":"IF(JT$23*$N72^JU$23+JT$24*$N72^JU$24+JT$25*$N72^JU$25+JT$26*$N72^JU$26+JT$27*$N72^JU$27>1,1,JT$23*$N72^JU$23+JT$24*$N72^JU$24+JT$25*$N72^JU$25+JT$26*$N72^JU$26+JT$27*$N72^JU$27)","v":0.97429817152133258},null,null,{"$f":"#REF!","v":{"$error":"#REF!"}}]
[3,7.4,100,23,60,1.04,0.6,200,1,0.63,1.6507936507936509,0.95238095238095233,null,{"$f":"Auswertung_Leistung!J317","v":81.627063125975369},null,null,{"$f":"IF(Q$23*$N73^R$23+Q$24*$N73^R$24+Q$25*$N73^R$25+Q$26*$N73^R$26+Q$27*$N73^R$27<1,1,Q$23*$N73^R$23+Q$24*$N73^R$24+Q$25*$N73^R$25+Q$26*$N73^R$26+Q$27*$N73^R$27)","v":1.4243039556453481},null,{"$f":"IF(S$23*$N73^T$23+S$24*$N73^T$24+S$25*$N73^T$25+S$26*$N73^T$26+S$27*$N73^T$27>1,1,S$23*$N73^T$23+S$24*$N73^T$24+S$25*$N73^T$25+S$26*$N73^T$26+S$27*$N73^T$27)","v":0.92607670336274373},null,null,{"$f":"#REF!","v":{"$error":"#REF!"}},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.4243039556453481,1.5218505309956356,1.5701276261228143,0.92607670336274373,0.96083516452126305,0.98101564165635269,{"$f":"LINEST(TRANSPOSE(Y73:AA73),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-2.4634740111554738E-6},1.714507956849524E-3,1.2774879000719497,{"$f":"AE73*X73^2+AF73*X73+AG73","v":1.5218505309956356},{"$f":"LINEST(TRANSPOSE(AB73:AD73),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-7.2889920117149123E-7},5.6625437193664194E-4,0.87674025818079415,{"$f":"AI73*X73^2+AJ73*X73+AK73","v":0.96083516452126294},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,81.627063125975369,null,null,{"$f":"IF(EQ$23*$N73^ER$23+EQ$24*$N73^ER$24+EQ$25*$N73^ER$25+EQ$26*$N73^ER$26+EQ$27*$N73^ER$27<1,1,EQ$23*$N73^ER$23+EQ$24*$N73^ER$24+EQ$25*$N73^ER$25+EQ$26*$N73^ER$26+EQ$27*$N73^ER$27)","v":1.5218505309956356},null,{"$f":"IF(ES$23*$N73^ET$23+ES$24*$N73^ET$24+ES$25*$N73^ET$25+ES$26*$N73^ET$26+ES$27*$N73^ET$27>1,1,ES$23*$N73^ET$23+ES$24*$N73^ET$24+ES$25*$N73^ET$25+ES$26*$N73^ET$26+ES$27*$N73^ET$27)","v":0.96083516452126305},null,null,{"$f":"#REF!","v":{"$error":"#REF!"}},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,81.627063125975369,null,null,{"$f":"IF(JR$23*$N73^JS$23+JR$24*$N73^JS$24+JR$25*$N73^JS$25+JR$26*$N73^JS$26+JR$27*$N73^JS$27<1,1,JR$23*$N73^JS$23+JR$24*$N73^JS$24+JR$25*$N73^JS$25+JR$26*$N73^JS$26+JR$27*$N73^JS$27)","v":1.5701276261228143},null,{"$f":"IF(JT$23*$N73^JU$23+JT$24*$N73^JU$24+JT$25*$N73^JU$25+JT$26*$N73^JU$26+JT$27*$N73^JU$27>1,1,JT$23*$N73^JU$23+JT$24*$N73^JU$24+JT$25*$N73^JU$25+JT$26*$N73^JU$26+JT$27*$N73^JU$27)","v":0.98101564165635269},null,null,{"$f":"#REF!","v":{"$error":"#REF!"}}]
[3,8,100,23,70,1.17,0.59,200,1,0.63,1.857142857142857,0.9365079365079364,null,{"$f":"Auswertung_Leistung!J318","v":86.350933922726639},null,null,{"$f":"IF(Q$23*$N74^R$23+Q$24*$N74^R$24+Q$25*$N74^R$25+Q$26*$N74^R$26+Q$27*$N74^R$27<1,1,Q$23*$N74^R$23+Q$24*$N74^R$24+Q$25*$N74^R$25+Q$26*$N74^R$26+Q$27*$N74^R$27)","v":1.408541085846214},null,{"$f":"IF(S$23*$N74^T$23+S$24*$N74^T$24+S$25*$N74^T$25+S$26*$N74^T$26+S$27*$N74^T$27>1,1,S$23*$N74^T$23+S$24*$N74^T$24+S$25*$N74^T$25+S$26*$N74^T$26+S$27*$N74^T$27)","v":0.92334642112330967},null,null,{"$f":"#REF!","v":{"$error":"#REF!"}},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.408541085846214,1.5160778851913601,1.5650246682586422,0.92334642112330967,0.95902503721811327,0.97915789256715047,{"$f":"LINEST(TRANSPOSE(Y74:AA74),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-2.9295008138931805E-6},1.9542182376194122E-3,1.2424142702232046,{"$f":"AE74*X74^2+AF74*X74+AG74","v":1.5160778851913599},{"$f":"LINEST(TRANSPOSE(AB74:AD74),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-7.7728803728833919E-7},5.8997257213453996E-4,0.87212204428273898,{"$f":"AI74*X74^2+AJ74*X74+AK74","v":0.95902503721811339},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,86.350933922726639,null,null,{"$f":"IF(EQ$23*$N74^ER$23+EQ$24*$N74^ER$24+EQ$25*$N74^ER$25+EQ$26*$N74^ER$26+EQ$27*$N74^ER$27<1,1,EQ$23*$N74^ER$23+EQ$24*$N74^ER$24+EQ$25*$N74^ER$25+EQ$26*$N74^ER$26+EQ$27*$N74^ER$27)","v":1.5160778851913601},null,{"$f":"IF(ES$23*$N74^ET$23+ES$24*$N74^ET$24+ES$25*$N74^ET$25+ES$26*$N74^ET$26+ES$27*$N74^ET$27>1,1,ES$23*$N74^ET$23+ES$24*$N74^ET$24+ES$25*$N74^ET$25+ES$26*$N74^ET$26+ES$27*$N74^ET$27)","v":0.95902503721811327},null,null,{"$f":"#REF!","v":{"$error":"#REF!"}},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,86.350933922726639,null,null,{"$f":"IF(JR$23*$N74^JS$23+JR$24*$N74^JS$24+JR$25*$N74^JS$25+JR$26*$N74^JS$26+JR$27*$N74^JS$27<1,1,JR$23*$N74^JS$23+JR$24*$N74^JS$24+JR$25*$N74^JS$25+JR$26*$N74^JS$26+JR$27*$N74^JS$27)","v":1.5650246682586422},null,{"$f":"IF(JT$23*$N74^JU$23+JT$24*$N74^JU$24+JT$25*$N74^JU$25+JT$26*$N74^JU$26+JT$27*$N74^JU$27>1,1,JT$23*$N74^JU$23+JT$24*$N74^JU$24+JT$25*$N74^JU$25+JT$26*$N74^JU$26+JT$27*$N74^JU$27)","v":0.97915789256715047},null,null,{"$f":"#REF!","v":{"$error":"#REF!"}}]
[3,8.6,100,23,80,1.3,0.57999999999999996,200,1,0.63,2.0634920634920637,0.92063492063492058,null,{"$f":"Auswertung_Leistung!J319","v":79.802348196225324},null,null,1.430489918732885,null,0.92715967180035075,null,null,{"$f":"#REF!","v":{"$error":"#REF!"}},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.430489918732885,1.5240756803566906,1.5721133337069699,0.92715967180035075,0.96153573290491057,0.98173789517765542,{"$f":"LINEST(TRANSPOSE(Y75:AA75),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-2.2774054136763626E-6},1.6190792403409711E-3,1.2913560488355509,1.5240756803566906,{"$f":"LINEST(TRANSPOSE(AB75:AD75),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-7.0869494159075122E-7},5.5636909352282525E-4,0.87860971186397552,0.96153573290491057,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,79.802348196225324,null,null,1.5240756803566906,null,0.96153573290491057,null,null,{"$f":"#REF!","v":{"$error":"#REF!"}},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,79.802348196225324,null,null,1.5721133337069699,null,0.98173789517765542,null,null,{"$f":"#REF!","v":{"$error":"#REF!"}}]
[3,9.1999999999999993,100,23,90,1.44,0.57999999999999996,200,1,0.63,2.2857142857142856,0.92063492063492058,null,{"$f":"Auswertung_Leistung!J320","v":63.7559727987841},null,null,1.4872552945776636,null,0.93735369583548767,null,null,{"$f":"#REF!","v":{"$error":"#REF!"}},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.4872552945776636,1.5435105748695774,1.5899311489915455,0.93735369583548767,0.96772069093466062,0.9881991711173157,{"$f":"LINEST(TRANSPOSE(Y76:AA76),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-4.9173530849726102E-7},7.1007339546831345E-4,1.4211653081158049,1.5435105748695772,{"$f":"LINEST(TRANSPOSE(AB76:AD76),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-4.9442574582591449E-7},4.5199767473950715E-4,0.89709818581979572,0.96772069093466051,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.7559727987841,null,null,1.5435105748695774,null,0.96772069093466062,null,null,{"$f":"#REF!","v":{"$error":"#REF!"}},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.7559727987841,null,null,1.5899311489915455,null,0.9881991711173157,null,null,{"$f":"#REF!","v":{"$error":"#REF!"}}]
[3,9.6999999999999993,100,23,99,1.56,0.56999999999999995,200,1,0.63,2.4761904761904763,0.90476190476190466,null,{"$f":"Auswertung_Leistung!J321","v":63.7559727987841},null,null,1.4872552945776636,null,0.93735369583548767,null,null,{"$f":"#REF!","v":{"$error":"#REF!"}},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.4872552945776636,1.5435105748695774,1.5899311489915455,0.93735369583548767,0.96772069093466062,0.9881991711173157,{"$f":"LINEST(TRANSPOSE(Y77:AA77),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-4.9173530849726102E-7},7.1007339546831345E-4,1.4211653081158049,1.5435105748695772,{"$f":"LINEST(TRANSPOSE(AB77:AD77),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-4.9442574582591449E-7},4.5199767473950715E-4,0.89709818581979572,0.96772069093466051,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.7559727987841,null,null,1.5435105748695774,null,0.96772069093466062,null,null,{"$f":"#REF!","v":{"$error":"#REF!"}},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.7559727987841,null,null,1.5899311489915455,null,0.9881991711173157,null,null,{"$f":"#REF!","v":{"$error":"#REF!"}}]
[3,4.8,100,23,1,0.64,0.64,300,0,0.64,1,1,null,{"$f":"Auswertung_Leistung!J322","v":63.7559727987841},null,null,1.4872552945776636,null,0.93735369583548767,null,null,{"$f":"#REF!","v":{"$error":"#REF!"}},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.4872552945776636,1.5435105748695774,1.5899311489915455,0.93735369583548767,0.96772069093466062,0.9881991711173157,{"$f":"LINEST(TRANSPOSE(Y78:AA78),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-4.9173530849726102E-7},7.1007339546831345E-4,1.4211653081158049,1.5435105748695772,{"$f":"LINEST(TRANSPOSE(AB78:AD78),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-4.9442574582591449E-7},4.5199767473950715E-4,0.89709818581979572,0.96772069093466051,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.7559727987841,null,null,1.5435105748695774,null,0.96772069093466062,null,null,{"$f":"#REF!","v":{"$error":"#REF!"}},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.7559727987841,null,null,1.5899311489915455,null,0.9881991711173157,null,null,{"$f":"#REF!","v":{"$error":"#REF!"}}]
[3,5.7,100,23,50,0.94,0.62,300,1,0.64,1.4687499999999998,0.96875]
[3,6.1,100,23,60,1.07,0.61,300,1,0.64,1.671875,0.953125]
[3,6.5,100,23,70,1.21,0.61,300,1,0.64,1.890625,0.953125]
[3,6.8,100,23,80,1.35,0.6,300,1,0.64,2.109375,0.9375]
[3,7.2,100,23,90,1.48,0.6,300,1,0.64,2.3125,0.9375]
[3,7.6,100,23,99,1.61,0.59,300,1,0.64,2.515625,0.92187499999999989]
[3,8.3000000000000007,100,24,1,0.62,0.62,100,0,0.62,1,1]
[3,10.199999999999999,100,24,50,0.84,0.56000000000000005,100,{"$f":"IF(F86<>G86,1,0)","v":1},0.62,{"$f":"F86/J86","v":1.3548387096774193},0.90322580645161299]
[3,11.2,100,24,60,0.96,0.55000000000000004,100,1,0.62,1.5483870967741935,{"$f":"G87/J87","v":0.88709677419354849}]
[3,12.3,100,24,70,1.08,0.53,100,1,0.62,1.741935483870968,0.85483870967741937]
[3,13.3,100,24,80,1.21,0.51,100,1,{"$f":"IF(F89/G89=1,F89,J88)","v":0.62},1.9516129032258065,0.82258064516129037,null,{"$f":"Auswertung_Leistung!J333","v":164.02443076580053},null,null,{"$f":"IF(Q$23*$N89^R$23+Q$24*$N89^R$24+Q$25*$N89^R$25+Q$26*$N89^R$26+Q$27*$N89^R$27<1,1,Q$23*$N89^R$23+Q$24*$N89^R$24+Q$25*$N89^R$25+Q$26*$N89^R$26+Q$27*$N89^R$27)","v":1.198479954560647},null,{"$f":"IF(S$23*$N89^T$23+S$24*$N89^T$24+S$25*$N89^T$25+S$26*$N89^T$26+S$27*$N89^T$27>1,1,S$23*$N89^T$23+S$24*$N89^T$24+S$25*$N89^T$25+S$26*$N89^T$26+S$27*$N89^T$27)","v":0.89440113314833414},null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.198479954560647,1.4203588067994268,1.4883967167775192,0.89440113314833414,0.93069193474908996,0.95124942607768725,{"$f":"LINEST(TRANSPOSE(Y89:AA89),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-7.6920471130343755E-6},4.5264026562981102E-3,0.8227601600611798,{"$f":"AE89*X89^2+AF89*X89+AG89","v":1.4203588067994268},{"$f":"LINEST(TRANSPOSE(AB89:AD89),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-7.8666551360793171E-7},5.9890767008994022E-4,0.84237702127541914,{"$f":"AI89*X89^2+AJ89*X89+AK89","v":0.93069193474908996},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,164.02443076580053,null,null,{"$f":"IF(EQ$23*$N89^ER$23+EQ$24*$N89^ER$24+EQ$25*$N89^ER$25+EQ$26*$N89^ER$26+EQ$27*$N89^ER$27<1,1,EQ$23*$N89^ER$23+EQ$24*$N89^ER$24+EQ$25*$N89^ER$25+EQ$26*$N89^ER$26+EQ$27*$N89^ER$27)","v":1.4203588067994268},null,{"$f":"IF(ES$23*$N89^ET$23+ES$24*$N89^ET$24+ES$25*$N89^ET$25+ES$26*$N89^ET$26+ES$27*$N89^ET$27>1,1,ES$23*$N89^ET$23+ES$24*$N89^ET$24+ES$25*$N89^ET$25+ES$26*$N89^ET$26+ES$27*$N89^ET$27)","v":0.93069193474908996},null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,164.02443076580053,null,null,{"$f":"IF(JR$23*$N89^JS$23+JR$24*$N89^JS$24+JR$25*$N89^JS$25+JR$26*$N89^JS$26+JR$27*$N89^JS$27<1,1,JR$23*$N89^JS$23+JR$24*$N89^JS$24+JR$25*$N89^JS$25+JR$26*$N89^JS$26+JR$27*$N89^JS$27)","v":1.4883967167775192},null,{"$f":"IF(JT$23*$N89^JU$23+JT$24*$N89^JU$24+JT$25*$N89^JU$25+JT$26*$N89^JU$26+JT$27*$N89^JU$27>1,1,JT$23*$N89^JU$23+JT$24*$N89^JU$24+JT$25*$N89^JU$25+JT$26*$N89^JU$26+JT$27*$N89^JU$27)","v":0.95124942607768725},null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"}]
[3,14.4,100,24,90,1.33,0.5,100,1,0.62,2.145161290322581,0.80645161290322587,null,{"$f":"Auswertung_Leistung!J334","v":154.89530616677845},null,null,{"$f":"IF(Q$23*$N90^R$23+Q$24*$N90^R$24+Q$25*$N90^R$25+Q$26*$N90^R$26+Q$27*$N90^R$27<1,1,Q$23*$N90^R$23+Q$24*$N90^R$24+Q$25*$N90^R$25+Q$26*$N90^R$26+Q$27*$N90^R$27)","v":1.2186136297276982},null,{"$f":"IF(S$23*$N90^T$23+S$24*$N90^T$24+S$25*$N90^T$25+S$26*$N90^T$26+S$27*$N90^T$27>1,1,S$23*$N90^T$23+S$24*$N90^T$24+S$25*$N90^T$25+S$26*$N90^T$26+S$27*$N90^T$27)","v":0.89617787561759632},null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.2186136297276982,1.431542005216897,1.4967355201248755,0.89617787561759632,0.93382245854282897,0.95425912652532729,{"$f":"LINEST(TRANSPOSE(Y90:AA90),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-7.3867430290609873E-6},4.3453066636102832E-3,0.85795039365727988,{"$f":"AE90*X90^2+AF90*X90+AG90","v":1.431542005216897},{"$f":"LINEST(TRANSPOSE(AB90:AD90),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-8.6039574713674657E-7},6.345645533933548E-4,0.84132537774962801,{"$f":"AI90*X90^2+AJ90*X90+AK90","v":0.93382245854282908},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,154.89530616677845,null,null,{"$f":"IF(EQ$23*$N90^ER$23+EQ$24*$N90^ER$24+EQ$25*$N90^ER$25+EQ$26*$N90^ER$26+EQ$27*$N90^ER$27<1,1,EQ$23*$N90^ER$23+EQ$24*$N90^ER$24+EQ$25*$N90^ER$25+EQ$26*$N90^ER$26+EQ$27*$N90^ER$27)","v":1.431542005216897},null,{"$f":"IF(ES$23*$N90^ET$23+ES$24*$N90^ET$24+ES$25*$N90^ET$25+ES$26*$N90^ET$26+ES$27*$N90^ET$27>1,1,ES$23*$N90^ET$23+ES$24*$N90^ET$24+ES$25*$N90^ET$25+ES$26*$N90^ET$26+ES$27*$N90^ET$27)","v":0.93382245854282897},null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,154.89530616677845,null,null,{"$f":"IF(JR$23*$N90^JS$23+JR$24*$N90^JS$24+JR$25*$N90^JS$25+JR$26*$N90^JS$26+JR$27*$N90^JS$27<1,1,JR$23*$N90^JS$23+JR$24*$N90^JS$24+JR$25*$N90^JS$25+JR$26*$N90^JS$26+JR$27*$N90^JS$27)","v":1.4967355201248755},null,{"$f":"IF(JT$23*$N90^JU$23+JT$24*$N90^JU$24+JT$25*$N90^JU$25+JT$26*$N90^JU$26+JT$27*$N90^JU$27>1,1,JT$23*$N90^JU$23+JT$24*$N90^JU$24+JT$25*$N90^JU$25+JT$26*$N90^JU$26+JT$27*$N90^JU$27)","v":0.95425912652532729},null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"}]
[3,15.3,100,24,99,1.43,0.48,100,1,0.62,2.3064516129032255,0.77419354838709675,null,{"$f":"Auswertung_Leistung!J335","v":98.926386288835431},null,null,{"$f":"IF(Q$23*$N91^R$23+Q$24*$N91^R$24+Q$25*$N91^R$25+Q$26*$N91^R$26+Q$27*$N91^R$27<1,1,Q$23*$N91^R$23+Q$24*$N91^R$24+Q$25*$N91^R$25+Q$26*$N91^R$26+Q$27*$N91^R$27)","v":1.3683249331773524},null,{"$f":"IF(S$23*$N91^T$23+S$24*$N91^T$24+S$25*$N91^T$25+S$26*$N91^T$26+S$27*$N91^T$27>1,1,S$23*$N91^T$23+S$24*$N91^T$24+S$25*$N91^T$25+S$26*$N91^T$26+S$27*$N91^T$27)","v":0.91659983129294642},null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.3683249331773524,1.500638422150776,1.5517011208252574,0.91659983129294642,0.95423647266969269,0.97429817152133258,{"$f":"LINEST(TRANSPOSE(Y91:AA91),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-4.0625395149470943E-6},2.5418967442183619E-3,1.1547606539049873,{"$f":"AE91*X91^2+AF91*X91+AG91","v":1.500638422150776},{"$f":"LINEST(TRANSPOSE(AB91:AD91),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-8.7874712625533724E-7},6.3999055164406539E-4,0.86138824739109299,{"$f":"AI91*X91^2+AJ91*X91+AK91","v":0.95423647266969258},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,98.926386288835431,null,null,{"$f":"IF(EQ$23*$N91^ER$23+EQ$24*$N91^ER$24+EQ$25*$N91^ER$25+EQ$26*$N91^ER$26+EQ$27*$N91^ER$27<1,1,EQ$23*$N91^ER$23+EQ$24*$N91^ER$24+EQ$25*$N91^ER$25+EQ$26*$N91^ER$26+EQ$27*$N91^ER$27)","v":1.500638422150776},null,{"$f":"IF(ES$23*$N91^ET$23+ES$24*$N91^ET$24+ES$25*$N91^ET$25+ES$26*$N91^ET$26+ES$27*$N91^ET$27>1,1,ES$23*$N91^ET$23+ES$24*$N91^ET$24+ES$25*$N91^ET$25+ES$26*$N91^ET$26+ES$27*$N91^ET$27)","v":0.95423647266969269},null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,98.926386288835431,null,null,{"$f":"IF(JR$23*$N91^JS$23+JR$24*$N91^JS$24+JR$25*$N91^JS$25+JR$26*$N91^JS$26+JR$27*$N91^JS$27<1,1,JR$23*$N91^JS$23+JR$24*$N91^JS$24+JR$25*$N91^JS$25+JR$26*$N91^JS$26+JR$27*$N91^JS$27)","v":1.5517011208252574},null,{"$f":"IF(JT$23*$N91^JU$23+JT$24*$N91^JU$24+JT$25*$N91^JU$25+JT$26*$N91^JU$26+JT$27*$N91^JU$27>1,1,JT$23*$N91^JU$23+JT$24*$N91^JU$24+JT$25*$N91^JU$25+JT$26*$N91^JU$26+JT$27*$N91^JU$27)","v":0.97429817152133258},null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"}]
[3,5.8,100,24,1,0.66,0.66,200,0,0.66,1,1,null,{"$f":"Auswertung_Leistung!J336","v":81.627063125975369},null,null,{"$f":"IF(Q$23*$N92^R$23+Q$24*$N92^R$24+Q$25*$N92^R$25+Q$26*$N92^R$26+Q$27*$N92^R$27<1,1,Q$23*$N92^R$23+Q$24*$N92^R$24+Q$25*$N92^R$25+Q$26*$N92^R$26+Q$27*$N92^R$27)","v":1.4243039556453481},null,{"$f":"IF(S$23*$N92^T$23+S$24*$N92^T$24+S$25*$N92^T$25+S$26*$N92^T$26+S$27*$N92^T$27>1,1,S$23*$N92^T$23+S$24*$N92^T$24+S$25*$N92^T$25+S$26*$N92^T$26+S$27*$N92^T$27)","v":0.92607670336274373},null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.4243039556453481,1.5218505309956356,1.5701276261228143,0.92607670336274373,0.96083516452126305,0.98101564165635269,{"$f":"LINEST(TRANSPOSE(Y92:AA92),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-2.4634740111554738E-6},1.714507956849524E-3,1.2774879000719497,{"$f":"AE92*X92^2+AF92*X92+AG92","v":1.5218505309956356},{"$f":"LINEST(TRANSPOSE(AB92:AD92),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-7.2889920117149123E-7},5.6625437193664194E-4,0.87674025818079415,{"$f":"AI92*X92^2+AJ92*X92+AK92","v":0.96083516452126294},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,81.627063125975369,null,null,{"$f":"IF(EQ$23*$N92^ER$23+EQ$24*$N92^ER$24+EQ$25*$N92^ER$25+EQ$26*$N92^ER$26+EQ$27*$N92^ER$27<1,1,EQ$23*$N92^ER$23+EQ$24*$N92^ER$24+EQ$25*$N92^ER$25+EQ$26*$N92^ER$26+EQ$27*$N92^ER$27)","v":1.5218505309956356},null,{"$f":"IF(ES$23*$N92^ET$23+ES$24*$N92^ET$24+ES$25*$N92^ET$25+ES$26*$N92^ET$26+ES$27*$N92^ET$27>1,1,ES$23*$N92^ET$23+ES$24*$N92^ET$24+ES$25*$N92^ET$25+ES$26*$N92^ET$26+ES$27*$N92^ET$27)","v":0.96083516452126305},null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,81.627063125975369,null,null,{"$f":"IF(JR$23*$N92^JS$23+JR$24*$N92^JS$24+JR$25*$N92^JS$25+JR$26*$N92^JS$26+JR$27*$N92^JS$27<1,1,JR$23*$N92^JS$23+JR$24*$N92^JS$24+JR$25*$N92^JS$25+JR$26*$N92^JS$26+JR$27*$N92^JS$27)","v":1.5701276261228143},null,{"$f":"IF(JT$23*$N92^JU$23+JT$24*$N92^JU$24+JT$25*$N92^JU$25+JT$26*$N92^JU$26+JT$27*$N92^JU$27>1,1,JT$23*$N92^JU$23+JT$24*$N92^JU$24+JT$25*$N92^JU$25+JT$26*$N92^JU$26+JT$27*$N92^JU$27)","v":0.98101564165635269},null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"}]
[3,7.2,100,24,50,0.98,0.63,200,1,0.66,1.4848484848484849,0.95454545454545447,null,{"$f":"Auswertung_Leistung!J337","v":86.350933922726639},null,null,{"$f":"IF(Q$23*$N93^R$23+Q$24*$N93^R$24+Q$25*$N93^R$25+Q$26*$N93^R$26+Q$27*$N93^R$27<1,1,Q$23*$N93^R$23+Q$24*$N93^R$24+Q$25*$N93^R$25+Q$26*$N93^R$26+Q$27*$N93^R$27)","v":1.408541085846214},null,{"$f":"IF(S$23*$N93^T$23+S$24*$N93^T$24+S$25*$N93^T$25+S$26*$N93^T$26+S$27*$N93^T$27>1,1,S$23*$N93^T$23+S$24*$N93^T$24+S$25*$N93^T$25+S$26*$N93^T$26+S$27*$N93^T$27)","v":0.92334642112330967},null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.408541085846214,1.5160778851913601,1.5650246682586422,0.92334642112330967,0.95902503721811327,0.97915789256715047,{"$f":"LINEST(TRANSPOSE(Y93:AA93),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-2.9295008138931805E-6},1.9542182376194122E-3,1.2424142702232046,{"$f":"AE93*X93^2+AF93*X93+AG93","v":1.5160778851913599},{"$f":"LINEST(TRANSPOSE(AB93:AD93),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-7.7728803728833919E-7},5.8997257213453996E-4,0.87212204428273898,{"$f":"AI93*X93^2+AJ93*X93+AK93","v":0.95902503721811339},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,86.350933922726639,null,null,{"$f":"IF(EQ$23*$N93^ER$23+EQ$24*$N93^ER$24+EQ$25*$N93^ER$25+EQ$26*$N93^ER$26+EQ$27*$N93^ER$27<1,1,EQ$23*$N93^ER$23+EQ$24*$N93^ER$24+EQ$25*$N93^ER$25+EQ$26*$N93^ER$26+EQ$27*$N93^ER$27)","v":1.5160778851913601},null,{"$f":"IF(ES$23*$N93^ET$23+ES$24*$N93^ET$24+ES$25*$N93^ET$25+ES$26*$N93^ET$26+ES$27*$N93^ET$27>1,1,ES$23*$N93^ET$23+ES$24*$N93^ET$24+ES$25*$N93^ET$25+ES$26*$N93^ET$26+ES$27*$N93^ET$27)","v":0.95902503721811327},null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,86.350933922726639,null,null,{"$f":"IF(JR$23*$N93^JS$23+JR$24*$N93^JS$24+JR$25*$N93^JS$25+JR$26*$N93^JS$26+JR$27*$N93^JS$27<1,1,JR$23*$N93^JS$23+JR$24*$N93^JS$24+JR$25*$N93^JS$25+JR$26*$N93^JS$26+JR$27*$N93^JS$27)","v":1.5650246682586422},null,{"$f":"IF(JT$23*$N93^JU$23+JT$24*$N93^JU$24+JT$25*$N93^JU$25+JT$26*$N93^JU$26+JT$27*$N93^JU$27>1,1,JT$23*$N93^JU$23+JT$24*$N93^JU$24+JT$25*$N93^JU$25+JT$26*$N93^JU$26+JT$27*$N93^JU$27)","v":0.97915789256715047},null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"}]
[3,7.8,100,24,60,1.1200000000000001,0.62,200,1,0.66,1.696969696969697,0.93939393939393934,null,{"$f":"Auswertung_Leistung!J338","v":79.802348196225324},null,null,1.430489918732885,null,0.92715967180035075,null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.430489918732885,1.5240756803566906,1.5721133337069699,0.92715967180035075,0.96153573290491057,0.98173789517765542,{"$f":"LINEST(TRANSPOSE(Y94:AA94),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-2.2774054136763626E-6},1.6190792403409711E-3,1.2913560488355509,1.5240756803566906,{"$f":"LINEST(TRANSPOSE(AB94:AD94),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-7.0869494159075122E-7},5.5636909352282525E-4,0.87860971186397552,0.96153573290491057,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,79.802348196225324,null,null,1.5240756803566906,null,0.96153573290491057,null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,79.802348196225324,null,null,1.5721133337069699,null,0.98173789517765542,null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"}]
[3,8.4,100,24,70,1.26,0.62,200,1,0.66,1.9090909090909089,0.93939393939393934,null,{"$f":"Auswertung_Leistung!J339","v":63.7559727987841},null,null,1.4872552945776636,null,0.93735369583548767,null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.4872552945776636,1.5435105748695774,1.5899311489915455,0.93735369583548767,0.96772069093466062,0.9881991711173157,{"$f":"LINEST(TRANSPOSE(Y95:AA95),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-4.9173530849726102E-7},7.1007339546831345E-4,1.4211653081158049,1.5435105748695772,{"$f":"LINEST(TRANSPOSE(AB95:AD95),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-4.9442574582591449E-7},4.5199767473950715E-4,0.89709818581979572,0.96772069093466051,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.7559727987841,null,null,1.5435105748695774,null,0.96772069093466062,null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.7559727987841,null,null,1.5899311489915455,null,0.9881991711173157,null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"}]
[3,9,100,24,80,1.4,0.61,200,1,0.66,2.1212121212121211,0.9242424242424242,null,{"$f":"Auswertung_Leistung!J340","v":63.7559727987841},null,null,1.4872552945776636,null,0.93735369583548767,null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},1.4872552945776636,1.5435105748695774,1.5899311489915455,0.93735369583548767,0.96772069093466062,0.9881991711173157,{"$f":"LINEST(TRANSPOSE(Y96:AA96),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-4.9173530849726102E-7},7.1007339546831345E-4,1.4211653081158049,1.5435105748695772,{"$f":"LINEST(TRANSPOSE(AB96:AD96),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-4.9442574582591449E-7},4.5199767473950715E-4,0.89709818581979572,0.96772069093466051,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.7559727987841,null,null,1.5435105748695774,null,0.96772069093466062,null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.7559727987841,null,null,1.5899311489915455,null,0.9881991711173157,null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"}]
[3,9.6,100,24,90,1.54,0.6,200,1,0.66,2.3333333333333335,0.90909090909090906,null,{"$f":"Auswertung_Leistung!J341","v":63.7559727987841},null,null,1.4872552945776636,null,0.93735369583548767,null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"},null,{"$f":"Auswertung_Leistung!$B$3","v":200},{"$f":"Q97","v":1.4872552945776636},{"$f":"EQ97","v":1.5435105748695774},{"$f":"JR97","v":1.5899311489915455},{"$f":"S97","v":0.93735369583548767},{"$f":"ES97","v":0.96772069093466062},{"$f":"JT97","v":0.9881991711173157},{"$f":"LINEST(TRANSPOSE(Y97:AA97),TRANSPOSE($Y$31:$AA$31)^{0,1,2},0,0)","v":-4.9173530849726102E-7},7.1007339546831345E-4,1.4211653081158049,1.5435105748695772,{"$f":"LINEST(TRANSPOSE(AB97:AD97),TRANSPOSE($AB$31:$AD$31)^{0,1,2},0,0)","v":-4.9442574582591449E-7},4.5199767473950715E-4,0.89709818581979572,0.96772069093466051,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"$N97","v":63.7559727987841},null,null,1.5435105748695774,null,0.96772069093466062,null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"$N97","v":63.7559727987841},null,null,1.5899311489915455,null,0.9881991711173157,null,null,{"$f":"Auswertung_Leistung!$A$328","v":"Baugröße 1200"}]
[3,10.1,100,24,99,1.66,0.59,200,1,0.66,2.5151515151515147,0.89393939393939381]
[3,4.9000000000000004,100,24,1,0.67,0.67,300,0,0.67,1,1]
[3,5.9,100,24,50,1.01,0.65,300,1,0.67,1.5074626865671641,0.97014925373134331]
[3,6.3,100,24,60,1.1499999999999999,0.64,300,1,0.67,1.716417910447761,0.95522388059701491]
[3,6.7,100,24,70,1.3,0.64,300,1,0.67,1.9402985074626866,0.95522388059701491]
[3,7.1,100,24,80,1.44,0.63,300,1,0.67,2.1492537313432836,0.94029850746268651]
[3,7.5,100,24,90,1.59,0.63,300,1,0.67,2.3731343283582089,0.94029850746268651]
[3,7.9,100,24,99,1.72,0.62,300,1,0.67,2.5671641791044775,0.9253731343283581]
[3,8.6,100,25,1,0.65,0.65,100,0,0.65,1,1]
[3,10.7,100,25,50,0.9,0.59,100,1,0.65,1.3846153846153846,0.90769230769230758,null,{"$f":"CONCATENATE(E5,E6,B11, \" % relFeuchte; \",E8)","v":"6 °C Vorlauf; 100 kg/h Kühlwasser; 50 % relFeuchte; 26 °C Ansaugtemp; "}]
[3,11.8,100,25,60,1.03,0.56999999999999995,100,1,0.65,1.5846153846153845,0.87692307692307681]
[3,12.9,100,25,70,1.1599999999999999,0.55000000000000004,100,1,0.65,1.7846153846153845,0.84615384615384615,null,"BG800"]
[3,14,100,25,80,1.29,0.53,100,1,0.65,1.9846153846153847,0.81538461538461537,null,{"$f":"CONCATENATE(N109,\"; \",E5,B11, \" % relFeuchte; \",E8)","v":"BG800; 6 °C Vorlauf; 50 % relFeuchte; 26 °C Ansaugtemp; "}]
[3,15.1,100,25,90,1.42,0.52,100,1,0.65,2.1846153846153844,0.8]
[3,16.100000000000001,100,25,99,1.53,0.5,100,1,0.65,2.3538461538461539,0.76923076923076916]
[3,6,100,25,1,0.69,0.69,200,0,0.69,1,1]
[3,7.5,100,25,50,1.05,0.66,200,1,0.69,1.5217391304347827,0.95652173913043492,null,null,"Ansaugtemperatur:","Kühlwasservorlauf1):","Kühlwasservorlauf \nkondensierender Betrieb2):","relative Feuchte:","Nennkühlwassermenge wOK:","Ist-Kühlwassermenge wK:"]
[3,8.1,100,25,60,1.2,0.65,200,1,0.69,1.7391304347826089,0.94202898550724645,null,"Minimal",{"$f":"MIN(D$22:D$10221)","v":21},null,{"$f":"MIN(A$22:A$10221)","v":3},1]
[3,8.8000000000000007,100,25,70,1.34,0.64,200,1,0.69,1.9420289855072466,0.92753623188405809,null,"Maximal",{"$f":"MAX(D$22:D$10221)","v":27},null,{"$f":"MAX(A$22:A$10221)","v":16},99]
[3,9.4,100,25,80,1.49,0.63,200,1,0.69,2.1594202898550727,0.91304347826086962]
[3,10,100,25,90,1.64,0.63,200,1,0.69,2.3768115942028984,0.91304347826086962]
[3,10.6,100,25,99,1.78,0.62,200,1,0.69,2.5797101449275366,0.89855072463768126]
[3,5,100,25,1,0.7,0.7,300,0,0.7,1,1]
[3,6.1,100,25,50,1.08,0.67,300,1,0.7,1.5428571428571431,0.9571428571428573]
[3,6.5,100,25,60,1.23,0.67,300,1,0.7,1.7571428571428573,0.9571428571428573]
[3,7,100,25,70,1.39,0.66,300,1,0.7,1.9857142857142858,0.94285714285714295]
[3,7.4,100,25,80,1.54,0.66,300,1,0.7,2.2000000000000002,0.94285714285714295]
[3,7.8,100,25,90,1.7,0.65,300,1,0.7,2.4285714285714288,0.92857142857142871]
[3,8.1999999999999993,100,25,99,1.83,0.65,300,1,0.7,2.6142857142857148,0.92857142857142871]
[3,8.8000000000000007,100,26,1,0.68,0.68,100,0,0.68,1,1]
[3,11.3,100,26,50,0.97,0.61,100,1,0.68,1.4264705882352939,0.89705882352941169]
[3,12.5,100,26,60,1.1000000000000001,0.59,100,1,0.68,1.6176470588235294,0.86764705882352933]
[3,13.6,100,26,70,1.24,0.56999999999999995,100,1,0.68,1.8235294117647058,0.83823529411764697]
[3,14.8,100,26,80,1.37,0.55000000000000004,100,1,0.68,2.0147058823529411,0.80882352941176472]
[3,16,100,26,90,1.51,0.54,100,1,0.68,2.2205882352941173,0.79411764705882348]
[3,17,100,26,99,1.63,0.52,100,1,0.68,2.3970588235294112,0.76470588235294112]
[3,6.1,100,26,1,0.72,0.72,200,0,0.72,1,1]
[3,7.8,100,26,50,1.1200000000000001,0.68,200,1,0.72,1.5555555555555558,0.94444444444444453]
[3,8.5,100,26,60,1.28,0.68,200,1,0.72,1.7777777777777779,0.94444444444444453]
[3,9.1,100,26,70,1.43,0.67,200,1,0.72,1.9861111111111112,0.93055555555555569]
[3,9.8000000000000007,100,26,80,1.59,0.66,200,1,0.72,2.2083333333333335,0.91666666666666674]
[3,10.5,100,26,90,1.75,0.65,200,1,0.72,2.4305555555555558,0.90277777777777779]
[3,11.1,100,26,99,1.89,0.64,200,1,0.72,2.625,0.88888888888888895]
[3,5.0999999999999996,100,26,1,0.73,0.73,300,0,0.73,1,1]
[3,6.3,100,26,50,1.1499999999999999,0.7,300,1,0.73,1.5753424657534245,0.95890410958904104]
[3,6.8,100,26,60,1.32,0.7,300,1,0.73,1.8082191780821919,0.95890410958904104]
[3,7.2,100,26,70,1.48,0.69,300,1,0.73,2.0273972602739727,0.9452054794520548]
[3,7.7,100,26,80,1.64,0.68,300,1,0.73,2.2465753424657535,0.93150684931506855]
[3,8.1999999999999993,100,26,90,1.81,0.68,300,1,0.73,2.4794520547945207,0.93150684931506855]
[3,8.6,100,26,99,1.95,0.67,300,1,0.73,2.6712328767123288,0.91780821917808231]
[3,9.1,100,27,1,0.71,0.71,100,0,0.71,1,1]
[3,11.8,100,27,50,1.03,0.63,100,1,0.71,1.4507042253521127,0.88732394366197187]
[3,13.1,100,27,60,1.18,0.61,100,{"$f":"IF(F150<>G150,1,0)","v":1},0.71,{"$f":"F150/J150","v":1.6619718309859155},0.85915492957746487]
[3,14.3,100,27,70,1.32,0.59,100,1,0.71,1.859154929577465,{"$f":"G151/J151","v":0.83098591549295775}]
[3,15.6,100,27,80,1.46,0.56999999999999995,100,1,0.71,2.056338028169014,0.80281690140845063]
[3,16.8,100,27,90,1.61,0.55000000000000004,100,1,{"$f":"IF(F153/G153=1,F153,J152)","v":0.71},2.267605633802817,0.77464788732394374]
[3,17.899999999999999,100,27,99,1.73,0.54,100,1,0.71,2.4366197183098595,0.76056338028169024]
[3,6.2,100,27,1,0.75,0.75,200,0,0.75,1,1]
[3,8.1,100,27,50,1.19,0.71,200,1,0.75,1.5866666666666667,0.94666666666666666]
[3,8.8000000000000007,100,27,60,1.36,0.7,200,1,0.75,1.8133333333333335,0.93333333333333324]
[3,9.5,100,27,70,1.53,0.69,200,1,0.75,2.04,0.91999999999999993]
[3,10.3,100,27,80,1.69,0.68,200,1,0.75,2.2533333333333334,0.90666666666666673]
[3,11,100,27,90,1.86,0.67,200,1,0.75,2.48,0.89333333333333342]
[3,11.6,100,27,99,2.0099999999999998,0.67,200,1,0.75,2.6799999999999997,0.89333333333333342]
[3,5.2,100,27,1,0.76,0.76,300,0,0.76,1,1]
[3,6.5,100,27,50,1.23,0.73,300,1,0.76,1.618421052631579,0.96052631578947367]
[3,7,100,27,60,1.4,0.72,300,1,0.76,1.8421052631578947,0.94736842105263153]
[3,7.5,100,27,70,1.58,0.72,300,1,0.76,2.0789473684210527,0.94736842105263153]
[3,8,100,27,80,1.75,0.71,300,1,0.76,2.3026315789473686,0.93421052631578938]
[3,8.5,100,27,90,1.92,0.7,300,1,0.76,2.5263157894736841,0.92105263157894735]
[3,8.9,100,27,99,2.08,0.7,300,1,0.76,2.736842105263158,0.92105263157894735]
[3,9.6999999999999993,170,21,1,0.78,0.78,100,0,0.78,1,1]
[3,10.4,170,21,50,0.86,0.7,100,1,0.78,1.1025641025641024,0.89743589743589736]
[3,11.5,170,21,60,0.99,0.66,100,1,0.78,1.2692307692307692,0.84615384615384615]
[3,12.6,170,21,70,1.1200000000000001,0.62,100,1,0.78,1.4358974358974359,0.79487179487179482]
[3,13.7,170,21,80,1.25,0.57999999999999996,100,1,0.78,1.6025641025641024,0.7435897435897435]
[3,14.8,170,21,90,1.37,0.55000000000000004,100,1,0.78,1.7564102564102564,0.70512820512820518]
[3,15.8,170,21,99,1.49,0.51,100,1,0.78,1.9102564102564101,0.65384615384615385]
[3,6.8,170,21,1,0.88,0.88,200,0,0.88,1,1]
[3,7.8,170,21,50,1.1299999999999999,0.83,200,1,0.88,1.2840909090909089,0.94318181818181812]
[3,8.6,170,21,60,1.3,0.8,200,1,0.88,1.4772727272727273,0.90909090909090917]
[3,9.3000000000000007,170,21,70,1.48,0.78,200,1,0.88,1.6818181818181819,0.88636363636363635]
[3,10.1,170,21,80,1.65,0.76,200,1,0.88,1.875,0.86363636363636365]
[3,10.8,170,21,90,1.82,0.74,200,1,0.88,2.0681818181818183,0.84090909090909094]
[3,11.5,170,21,99,1.98,0.72,200,1,0.88,2.25,0.81818181818181812]
[3,5.6,170,21,1,0.91,0.91,300,0,0.91,1,1]
[3,6.5,170,21,50,1.22,0.87,300,1,0.91,1.3406593406593406,0.95604395604395598]
[3,7,170,21,60,1.4,0.85,300,1,0.91,1.5384615384615383,0.93406593406593397]
[3,7.5,170,21,70,1.59,0.84,300,1,0.91,1.7472527472527473,0.92307692307692302]
[3,8.1,170,21,80,1.78,0.83,300,1,0.91,1.956043956043956,0.91208791208791207]
[3,8.6,170,21,90,1.96,0.81,300,1,0.91,2.1538461538461537,0.89010989010989017]
[3,9.1,170,21,99,2.13,0.8,300,1,0.91,2.3406593406593403,0.87912087912087911]
[3,10,170,22,1,0.82,0.82,100,0,0.82,1,1]
[3,11,170,22,50,0.93,0.72,100,1,0.82,1.1341463414634148,0.87804878048780488]
[3,12.2,170,22,60,1.07,0.69,100,1,0.82,1.3048780487804879,0.84146341463414631]
[3,13.3,170,22,70,1.21,0.65,100,1,0.82,1.475609756097561,0.79268292682926833]
[3,14.5,170,22,80,1.34,0.61,100,1,0.82,1.6341463414634148,0.74390243902439024]
[3,15.7,170,22,90,1.48,0.56999999999999995,100,1,0.82,1.8048780487804879,0.69512195121951215]
[3,16.7,170,22,99,1.6,0.53,100,1,0.82,1.9512195121951221,0.64634146341463417]
[3,7,170,22,1,0.93,0.93,200,0,0.93,1,1]
[3,8.3000000000000007,170,22,50,1.23,0.87,200,1,0.93,1.3225806451612903,0.93548387096774188]
[3,9,170,22,60,1.41,0.84,200,1,0.93,1.5161290322580643,0.90322580645161277]
[3,9.8000000000000007,170,22,70,1.59,0.82,200,1,0.93,1.7096774193548387,0.88172043010752676]
[3,10.6,170,22,80,1.78,0.8,200,1,0.93,1.9139784946236558,0.86021505376344087]
[3,11.4,170,22,90,1.96,0.78,200,1,0.93,2.10752688172043,0.83870967741935487]
[3,12.1,170,22,99,2.13,0.76,200,1,0.93,2.290322580645161,0.81720430107526876]
[3,5.7,170,22,1,0.96,0.96,300,0,0.96,1,1]
[3,6.8,170,22,50,1.32,0.91,300,1,0.96,1.3750000000000002,0.94791666666666674]
[3,7.3,170,22,60,1.52,0.9,300,1,0.96,1.5833333333333335,0.93750000000000011]
[3,7.9,170,22,70,1.72,0.88,300,1,0.96,1.7916666666666667,0.91666666666666674]
[3,8.5,170,22,80,1.91,0.87,300,1,0.96,1.9895833333333333,0.90625]
[3,9,170,22,90,2.11,0.85,300,1,0.96,2.1979166666666665,0.88541666666666663]
[3,9.5,170,22,99,2.29,0.84,300,1,0.96,2.385416666666667,0.875]
[3,10.4,170,23,1,0.86,0.86,100,0,0.86,1,1]
[3,11.6,170,23,50,1.01,0.75,100,1,0.86,1.1744186046511629,0.87209302325581395]
[3,12.9,170,23,60,1.1499999999999999,0.71,100,1,0.86,1.3372093023255813,0.82558139534883723]
[3,14.1,170,23,70,1.3,0.67,100,{"$f":"IF(F214<>G214,1,0)","v":1},0.86,{"$f":"F214/J214","v":1.5116279069767442},0.77906976744186052]
[3,15.3,170,23,80,1.44,0.63,100,1,0.86,1.6744186046511627,{"$f":"G215/J215","v":0.73255813953488369}]
[3,16.600000000000001,170,23,90,1.58,0.59,100,1,0.86,1.8372093023255816,0.68604651162790697]
[3,17.7,170,23,99,1.71,0.55000000000000004,100,1,{"$f":"IF(F217/G217=1,F217,J216)","v":0.86},1.9883720930232558,0.63953488372093026]
[3,7.2,170,23,1,0.98,0.98,200,0,0.98,1,1]
[3,8.6999999999999993,170,23,50,1.33,0.9,200,1,0.98,1.3571428571428572,0.91836734693877553]
[3,9.5,170,23,60,1.52,0.88,200,1,0.98,1.5510204081632653,0.89795918367346939]
[3,10.4,170,23,70,1.71,0.86,200,1,0.98,1.7448979591836735,0.87755102040816324]
[3,11.2,170,23,80,1.91,0.83,200,1,0.98,1.9489795918367347,0.84693877551020402]
[3,12,170,23,90,2.1,0.81,200,1,0.98,2.1428571428571428,0.82653061224489799]
[3,12.8,170,23,99,2.2799999999999998,0.79,200,1,0.98,2.3265306122448979,0.80612244897959184]
[3,5.9,170,23,1,1.01,1.01,300,0,1.01,1,1]
[3,7.1,170,23,50,1.43,0.95,300,1,1.01,1.4158415841584158,0.94059405940594054]
[3,7.7,170,23,60,1.64,0.94,300,1,1.01,1.6237623762376237,0.93069306930693063]
[3,8.3000000000000007,170,23,70,1.85,0.92,300,1,1.01,1.8316831683168318,0.91089108910891092]
[3,8.9,170,23,80,2.06,0.91,300,1,1.01,2.0396039603960396,0.90099009900990101]
[3,9.5,170,23,90,2.27,0.89,300,1,1.01,2.2475247524752477,0.88118811881188119]
[3,10,170,23,99,2.46,0.87,300,1,1.01,2.4356435643564356,0.86138613861386137]
[3,10.8,170,24,1,0.91,0.91,100,0,0.91,1,1]
[3,12.3,170,24,50,1.08,0.78,100,1,0.91,1.1868131868131868,0.8571428571428571]
[3,13.6,170,24,60,1.24,0.74,100,1,0.91,1.3626373626373627,0.81318681318681318]
[3,14.9,170,24,70,1.39,0.69,100,1,0.91,1.5274725274725274,0.75824175824175821]
[3,16.2,170,24,80,1.54,0.65,100,1,0.91,1.6923076923076923,0.7142857142857143]
[3,17.5,170,24,90,1.69,0.61,100,1,0.91,1.857142857142857,0.67032967032967028]
[3,18.600000000000001,170,24,99,1.82,0.56999999999999995,100,1,0.91,2,0.62637362637362626]
[3,7.4,170,24,1,1.02,1.02,200,0,1.02,1,1]
[3,9.1,170,24,50,1.43,0.94,200,1,1.02,1.4019607843137254,0.92156862745098034]
[3,10,170,24,60,1.63,0.92,200,1,1.02,1.5980392156862744,0.90196078431372551]
[3,10.9,170,24,70,1.84,0.89,200,1,1.02,1.803921568627451,0.87254901960784315]
[3,11.8,170,24,80,2.0499999999999998,0.87,200,1,1.02,2.0098039215686274,0.8529411764705882]
[3,12.7,170,24,90,2.25,0.84,200,1,1.02,2.2058823529411766,0.82352941176470584]
[3,13.4,170,24,99,2.44,0.82,200,1,1.02,2.392156862745098,0.8039215686274509]
[3,6,170,24,1,1.06,1.06,300,0,1.06,1,1]
[3,7.4,170,24,50,1.54,1,300,1,1.06,1.4528301886792452,0.94339622641509424]
[3,8,170,24,60,1.76,0.98,300,1,1.06,1.6603773584905659,0.92452830188679236]
[3,8.6999999999999993,170,24,70,1.98,0.96,300,1,1.06,1.8679245283018866,0.90566037735849048]
[3,9.3000000000000007,170,24,80,2.2000000000000002,0.94,300,1,1.06,2.0754716981132075,0.88679245283018859]
[3,9.9,170,24,90,2.4300000000000002,0.93,300,1,1.06,2.2924528301886791,0.87735849056603776]
[3,10.5,170,24,99,2.63,0.91,300,1,1.06,2.4811320754716979,0.85849056603773588]
[3,11.1,170,25,1,0.95,0.95,100,0,0.95,1,1]
[3,13,170,25,50,1.1599999999999999,0.81,100,1,0.95,1.2210526315789474,0.85263157894736852]
[3,14.4,170,25,60,1.33,0.76,100,1,0.95,1.4000000000000001,0.8]
[3,15.7,170,25,70,1.48,0.72,100,1,0.95,1.5578947368421052,0.75789473684210529]
[3,17.100000000000001,170,25,80,1.64,0.67,100,1,0.95,1.7263157894736842,0.70526315789473693]
[3,18.399999999999999,170,25,90,1.8,0.63,100,1,0.95,1.8947368421052633,0.66315789473684217]
[3,19.600000000000001,170,25,99,1.94,0.59,100,1,0.95,2.0421052631578949,0.62105263157894741]
[3,7.6,170,25,1,1.07,1.07,200,0,1.07,1,1]
[3,9.6,170,25,50,1.53,0.98,200,1,1.07,1.4299065420560748,0.9158878504672896]
[3,10.5,170,25,60,1.75,0.95,200,1,1.07,1.6355140186915886,0.8878504672897195]
[3,11.4,170,25,70,1.97,0.93,200,1,1.07,1.8411214953271027,0.86915887850467288]
[3,12.4,170,25,80,2.19,0.9,200,1,1.07,2.0467289719626165,0.84112149532710279]
[3,13.3,170,25,90,2.4,0.88,200,1,1.07,2.2429906542056073,0.82242990654205606]
[3,14.2,170,25,99,2.6,0.85,200,1,1.07,2.4299065420560746,0.79439252336448596]
[3,6.1,170,25,1,1.1000000000000001,1.1000000000000001,300,0,1.1000000000000001,1,1]
[3,7.7,170,25,50,1.65,1.04,300,1,1.1000000000000001,1.4999999999999998,0.94545454545454544]
[3,8.4,170,25,60,1.89,1.02,300,1,1.1000000000000001,1.718181818181818,0.92727272727272725]
[3,9.1,170,25,70,2.12,1,300,1,1.1000000000000001,1.9272727272727272,0.90909090909090906]
[3,9.6999999999999993,170,25,80,2.36,0.98,300,1,1.1000000000000001,2.1454545454545451,0.89090909090909087]
[3,10.4,170,25,90,2.6,0.96,300,1,1.1000000000000001,2.3636363636363633,0.87272727272727257]
[3,11,170,25,99,2.81,0.95,300,1,1.1000000000000001,2.5545454545454542,0.86363636363636354]
[3,11.5,170,26,1,0.99,0.99,100,0,0.99,1,1]
[3,13.7,170,26,50,1.24,0.84,100,1,0.99,1.2525252525252526,0.84848484848484851]
[3,15.1,170,26,60,1.41,0.79,100,1,0.99,1.4242424242424241,0.79797979797979801]
[3,16.600000000000001,170,26,70,1.58,0.74,100,1,0.99,1.595959595959596,0.74747474747474751]
[3,18,170,26,80,1.75,0.69,100,{"$f":"IF(F278<>G278,1,0)","v":1},0.99,{"$f":"F278/J278","v":1.7676767676767677},0.69696969696969691]
[3,19.399999999999999,170,26,90,1.91,0.64,100,1,0.99,1.9292929292929293,{"$f":"G279/J279","v":0.64646464646464652}]
[3,20.7,170,26,99,2.06,0.6,100,1,0.99,2.0808080808080809,0.60606060606060608]
[3,7.8,170,26,1,1.1200000000000001,1.1200000000000001,200,0,{"$f":"IF(F281/G281=1,F281,J280)","v":1.1200000000000001},1,1]
[3,10,170,26,50,1.64,1.02,200,1,1.1200000000000001,1.464285714285714,0.9107142857142857]
[3,11,170,26,60,1.87,0.99,200,1,1.1200000000000001,1.669642857142857,0.88392857142857129]
[3,12,170,26,70,2.1,0.96,200,1,1.1200000000000001,1.875,0.85714285714285698]
[3,13,170,26,80,2.33,0.93,200,1,1.1200000000000001,2.0803571428571428,0.83035714285714279]
[3,14,170,26,90,2.56,0.91,200,1,1.1200000000000001,2.2857142857142856,0.8125]
[3,14.9,170,26,99,2.77,0.88,200,1,1.1200000000000001,2.4732142857142856,0.7857142857142857]
[3,6.3,170,26,1,1.1499999999999999,1.1499999999999999,300,0,1.1499999999999999,1,1]
[3,8,170,26,50,1.77,1.08,300,1,1.1499999999999999,1.5391304347826089,0.93913043478260883]
[3,8.8000000000000007,170,26,60,2.02,1.06,300,1,1.1499999999999999,1.7565217391304349,0.92173913043478273]
[3,9.5,170,26,70,2.27,1.04,300,1,1.1499999999999999,1.973913043478261,0.90434782608695663]
[3,10.199999999999999,170,26,80,2.5099999999999998,1.02,300,1,1.1499999999999999,2.1826086956521737,0.88695652173913053]
[3,10.9,170,26,90,2.77,1,300,1,1.1499999999999999,2.4086956521739133,0.86956521739130443]
[3,11.5,170,26,99,2.99,0.98,300,1,1.1499999999999999,2.6000000000000005,0.85217391304347834]
[3,11.8,170,27,1,1.03,1.03,100,0,1.03,1,1]
[3,14.4,170,27,50,1.33,0.86,100,1,1.03,1.2912621359223302,0.83495145631067957]
[3,15.9,170,27,60,1.51,0.81,100,1,1.03,1.4660194174757282,0.78640776699029125]
[3,17.5,170,27,70,1.68,0.76,100,1,1.03,1.6310679611650485,0.73786407766990292]
[3,19,170,27,80,1.86,0.71,100,1,1.03,1.8058252427184467,0.68932038834951448]
[3,20.399999999999999,170,27,90,2.0299999999999998,0.66,100,1,1.03,1.9708737864077668,0.64077669902912626]
[3,21.7,170,27,99,2.1800000000000002,0.61,100,1,1.03,2.116504854368932,0.59223300970873782]
[3,8,170,27,1,1.1599999999999999,1.1599999999999999,200,0,1.1599999999999999,1,1]
[3,10.5,170,27,50,1.75,1.05,200,1,1.1599999999999999,1.5086206896551726,0.90517241379310354]
[3,11.6,170,27,60,2,1.02,200,1,1.1599999999999999,1.7241379310344829,0.8793103448275863]
[3,12.6,170,27,70,2.2400000000000002,1,200,1,1.1599999999999999,1.931034482758621,0.86206896551724144]
[3,13.7,170,27,80,2.4900000000000002,0.97,200,1,1.1599999999999999,2.1465517241379315,0.8362068965517242]
[3,14.7,170,27,90,2.73,0.94,200,1,1.1599999999999999,2.353448275862069,0.81034482758620696]
[3,15.6,170,27,99,2.95,0.91,200,1,1.1599999999999999,2.5431034482758625,0.78448275862068972]
[3,6.4,170,27,1,1.2,1.2,300,0,1.2,1,1]
[3,8.4,170,27,50,1.89,1.1200000000000001,300,1,1.2,1.575,0.93333333333333346]
[3,9.1,170,27,60,2.15,1.1000000000000001,300,1,1.2,1.7916666666666667,0.91666666666666674]
[3,9.9,170,27,70,2.41,1.08,300,1,1.2,2.0083333333333337,0.90000000000000013]
[3,10.7,170,27,80,2.68,1.06,300,1,1.2,2.2333333333333334,0.88333333333333341]
[3,11.4,170,27,90,2.95,1.04,300,1,1.2,2.4583333333333335,0.8666666666666667]
[3,12.1,170,27,99,3.18,1.02,300,1,1.2,2.6500000000000004,0.85000000000000009]
[3,11.1,240,21,1,0.95,0.95,100,0,0.95,1,1]
[3,11.2,240,21,50,0.96,0.85,100,1,0.95,1.0105263157894737,0.89473684210526316]
[3,12.5,240,21,60,1.1000000000000001,0.78,100,1,0.95,1.1578947368421053,0.82105263157894748]
[3,13.7,240,21,70,1.25,0.72,100,1,0.95,1.3157894736842106,0.75789473684210529]
[3,14.9,240,21,80,1.38,0.66,100,1,0.95,1.4526315789473683,0.69473684210526321]
[3,16.100000000000001,240,21,90,1.52,0.6,100,1,0.95,1.6,0.63157894736842102]
[3,17.100000000000001,240,21,99,1.65,0.55000000000000004,100,1,0.95,1.736842105263158,0.57894736842105265]
[3,7.8,240,21,1,1.1299999999999999,1.1299999999999999,200,0,1.1299999999999999,1,1]
[3,8.9,240,21,50,1.38,1.04,200,1,1.1299999999999999,1.2212389380530975,0.92035398230088505]
[3,9.8000000000000007,240,21,60,1.59,1,200,1,1.1299999999999999,1.4070796460176993,0.88495575221238942]
[3,10.7,240,21,70,1.79,0.96,200,1,1.1299999999999999,1.5840707964601772,0.8495575221238939]
[3,11.6,240,21,80,2,0.92,200,1,1.1299999999999999,1.7699115044247788,0.81415929203539839]
[3,12.5,240,21,90,2.21,0.88,200,1,1.1299999999999999,1.9557522123893807,0.77876106194690276]
[3,13.3,240,21,99,2.4,0.85,200,1,1.1299999999999999,2.1238938053097347,0.75221238938053103]
[3,6.4,240,21,1,1.19,1.19,300,0,1.19,1,1]
[3,7.4,240,21,50,1.54,1.1100000000000001,300,1,1.19,1.2941176470588236,0.93277310924369761]
[3,8.1,240,21,60,1.77,1.0900000000000001,300,1,1.19,1.4873949579831933,0.91596638655462193]
[3,8.6999999999999993,240,21,70,2.0099999999999998,1.06,300,1,1.19,1.6890756302521008,0.89075630252100846]
[3,9.4,240,21,80,2.2400000000000002,1.03,300,1,1.19,1.8823529411764708,0.86554621848739499]
[3,10.1,240,21,90,2.48,1,300,1,1.19,2.0840336134453783,0.84033613445378152]
[3,10.7,240,21,99,2.69,0.98,300,1,1.19,2.2605042016806722,0.82352941176470595]
[3,11.5,240,22,1,1,1,100,0,1,1,1]
[3,11.9,240,22,50,1.04,0.88,100,1,1,1.04,0.88]
[3,13.2,240,22,60,1.19,0.81,100,1,1,1.19,0.81]
[3,14.5,240,22,70,1.34,0.75,100,1,1,1.34,0.75]
[3,15.8,240,22,80,1.49,0.68,100,1,1,1.49,0.68]
[3,17,240,22,90,1.63,0.62,100,{"$f":"IF(F342<>G342,1,0)","v":1},1,{"$f":"F342/J342","v":1.63},0.62]
[3,18.100000000000001,240,22,99,1.76,0.56000000000000005,100,1,1,1.76,{"$f":"G343/J343","v":0.56000000000000005}]
[3,8.1,240,22,1,1.19,1.19,200,0,1.19,1,1]
[3,9.4,240,22,50,1.49,1.08,200,1,{"$f":"IF(F345/G345=1,F345,J344)","v":1.19},1.2521008403361344,0.90756302521008414]
[3,10.4,240,22,60,1.72,1.04,200,1,1.19,1.4453781512605042,0.87394957983193289]
[3,11.3,240,22,70,1.94,1,200,1,1.19,1.6302521008403361,0.84033613445378152]
[3,12.2,240,22,80,2.16,0.96,200,1,1.19,1.8151260504201683,0.80672268907563027]
[3,13.2,240,22,90,2.38,0.92,200,1,1.19,2,0.77310924369747902]
[3,14,240,22,99,2.58,0.88,200,1,1.19,2.1680672268907566,0.73949579831932777]
[3,6.6,240,22,1,1.25,1.25,300,0,1.25,1,1]
[3,7.8,240,22,50,1.67,1.17,300,1,1.25,1.3359999999999999,0.93599999999999994]
[3,8.5,240,22,60,1.92,1.1399999999999999,300,1,1.25,1.536,0.91199999999999992]
[3,9.1999999999999993,240,22,70,2.17,1.1100000000000001,300,1,1.25,1.736,0.88800000000000012]
[3,9.9,240,22,80,2.42,1.08,300,1,1.25,1.9359999999999999,0.8640000000000001]
[3,10.6,240,22,90,2.67,1.05,300,1,1.25,2.1360000000000001,0.84000000000000008]
[3,11.3,240,22,99,2.89,1.02,300,1,1.25,2.3120000000000003,0.81600000000000006]
[3,12,240,23,1,1.05,1.05,100,0,1.05,1,1]
[3,12.7,240,23,50,1.1299999999999999,0.91,100,1,1.05,1.0761904761904761,0.8666666666666667]
[3,14,240,23,60,1.28,0.84,100,1,1.05,1.2190476190476189,0.79999999999999993]
[3,15.4,240,23,70,1.44,0.78,100,1,1.05,1.3714285714285712,0.74285714285714288]
[3,16.7,240,23,80,1.6,0.71,100,1,1.05,1.5238095238095237,0.67619047619047612]
[3,18,240,23,90,1.75,0.64,100,1,1.05,1.6666666666666665,0.60952380952380947]
[3,19.100000000000001,240,23,99,1.88,0.57999999999999996,100,1,1.05,1.7904761904761903,0.55238095238095231]
[3,8.4,240,23,1,1.25,1.25,200,0,1.25,1,1]
[3,9.9,240,23,50,1.61,1.1299999999999999,200,1,1.25,1.288,0.90399999999999991]
[3,10.9,240,23,60,1.85,1.0900000000000001,200,1,1.25,1.48,0.87200000000000011]
[3,11.9,240,23,70,2.08,1.04,200,1,1.25,1.6640000000000001,0.83200000000000007]
[3,12.9,240,23,80,2.3199999999999998,1,200,1,1.25,1.8559999999999999,0.8]
[3,13.9,240,23,90,2.5499999999999998,0.96,200,1,1.25,2.04,0.76800000000000002]
[3,14.8,240,23,99,2.76,0.92,200,1,1.25,2.2079999999999997,0.73599999999999999]
[3,6.8,240,23,1,1.31,1.31,300,0,1.31,1,1]
[3,8.1999999999999993,240,23,50,1.8,1.22,300,1,1.31,1.3740458015267176,0.93129770992366412]
[3,8.9,240,23,60,2.0699999999999998,1.19,300,1,1.31,1.580152671755725,0.90839694656488545]
[3,9.6999999999999993,240,23,70,2.33,1.1599999999999999,300,1,1.31,1.7786259541984732,0.88549618320610679]
[3,10.4,240,23,80,2.6,1.1200000000000001,300,1,1.31,1.9847328244274809,0.85496183206106879]
[3,11.2,240,23,90,2.86,1.0900000000000001,300,1,1.31,2.1832061068702289,0.83206106870229013]
[3,11.9,240,23,99,3.1,1.06,300,1,1.31,2.3664122137404582,0.80916030534351147]
[3,12.4,240,24,1,1.1000000000000001,1.1000000000000001,100,0,1.1000000000000001,1,1]
[3,13.4,240,24,50,1.21,0.95,100,1,1.1000000000000001,1.0999999999999999,0.86363636363636354]
[3,14.8,240,24,60,1.38,0.87,100,1,1.1000000000000001,1.2545454545454544,0.79090909090909089]
[3,16.2,240,24,70,1.54,0.8,100,1,1.1000000000000001,1.4,0.72727272727272729]
[3,17.600000000000001,240,24,80,1.7,0.73,100,1,1.1000000000000001,1.5454545454545452,0.66363636363636358]
[3,19,240,24,90,1.86,0.66,100,1,1.1000000000000001,1.6909090909090909,0.6]
[3,20.2,240,24,99,2,0.6,100,1,1.1000000000000001,1.8181818181818181,0.54545454545454541]
[3,8.6,240,24,1,1.31,1.31,200,0,1.31,1,1]
[3,10.5,240,24,50,1.74,1.18,200,1,1.31,1.3282442748091603,0.9007633587786259]
[3,11.5,240,24,60,1.99,1.1299999999999999,200,1,1.31,1.5190839694656488,0.86259541984732813]
[3,12.6,240,24,70,2.23,1.08,200,1,1.31,1.7022900763358777,0.82442748091603058]
[3,13.6,240,24,80,2.48,1.04,200,1,1.31,1.8931297709923662,0.79389312977099236]
[3,14.7,240,24,90,2.73,0.99,200,1,1.31,2.0839694656488548,0.75572519083969458]
[3,15.6,240,24,99,2.95,0.95,200,1,1.31,2.2519083969465647,0.72519083969465647]
[3,6.9,240,24,1,1.38,1.38,300,0,1.38,1,1]
[3,8.5,240,24,50,1.94,1.27,300,1,1.38,1.4057971014492754,0.92028985507246386]
[3,9.3000000000000007,240,24,60,2.2200000000000002,1.24,300,1,1.38,1.6086956521739133,0.89855072463768126]
[3,10.1,240,24,70,2.5,1.2,300,1,1.38,1.8115942028985508,0.86956521739130443]
[3,11,240,24,80,2.78,1.17,300,1,1.38,2.0144927536231885,0.84782608695652173]
[3,11.8,240,24,90,3.06,1.1399999999999999,300,1,1.38,2.2173913043478262,0.82608695652173914]
[3,12.5,240,24,99,3.32,1.1000000000000001,300,1,1.38,2.4057971014492754,0.79710144927536242]
[3,12.9,240,25,1,1.1499999999999999,1.1499999999999999,100,0,1.1499999999999999,1,1]
[3,14.1,240,25,50,1.3,0.98,100,1,1.1499999999999999,1.1304347826086958,0.85217391304347834]
[3,15.6,240,25,60,1.47,0.9,100,1,1.1499999999999999,1.2782608695652176,0.78260869565217395]
[3,17.100000000000001,240,25,70,1.64,0.82,100,1,1.1499999999999999,1.4260869565217391,0.71304347826086956]
[3,18.600000000000001,240,25,80,1.81,0.75,100,1,1.1499999999999999,1.5739130434782611,0.65217391304347827]
[3,20,240,25,90,1.98,0.68,100,1,1.1499999999999999,1.7217391304347827,0.5913043478260871]
[3,21.2,240,25,99,2.12,0.61,100,{"$f":"IF(F406<>G406,1,0)","v":1},1.1499999999999999,{"$f":"F406/J406","v":1.8434782608695655},0.5304347826086957]
[3,8.9,240,25,1,1.37,1.37,200,0,1.37,1,{"$f":"G407/J407","v":1}]
[3,11,240,25,50,1.86,1.22,200,1,1.37,1.3576642335766422,0.8905109489051094]
[3,12.1,240,25,60,2.13,1.17,200,1,{"$f":"IF(F409/G409=1,F409,J408)","v":1.37},1.554744525547445,0.85401459854014583]
[3,13.2,240,25,70,2.39,1.1200000000000001,200,1,1.37,1.7445255474452555,0.81751824817518248]
[3,14.4,240,25,80,2.65,1.08,200,1,1.37,1.9343065693430654,0.78832116788321172]
[3,15.5,240,25,90,2.91,1.03,200,1,1.37,2.1240875912408756,0.75182481751824815]
[3,16.5,240,25,99,3.14,0.98,200,1,1.37,2.2919708029197081,0.71532846715328458]
[3,7.1,240,25,1,1.44,1.44,300,0,1.44,1,1]
[3,9,240,25,50,2.08,1.32,300,1,1.44,1.4444444444444446,0.91666666666666674]
[3,9.8000000000000007,240,25,60,2.38,1.29,300,1,1.44,1.6527777777777777,0.89583333333333337]
[3,10.7,240,25,70,2.68,1.25,300,1,1.44,1.8611111111111114,0.86805555555555558]
[3,11.5,240,25,80,2.97,1.21,300,1,1.44,2.0625,0.84027777777777779]
[3,12.4,240,25,90,3.27,1.18,300,1,1.44,2.2708333333333335,0.81944444444444442]
[3,13.1,240,25,99,3.54,1.1499999999999999,300,1,1.44,2.4583333333333335,0.79861111111111105]
[3,13.3,240,26,1,1.21,1.21,100,0,1.21,1,1]
[3,14.9,240,26,50,1.38,1.01,100,1,1.21,1.140495867768595,0.83471074380165289]
[3,16.5,240,26,60,1.57,0.93,100,1,1.21,1.2975206611570249,0.76859504132231415]
[3,18,240,26,70,1.75,0.85,100,1,1.21,1.4462809917355373,0.7024793388429752]
[3,19.5,240,26,80,1.93,0.77,100,1,1.21,1.5950413223140496,0.63636363636363635]
[3,21,240,26,90,2.1,0.69,100,1,1.21,1.7355371900826448,0.57024793388429751]
[3,22.3,240,26,99,2.25,0.62,100,1,1.21,1.859504132231405,0.51239669421487599]
[3,9.1,240,26,1,1.43,1.43,200,0,1.43,1,1]
[3,11.6,240,26,50,2,1.26,200,1,1.43,1.3986013986013988,0.88111888111888115]
[3,12.8,240,26,60,2.27,1.21,200,1,1.43,1.5874125874125875,0.84615384615384615]
[3,13.9,240,26,70,2.5499999999999998,1.1599999999999999,200,1,1.43,1.7832167832167831,0.81118881118881114]
[3,15.1,240,26,80,2.83,1.1100000000000001,200,1,1.43,1.9790209790209792,0.77622377622377636]
[3,16.3,240,26,90,3.1,1.06,200,1,1.43,2.1678321678321679,0.74125874125874136]
[3,17.399999999999999,240,26,99,3.35,1.01,200,1,1.43,2.3426573426573429,0.70629370629370636]
[3,7.3,240,26,1,1.5,1.5,300,0,1.5,1,1]
[3,9.4,240,26,50,2.23,1.37,300,1,1.5,1.4866666666666666,0.91333333333333344]
[3,10.3,240,26,60,2.54,1.34,300,1,1.5,1.6933333333333334,0.89333333333333342]
[3,11.2,240,26,70,2.86,1.3,300,1,1.5,1.9066666666666665,0.8666666666666667]
[3,12.1,240,26,80,3.18,1.26,300,1,1.5,2.12,0.84]
[3,13,240,26,90,3.49,1.22,300,1,1.5,2.3266666666666667,0.81333333333333335]
[3,13.8,240,26,99,3.77,1.19,300,1,1.5,2.5133333333333332,0.79333333333333333]
[3,13.8,240,27,1,1.26,1.26,100,0,1.26,1,1]
[3,15.7,240,27,50,1.48,1.04,100,1,1.26,1.1746031746031746,0.82539682539682546]
[3,17.3,240,27,60,1.67,0.95,100,1,1.26,1.3253968253968254,0.75396825396825395]
[3,19,240,27,70,1.86,0.87,100,1,1.26,1.4761904761904763,0.69047619047619047]
[3,20.5,240,27,80,2.04,0.79,100,1,1.26,1.6190476190476191,0.62698412698412698]
[3,22.1,240,27,90,2.2200000000000002,0.71,100,1,1.26,1.7619047619047621,0.56349206349206349]
[3,23.4,240,27,99,2.38,0.63,100,1,1.26,1.8888888888888888,0.5]
[3,9.4,240,27,1,1.49,1.49,200,0,1.49,1,1]
[3,12.1,240,27,50,2.13,1.31,200,1,1.49,1.4295302013422819,0.87919463087248328]
[3,13.4,240,27,60,2.42,1.25,200,1,1.49,1.6241610738255032,0.83892617449664431]
[3,14.7,240,27,70,2.72,1.2,200,1,1.49,1.8255033557046982,0.80536912751677847]
[3,15.9,240,27,80,3.01,1.1399999999999999,200,1,1.49,2.0201342281879193,0.76510067114093949]
[3,17.100000000000001,240,27,90,3.3,1.0900000000000001,200,1,1.49,2.2147651006711406,0.73154362416107388]
[3,18.3,240,27,99,3.56,1.04,200,1,1.49,2.3892617449664431,0.69798657718120805]
[3,7.5,240,27,1,1.57,1.57,300,0,1.57,1,1]
[3,9.8000000000000007,240,27,50,2.38,1.42,300,1,1.57,1.5159235668789808,0.90445859872611456]
[3,10.8,240,27,60,2.71,1.38,300,1,1.57,1.7261146496815285,0.87898089171974514]
[3,11.7,240,27,70,3.05,1.34,300,1,1.57,1.9426751592356686,0.85350318471337583]
[3,12.7,240,27,80,3.38,1.3,300,1,1.57,2.1528662420382165,0.82802547770700641]
[3,13.6,240,27,90,3.72,1.26,300,1,1.57,2.3694267515923566,0.80254777070063688]
[3,14.5,240,27,99,4.0199999999999996,1.22,300,1,1.57,2.5605095541401268,0.77707006369426745]
[3,12.1,310,21,1,1.07,1.07,100,0,1.07,1,1]
[3,12.1,310,21,50,1.06,1.06,100,0,1.06,1,1]
[3,13.1,310,21,60,1.17,0.89,100,1,1.06,1.1037735849056602,0.83962264150943389]
[3,14.3,310,21,70,1.32,0.8,100,1,1.06,1.2452830188679245,0.75471698113207553]
[3,15.6,310,21,80,1.47,0.72,100,1,1.06,1.3867924528301885,0.67924528301886788]
[3,16.8,310,21,90,1.61,0.64,100,1,1.06,1.5188679245283019,0.60377358490566035]
[3,17.899999999999999,310,21,99,1.73,0.56000000000000005,100,1,1.06,1.6320754716981132,0.52830188679245282]
[3,8.6999999999999993,310,21,1,1.33,1.33,200,{"$f":"IF(F470<>G470,1,0)","v":0},1.33,{"$f":"F470/J470","v":1},1]
[3,9.6999999999999993,310,21,50,1.55,1.21,200,1,1.33,1.1654135338345863,{"$f":"G471/J471","v":0.90977443609022546}]
[3,10.7,310,21,60,1.79,1.1499999999999999,200,1,1.33,1.3458646616541352,0.86466165413533824]
[3,11.7,310,21,70,2.02,1.0900000000000001,200,1,{"$f":"IF(F473/G473=1,F473,J472)","v":1.33},1.518796992481203,0.81954887218045114]
[3,12.6,310,21,80,2.25,1.03,200,1,1.33,1.6917293233082706,0.77443609022556392]
[3,13.6,310,21,90,2.48,0.97,200,1,1.33,1.8646616541353382,0.7293233082706766]
[3,14.5,310,21,99,2.69,0.92,200,1,1.33,2.0225563909774436,0.69172932330827064]
[3,7.1,310,21,1,1.42,1.42,300,0,1.42,1,1]
[3,8.1,310,21,50,1.79,1.32,300,1,1.42,1.2605633802816902,0.92957746478873249]
[3,8.9,310,21,60,2.06,1.27,300,1,1.42,1.4507042253521127,0.89436619718309862]
[3,9.6999999999999993,310,21,70,2.33,1.23,300,1,1.42,1.6408450704225352,0.86619718309859162]
[3,10.4,310,21,80,2.6,1.19,300,1,1.42,1.830985915492958,0.8380281690140845]
[3,11.2,310,21,90,2.87,1.1399999999999999,300,1,1.42,2.0211267605633805,0.80281690140845063]
[3,11.9,310,21,99,3.11,1.1000000000000001,300,1,1.42,2.1901408450704225,0.77464788732394374]
[3,12.6,310,22,1,1.1299999999999999,1.1299999999999999,100,0,1.1299999999999999,1,1]
[3,12.5,310,22,50,1.1100000000000001,1.01,100,1,1.1299999999999999,0.98230088495575241,0.89380530973451333]
[3,13.9,310,22,60,1.27,0.92,100,1,1.1299999999999999,1.1238938053097347,0.81415929203539839]
[3,15.2,310,22,70,1.42,0.83,100,1,1.1299999999999999,1.2566371681415929,0.73451327433628322]
[3,16.5,310,22,80,1.57,0.74,100,1,1.1299999999999999,1.3893805309734515,0.65486725663716816]
[3,17.8,310,22,90,1.72,0.66,100,1,1.1299999999999999,1.5221238938053099,0.58407079646017712]
[3,18.899999999999999,310,22,99,1.85,0.57999999999999996,100,1,1.1299999999999999,1.6371681415929207,0.51327433628318586]
[3,9,310,22,1,1.4,1.4,200,0,1.4,1,1]
[3,10.199999999999999,310,22,50,1.68,1.26,200,1,1.4,1.2,0.9]
[3,11.3,310,22,60,1.93,1.2,200,1,1.4,1.3785714285714286,0.85714285714285721]
[3,12.3,310,22,70,2.1800000000000002,1.1399999999999999,200,1,1.4,1.5571428571428574,0.81428571428571428]
[3,13.4,310,22,80,2.42,1.08,200,1,1.4,1.7285714285714286,0.77142857142857157]
[3,14.4,310,22,90,2.66,1.02,200,1,1.4,1.9000000000000001,0.72857142857142865]
[3,15.4,310,22,99,2.88,0.96,200,1,1.4,2.0571428571428574,0.68571428571428572]
[3,7.3,310,22,1,1.5,1.5,300,0,1.5,1,1]
[3,8.5,310,22,50,1.94,1.38,300,1,1.5,1.2933333333333332,0.91999999999999993]
[3,9.4,310,22,60,2.23,1.33,300,1,1.5,1.4866666666666666,0.88666666666666671]
[3,10.199999999999999,310,22,70,2.5099999999999998,1.29,300,1,1.5,1.6733333333333331,0.86]
[3,11,310,22,80,2.8,1.24,300,1,1.5,1.8666666666666665,0.82666666666666666]
[3,11.8,310,22,90,3.09,1.19,300,1,1.5,2.06,0.79333333333333333]
[3,12.6,310,22,99,3.35,1.1499999999999999,300,1,1.5,2.2333333333333334,0.76666666666666661]
[3,13.2,310,23,1,1.19,1.19,100,0,1.19,1,1]
[3,13.3,310,23,50,1.2,1.05,100,1,1.19,1.0084033613445378,0.88235294117647067]
[3,14.7,310,23,60,1.36,0.95,100,1,1.19,1.142857142857143,0.79831932773109249]
[3,16.100000000000001,310,23,70,1.52,0.86,100,1,1.19,1.277310924369748,0.72268907563025209]
[3,17.399999999999999,310,23,80,1.68,0.77,100,1,1.19,1.411764705882353,0.6470588235294118]
[3,18.8,310,23,90,1.84,0.68,100,1,1.19,1.546218487394958,0.57142857142857151]
[3,20,310,23,99,1.97,0.6,100,1,1.19,1.6554621848739497,0.50420168067226889]
[3,9.3000000000000007,310,23,1,1.48,1.48,200,0,1.48,1,1]
[3,10.8,310,23,50,1.82,1.31,200,1,1.48,1.2297297297297298,0.8851351351351352]
[3,11.9,310,23,60,2.08,1.25,200,1,1.48,1.4054054054054055,0.84459459459459463]
[3,13,310,23,70,2.34,1.18,200,1,1.48,1.5810810810810809,0.79729729729729726]
[3,14.2,310,23,80,2.6,1.1200000000000001,200,1,1.48,1.7567567567567568,0.7567567567567568]
[3,15.3,310,23,90,2.86,1.05,200,1,1.48,1.9324324324324325,0.70945945945945954]
[3,16.2,310,23,99,3.08,1,200,1,1.48,2.0810810810810811,0.67567567567567566]
[3,7.5,310,23,1,1.57,1.57,300,0,1.57,1,1]
[3,9,310,23,50,2.1,1.44,300,1,1.57,1.3375796178343948,0.91719745222929927]
[3,9.9,310,23,60,2.4,1.39,300,1,1.57,1.5286624203821655,0.88535031847133749]
[3,10.7,310,23,70,2.71,1.34,300,1,1.57,1.7261146496815285,0.85350318471337583]
[3,11.6,310,23,80,3.01,1.29,300,1,1.57,1.9171974522292992,0.82165605095541405]
[3,12.5,310,23,90,3.31,1.24,300,1,1.57,2.1082802547770698,0.78980891719745216]
[3,13.3,310,23,99,3.59,1.2,300,1,1.57,2.2866242038216558,0.76433121019108274]
[3,13.7,310,24,1,1.24,1.24,100,0,1.24,1,1]
[3,14,310,24,50,1.28,1.08,100,1,1.24,1.032258064516129,0.87096774193548399]
[3,15.5,310,24,60,1.46,0.98,100,1,1.24,1.1774193548387097,0.79032258064516125]
[3,17,310,24,70,1.63,0.88,100,1,1.24,1.314516129032258,0.70967741935483875]
[3,18.399999999999999,310,24,80,1.8,0.79,100,1,1.24,1.4516129032258065,0.63709677419354838]
[3,19.8,310,24,90,1.96,0.69,100,1,1.24,1.5806451612903225,0.55645161290322576]
[3,21,310,24,99,2.1,0.61,100,1,1.24,1.6935483870967742,0.49193548387096775]
[3,9.6,310,24,1,1.55,1.55,200,0,1.55,1,1]
[3,11.4,310,24,50,1.96,1.36,200,{"$f":"IF(F534<>G534,1,0)","v":1},1.55,{"$f":"F534/J534","v":1.264516129032258},0.8774193548387097]
[3,12.6,310,24,60,2.23,1.29,200,1,1.55,1.4387096774193548,{"$f":"G535/J535","v":0.83225806451612905}]
[3,13.8,310,24,70,2.5099999999999998,1.23,200,1,1.55,1.6193548387096772,0.79354838709677411]
[3,14.9,310,24,80,2.78,1.1599999999999999,200,1,{"$f":"IF(F537/G537=1,F537,J536)","v":1.55},1.7935483870967741,0.74838709677419346]
[3,16.100000000000001,310,24,90,3.06,1.0900000000000001,200,1,1.55,1.9741935483870967,0.70322580645161292]
[3,17.100000000000001,310,24,99,3.3,1.03,200,1,1.55,2.129032258064516,0.6645161290322581]
[3,7.7,310,24,1,1.65,1.65,300,0,1.65,1,1]
[3,9.4,310,24,50,2.2599999999999998,1.5,300,1,1.65,1.3696969696969696,0.90909090909090917]
[3,10.4,310,24,60,2.58,1.45,300,1,1.65,1.5636363636363637,0.87878787878787878]
[3,11.3,310,24,70,2.9,1.39,300,1,1.65,1.7575757575757576,0.84242424242424241]
[3,12.2,310,24,80,3.23,1.34,300,1,1.65,1.9575757575757577,0.81212121212121224]
[3,13.1,310,24,90,3.55,1.29,300,1,1.65,2.1515151515151514,0.78181818181818186]
[3,14,310,24,99,3.84,1.24,300,1,1.65,2.3272727272727272,0.75151515151515158]
[3,14.2,310,25,1,1.3,1.3,100,0,1.3,1,1]
[3,14.8,310,25,50,1.37,1.1200000000000001,100,1,1.3,1.0538461538461539,0.86153846153846159]
[3,16.399999999999999,310,25,60,1.56,1.01,100,1,1.3,1.2,0.77692307692307694]
[3,17.899999999999999,310,25,70,1.73,0.91,100,1,1.3,1.3307692307692307,0.7]
[3,19.399999999999999,310,25,80,1.91,0.81,100,1,1.3,1.4692307692307691,0.62307692307692308]
[3,20.8,310,25,90,2.08,0.71,100,1,1.3,1.6,0.5461538461538461]
[3,22.1,310,25,99,2.2200000000000002,0.62,100,1,1.3,1.7076923076923078,0.47692307692307689]
[3,9.9,310,25,1,1.62,1.62,200,0,1.62,1,1]
[3,12,310,25,50,2.1,1.41,200,1,1.62,1.2962962962962963,0.87037037037037024]
[3,13.3,310,25,60,2.39,1.34,200,1,1.62,1.4753086419753085,0.8271604938271605]
[3,14.5,310,25,70,2.68,1.27,200,1,1.62,1.654320987654321,0.78395061728395055]
[3,15.7,310,25,80,2.97,1.19,200,1,1.62,1.8333333333333333,0.73456790123456783]
[3,17,310,25,90,3.26,1.1200000000000001,200,1,1.62,2.0123456790123453,0.6913580246913581]
[3,18.100000000000001,310,25,99,3.51,1.06,200,1,1.62,2.1666666666666665,0.65432098765432101]
[3,7.9,310,25,1,1.73,1.73,300,0,1.73,1,1]
[3,9.9,310,25,50,2.42,1.56,300,1,1.73,1.3988439306358382,0.90173410404624277]
[3,10.9,310,25,60,2.76,1.5,300,1,1.73,1.5953757225433525,0.86705202312138729]
[3,11.9,310,25,70,3.11,1.44,300,1,1.73,1.7976878612716762,0.83236994219653182]
[3,12.9,310,25,80,3.45,1.39,300,1,1.73,1.9942196531791909,0.80346820809248554]
[3,13.8,310,25,90,3.79,1.33,300,1,1.73,2.1907514450867054,0.76878612716763006]
[3,14.7,310,25,99,4.0999999999999996,1.28,300,1,1.73,2.3699421965317917,0.73988439306358389]
[3,14.7,310,26,1,1.36,1.36,100,0,1.36,1,1]
[3,15.6,310,26,50,1.47,1.1499999999999999,100,1,1.36,1.0808823529411764,0.84558823529411753]
[3,17.2,310,26,60,1.66,1.04,100,1,1.36,1.2205882352941175,0.76470588235294112]
[3,18.8,310,26,70,1.84,0.93,100,1,1.36,1.3529411764705881,0.68382352941176472]
[3,20.399999999999999,310,26,80,2.02,0.82,100,1,1.36,1.4852941176470587,0.6029411764705882]
[3,21.9,310,26,90,2.2000000000000002,0.72,100,1,1.36,1.6176470588235294,0.52941176470588225]
[3,23.2,310,26,99,2.35,0.63,100,1,1.36,1.7279411764705881,0.46323529411764702]
[3,10.199999999999999,310,26,1,1.69,1.69,200,0,1.69,1,1]
[3,12.6,310,26,50,2.25,1.46,200,1,1.69,1.3313609467455623,0.86390532544378695]
[3,14,310,26,60,2.56,1.38,200,1,1.69,1.5147928994082842,0.81656804733727806]
[3,15.3,310,26,70,2.86,1.31,200,1,1.69,1.6923076923076923,0.77514792899408291]
[3,16.600000000000001,310,26,80,3.16,1.23,200,1,1.69,1.8698224852071008,0.72781065088757402]
[3,17.899999999999999,310,26,90,3.47,1.1499999999999999,200,1,1.69,2.0532544378698225,0.68047337278106501]
[3,19,310,26,99,3.74,1.0900000000000001,200,1,1.69,2.2130177514792901,0.64497041420118351]
[3,8.1,310,26,1,1.8,1.8,300,0,1.8,1,1]
[3,10.4,310,26,50,2.59,1.61,300,1,1.8,1.4388888888888889,0.89444444444444449]
[3,11.4,310,26,60,2.95,1.55,300,1,1.8,1.6388888888888888,0.86111111111111116]
[3,12.5,310,26,70,3.32,1.5,300,1,1.8,1.8444444444444443,0.83333333333333326]
[3,13.5,310,26,80,3.68,1.44,300,1,1.8,2.0444444444444443,0.79999999999999993]
[3,14.6,310,26,90,4.04,1.38,300,1,1.8,2.2444444444444445,0.76666666666666661]
[3,15.5,310,26,99,4.37,1.32,300,1,1.8,2.4277777777777776,0.73333333333333339]
[3,15.2,310,27,1,1.42,1.42,100,0,1.42,1,1]
[3,16.399999999999999,310,27,50,1.56,1.18,100,1,1.42,1.0985915492957747,0.83098591549295775]
[3,18.100000000000001,310,27,60,1.76,1.06,100,1,1.42,1.23943661971831,0.74647887323943674]
[3,19.8,310,27,70,1.95,0.95,100,1,1.42,1.3732394366197183,0.66901408450704225]
[3,21.4,310,27,80,2.14,0.84,100,1,1.42,1.507042253521127,0.59154929577464788]
[3,22.9,310,27,90,2.3199999999999998,0.73,100,1,1.42,1.6338028169014085,0.5140845070422535]
[3,24.3,310,27,99,2.48,0.64,100,1,1.42,1.7464788732394367,0.45070422535211269]
[3,10.6,310,27,1,1.76,1.76,200,0,1.76,1,1]
[3,13.3,310,27,50,2.4,1.51,200,1,1.76,1.3636363636363635,0.85795454545454541]
[3,14.7,310,27,60,2.72,1.43,200,{"$f":"IF(F598<>G598,1,0)","v":1},1.76,{"$f":"F598/J598","v":1.5454545454545456},0.8125]
[3,16.100000000000001,310,27,70,3.05,1.34,200,1,1.76,1.7329545454545454,{"$f":"G599/J599","v":0.76136363636363635}]
[3,17.399999999999999,310,27,80,3.36,1.26,200,1,1.76,1.9090909090909089,0.71590909090909094]
[3,18.8,310,27,90,3.68,1.19,200,1,{"$f":"IF(F601/G601=1,F601,J600)","v":1.76},2.0909090909090908,0.67613636363636365]
[3,20,310,27,99,3.96,1.1100000000000001,200,1,1.76,2.25,0.63068181818181823]
[3,8.4,310,27,1,1.88,1.88,300,0,1.88,1,1]
[3,10.9,310,27,50,2.77,1.67,300,1,1.88,1.4734042553191491,0.88829787234042556]
[3,12,310,27,60,3.15,1.61,300,1,1.88,1.675531914893617,0.85638297872340441]
[3,13.1,310,27,70,3.53,1.54,300,1,1.88,1.8776595744680851,0.81914893617021278]
[3,14.2,310,27,80,3.92,1.48,300,1,1.88,2.0851063829787235,0.78723404255319152]
[3,15.3,310,27,90,4.3,1.42,300,1,1.88,2.2872340425531914,0.75531914893617025]
[3,16.3,310,27,99,4.6399999999999997,1.36,300,1,1.88,2.4680851063829787,0.72340425531914898]
[3,12.9,380,21,1,1.1599999999999999,1.1599999999999999,100,0,1.1599999999999999,1,1]
[3,12.9,380,21,50,1.1499999999999999,1.1499999999999999,100,0,1.1499999999999999,1,1]
[3,13.5,380,21,60,1.22,0.98,100,1,1.1499999999999999,1.0608695652173914,0.85217391304347834]
[3,14.8,380,21,70,1.37,0.87,100,1,1.1499999999999999,1.1913043478260872,0.75652173913043486]
[3,16,380,21,80,1.52,0.77,100,1,1.1499999999999999,1.3217391304347827,0.66956521739130437]
[3,17.3,380,21,90,1.66,0.66,100,1,1.1499999999999999,1.4434782608695653,0.57391304347826089]
[3,18.399999999999999,380,21,99,1.79,0.56999999999999995,100,1,1.1499999999999999,1.5565217391304349,0.49565217391304345]
[3,9.4,380,21,1,1.5,1.5,200,0,1.5,1,1]
[3,10.199999999999999,380,21,50,1.68,1.35,200,1,1.5,1.1199999999999999,0.9]
[3,11.3,380,21,60,1.93,1.27,200,1,1.5,1.2866666666666666,0.84666666666666668]
[3,12.4,380,21,70,2.1800000000000002,1.2,200,1,1.5,1.4533333333333334,0.79999999999999993]
[3,13.4,380,21,80,2.4300000000000002,1.1200000000000001,200,1,1.5,1.62,0.7466666666666667]
[3,14.5,380,21,90,2.68,1.04,200,1,1.5,1.7866666666666668,0.69333333333333336]
[3,15.4,380,21,99,2.9,0.98,200,1,1.5,1.9333333333333333,0.65333333333333332]
[3,7.6,380,21,1,1.62,1.62,300,0,1.62,1,1]
[3,8.6999999999999993,380,21,50,1.98,1.49,300,1,1.62,1.2222222222222221,0.91975308641975306]
[3,9.5,380,21,60,2.2799999999999998,1.43,300,1,1.62,1.4074074074074072,0.88271604938271597]
[3,10.4,380,21,70,2.58,1.37,300,1,1.62,1.5925925925925926,0.84567901234567899]
[3,11.2,380,21,80,2.88,1.31,300,1,1.62,1.7777777777777777,0.8086419753086419]
[3,12.1,380,21,90,3.18,1.25,300,1,1.62,1.962962962962963,0.77160493827160492]
[3,12.9,380,21,99,3.45,1.19,300,1,1.62,2.1296296296296298,0.73456790123456783]
[3,13.5,380,22,1,1.22,1.22,100,0,1.22,1,1]
[3,13.5,380,22,50,1.22,1.22,100,0,1.22,1,1]
[3,14.3,380,22,60,1.31,1.01,100,1,1.22,1.0737704918032787,0.82786885245901642]
[3,15.6,380,22,70,1.47,0.9,100,1,1.22,1.2049180327868851,0.73770491803278693]
[3,17,380,22,80,1.63,0.79,100,1,1.22,1.3360655737704918,0.64754098360655743]
[3,18.3,380,22,90,1.78,0.68,100,1,1.22,1.459016393442623,0.55737704918032793]
[3,19.399999999999999,380,22,99,1.91,0.59,100,1,1.22,1.5655737704918034,0.48360655737704916]
[3,9.8000000000000007,380,22,1,1.58,1.58,200,0,1.58,1,1]
[3,10.8,380,22,50,1.83,1.41,200,1,1.58,1.1582278481012658,0.89240506329113911]
[3,12,380,22,60,2.09,1.33,200,1,1.58,1.3227848101265822,0.84177215189873422]
[3,13.1,380,22,70,2.35,1.25,200,1,1.58,1.4873417721518987,0.79113924050632911]
[3,14.2,380,22,80,2.62,1.1599999999999999,200,1,1.58,1.6582278481012658,0.73417721518987333]
[3,15.3,380,22,90,2.87,1.08,200,1,1.58,1.8164556962025316,0.68354430379746833]
[3,16.3,380,22,99,3.11,1.01,200,1,1.58,1.9683544303797467,0.63924050632911389]
[3,7.9,380,22,1,1.71,1.71,300,0,1.71,1,1]
[3,9.1,380,22,50,2.15,1.56,300,1,1.71,1.2573099415204678,0.91228070175438603]
[3,10.1,380,22,60,2.4700000000000002,1.49,300,1,1.71,1.4444444444444446,0.87134502923976609]
[3,11,380,22,70,2.79,1.43,300,1,1.71,1.631578947368421,0.83625730994152048]
[3,11.9,380,22,80,3.11,1.37,300,1,1.71,1.8187134502923976,0.80116959064327498]
[3,12.8,380,22,90,3.42,1.3,300,1,1.71,2,0.76023391812865504]
[3,13.6,380,22,99,3.71,1.25,300,1,1.71,2.1695906432748537,0.73099415204678364]
[3,14,380,23,1,1.29,1.29,100,0,1.29,1,1]
[3,13.7,380,23,50,1.24,1.17,100,1,1.29,0.96124031007751931,0.90697674418604646]
[3,15.1,380,23,60,1.41,1.05,100,1,1.29,1.0930232558139534,0.81395348837209303]
[3,16.5,380,23,70,1.58,0.93,100,1,1.29,1.2248062015503876,0.72093023255813959]
[3,17.899999999999999,380,23,80,1.74,0.81,100,1,1.29,1.3488372093023255,0.62790697674418605]
[3,19.3,380,23,90,1.9,0.7,100,1,1.29,1.4728682170542635,0.54263565891472865]
[3,20.5,380,23,99,2.0299999999999998,0.61,100,1,1.29,1.5736434108527131,0.47286821705426352]
[3,10.1,380,23,1,1.66,1.66,200,0,1.66,1,1]
[3,11.4,380,23,50,1.97,1.46,200,1,1.66,1.1867469879518073,0.87951807228915668]
[3,12.7,380,23,60,2.25,1.38,200,1,1.66,1.3554216867469879,0.83132530120481929]
[3,13.9,380,23,70,2.5299999999999998,1.29,200,{"$f":"IF(F662<>G662,1,0)","v":1},1.66,{"$f":"F662/J662","v":1.5240963855421685},0.77710843373493976]
[3,15,380,23,80,2.81,1.2,200,1,1.66,1.6927710843373496,{"$f":"G663/J663","v":0.72289156626506024}]
[3,16.2,380,23,90,3.08,1.1200000000000001,200,1,1.66,1.8554216867469882,0.67469879518072295]
[3,17.3,380,23,99,3.32,1.04,200,1,{"$f":"IF(F665/G665=1,F665,J664)","v":1.66},2,0.62650602409638556]
[3,8.1,380,23,1,1.8,1.8,300,0,1.8,1,1]
[3,9.6,380,23,50,2.33,1.62,300,1,1.8,1.2944444444444445,0.9]
[3,10.6,380,23,60,2.66,1.55,300,1,1.8,1.4777777777777779,0.86111111111111116]
[3,11.6,380,23,70,3,1.49,300,1,1.8,1.6666666666666665,0.82777777777777772]
[3,12.5,380,23,80,3.34,1.42,300,1,1.8,1.8555555555555554,0.78888888888888886]
[3,13.5,380,23,90,3.67,1.35,300,1,1.8,2.0388888888888888,0.75]
[3,14.4,380,23,99,3.97,1.29,300,1,1.8,2.2055555555555557,0.71666666666666667]
[3,14.6,380,24,1,1.35,1.35,100,0,1.35,1,1]
[3,14.4,380,24,50,1.33,1.2,100,1,1.35,0.98518518518518516,0.88888888888888884]
[3,16,380,24,60,1.51,1.08,100,1,1.35,1.1185185185185185,0.8]
[3,17.5,380,24,70,1.68,0.95,100,1,1.35,1.2444444444444442,0.70370370370370361]
[3,18.899999999999999,380,24,80,1.85,0.83,100,1,1.35,1.3703703703703702,0.6148148148148147]
[3,20.3,380,24,90,2.02,0.72,100,1,1.35,1.4962962962962962,0.53333333333333333]
[3,21.5,380,24,99,2.16,0.62,100,1,1.35,1.6,0.4592592592592592]
[3,10.5,380,24,1,1.74,1.74,200,0,1.74,1,1]
[3,12.1,380,24,50,2.12,1.52,200,1,1.74,1.2183908045977012,0.87356321839080464]
[3,13.4,380,24,60,2.42,1.43,200,1,1.74,1.3908045977011494,0.82183908045977005]
[3,14.6,380,24,70,2.71,1.34,200,1,1.74,1.5574712643678161,0.77011494252873569]
[3,15.9,380,24,80,3,1.25,200,1,1.74,1.7241379310344829,0.7183908045977011]
[3,17.100000000000001,380,24,90,3.29,1.1599999999999999,200,1,1.74,1.8908045977011494,0.66666666666666663]
[3,18.2,380,24,99,3.54,1.08,200,1,1.74,2.0344827586206895,0.62068965517241381]
[3,8.4,380,24,1,1.88,1.88,300,0,1.88,1,1]
[3,10.199999999999999,380,24,50,2.5,1.69,300,1,1.88,1.3297872340425532,0.89893617021276595]
[3,11.2,380,24,60,2.86,1.62,300,1,1.88,1.5212765957446808,0.86170212765957455]
[3,12.2,380,24,70,3.22,1.54,300,1,1.88,1.7127659574468088,0.81914893617021278]
[3,13.2,380,24,80,3.58,1.47,300,1,1.88,1.9042553191489364,0.78191489361702127]
[3,14.2,380,24,90,3.93,1.4,300,1,1.88,2.0904255319148937,0.74468085106382975]
[3,15.1,380,24,99,4.25,1.34,300,1,1.88,2.2606382978723407,0.7127659574468086]
[3,15.2,380,25,1,1.42,1.42,100,0,1.42,1,1]
[3,15.2,380,25,50,1.42,1.24,100,1,1.42,1,0.87323943661971837]
[3,16.8,380,25,60,1.61,1.1100000000000001,100,1,1.42,1.1338028169014085,0.78169014084507049]
[3,18.399999999999999,380,25,70,1.79,0.98,100,1,1.42,1.2605633802816902,0.6901408450704225]
[3,19.899999999999999,380,25,80,1.97,0.85,100,1,1.42,1.387323943661972,0.59859154929577463]
[3,21.3,380,25,90,2.14,0.73,100,1,1.42,1.507042253521127,0.5140845070422535]
[3,22.6,380,25,99,2.2799999999999998,0.63,100,1,1.42,1.6056338028169013,0.44366197183098594]
[3,10.8,380,25,1,1.82,1.82,200,0,1.82,1,1]
[3,12.7,380,25,50,2.27,1.57,200,1,1.82,1.2472527472527473,0.86263736263736268]
[3,14.1,380,25,60,2.59,1.47,200,1,1.82,1.4230769230769229,0.8076923076923076]
[3,15.4,380,25,70,2.9,1.38,200,1,1.82,1.5934065934065933,0.75824175824175821]
[3,16.7,380,25,80,3.2,1.29,200,1,1.82,1.7582417582417582,0.70879120879120883]
[3,18,380,25,90,3.5,1.19,200,1,1.82,1.9230769230769229,0.65384615384615374]
[3,19.2,380,25,99,3.77,1.1100000000000001,200,1,1.82,2.0714285714285712,0.60989010989010994]
[3,8.6,380,25,1,1.97,1.97,300,0,1.97,1,1]
[3,10.7,380,25,50,2.69,1.75,300,1,1.97,1.3654822335025381,0.8883248730964467]
[3,11.8,380,25,60,3.07,1.68,300,1,1.97,1.5583756345177664,0.85279187817258884]
[3,12.9,380,25,70,3.44,1.6,300,1,1.97,1.7461928934010151,0.81218274111675137]
[3,13.9,380,25,80,3.82,1.52,300,1,1.97,1.9390862944162437,0.77157360406091369]
[3,15,380,25,90,4.2,1.45,300,1,1.97,2.1319796954314723,0.73604060913705582]
[3,16,380,25,99,4.53,1.38,300,1,1.97,2.2994923857868024,0.70050761421319796]
[3,15.7,380,26,1,1.48,1.48,100,0,1.48,1,1]
[3,16,380,26,50,1.52,1.27,100,1,1.48,1.027027027027027,0.85810810810810811]
[3,17.7,380,26,60,1.71,1.1399999999999999,100,1,1.48,1.1554054054054055,0.77027027027027017]
[3,19.3,380,26,70,1.9,1,100,1,1.48,1.2837837837837838,0.67567567567567566]
[3,20.9,380,26,80,2.08,0.87,100,1,1.48,1.4054054054054055,0.58783783783783783]
[3,22.4,380,26,90,2.2599999999999998,0.75,100,1,1.48,1.527027027027027,0.5067567567567568]
[3,23.7,380,26,99,2.41,0.64,100,1,1.48,1.6283783783783785,0.43243243243243246]
[3,11.2,380,26,1,1.91,1.91,200,0,1.91,1,1]
[3,13.4,380,26,50,2.4300000000000002,1.62,200,1,1.91,1.2722513089005236,0.84816753926701582]
[3,14.8,380,26,60,2.76,1.52,200,1,1.91,1.4450261780104712,0.79581151832460739]
[3,16.2,380,26,70,3.08,1.42,200,1,1.91,1.6125654450261782,0.74345549738219896]
[3,17.600000000000001,380,26,80,3.41,1.32,200,{"$f":"IF(F726<>G726,1,0)","v":1},1.91,{"$f":"F726/J726","v":1.7853403141361257},0.69109947643979064]
[3,19,380,26,90,3.72,1.22,200,1,1.91,1.9476439790575919,{"$f":"G727/J727","v":0.63874345549738221}]
[3,20.2,380,26,99,4,1.1299999999999999,200,1,1.91,2.0942408376963351,0.59162303664921467]
[3,8.9,380,26,1,2.06,2.06,300,0,{"$f":"IF(F729/G729=1,F729,J728)","v":2.06},1,1]
[3,11.2,380,26,50,2.88,1.81,300,1,2.06,1.3980582524271843,0.87864077669902918]
[3,12.4,380,26,60,3.28,1.73,300,1,2.06,1.5922330097087378,0.83980582524271841]
[3,13.5,380,26,70,3.68,1.65,300,1,2.06,1.7864077669902914,0.80097087378640774]
[3,14.7,380,26,80,4.07,1.57,300,1,2.06,1.9757281553398058,0.76213592233009708]
[3,15.8,380,26,90,4.47,1.49,300,1,2.06,2.1699029126213589,0.72330097087378642]
[3,16.8,380,26,99,4.83,1.42,300,1,2.06,2.3446601941747574,0.68932038834951448]
[3,16.3,380,27,1,1.55,1.55,100,0,1.55,1,1]
[3,16.899999999999999,380,27,50,1.62,1.31,100,1,1.55,1.0451612903225806,0.84516129032258069]
[3,18.600000000000001,380,27,60,1.82,1.1599999999999999,100,1,1.55,1.1741935483870969,0.74838709677419346]
[3,20.3,380,27,70,2.0099999999999998,1.02,100,1,1.55,1.296774193548387,0.65806451612903227]
[3,21.9,380,27,80,2.2000000000000002,0.89,100,1,1.55,1.4193548387096775,0.5741935483870968]
[3,23.5,380,27,90,2.38,0.76,100,1,1.55,1.5354838709677419,0.49032258064516127]
[3,24.8,380,27,99,2.54,0.64,100,1,1.55,1.6387096774193548,0.41290322580645161]
[3,11.5,380,27,1,1.99,1.99,200,0,1.99,1,1]
[3,14.1,380,27,50,2.59,1.67,200,1,1.99,1.3015075376884422,0.83919597989949746]
[3,15.6,380,27,60,2.94,1.57,200,1,1.99,1.4773869346733668,0.78894472361809054]
[3,17.100000000000001,380,27,70,3.28,1.46,200,1,1.99,1.6482412060301506,0.73366834170854267]
[3,18.5,380,27,80,3.62,1.35,200,1,1.99,1.8190954773869348,0.67839195979899503]
[3,20,380,27,90,3.95,1.25,200,1,1.99,1.9849246231155779,0.62814070351758799]
[3,21.2,380,27,99,4.24,1.1599999999999999,200,1,1.99,2.1306532663316582,0.58291457286432158]
[3,9.1,380,27,1,2.15,2.15,300,0,2.15,1,1]
[3,11.8,380,27,50,3.07,1.87,300,1,2.15,1.4279069767441861,0.86976744186046517]
[3,13,380,27,60,3.49,1.79,300,1,2.15,1.6232558139534885,0.83255813953488378]
[3,14.2,380,27,70,3.92,1.7,300,1,2.15,1.8232558139534885,0.79069767441860461]
[3,15.4,380,27,80,4.33,1.62,300,1,2.15,2.0139534883720933,0.75348837209302333]
[3,16.600000000000001,380,27,90,4.75,1.54,300,1,2.15,2.2093023255813953,0.71627906976744193]
[3,17.7,380,27,99,5.13,1.46,300,1,2.15,2.386046511627907,0.67906976744186043]
[4,8.4,100,21,1,0.51,0.51,100,0,0.51,1,1]
[4,9.3000000000000007,100,21,50,0.61,0.47,100,1,0.51,1.196078431372549,0.92156862745098034]
[4,10.1,100,21,60,0.72,0.45,100,1,0.51,1.4117647058823528,0.88235294117647056]
[4,11,100,21,70,0.82,0.44,100,1,0.51,1.6078431372549018,0.86274509803921573]
[4,11.9,100,21,80,0.92,0.43,100,1,0.51,1.803921568627451,0.84313725490196079]
[4,12.7,100,21,90,1.02,0.41,100,1,0.51,2,0.8039215686274509]
[4,13.5,100,21,99,1.1100000000000001,0.4,100,1,0.51,2.1764705882352944,0.78431372549019607]
[4,6.3,100,21,1,0.54,0.54,200,0,0.54,1,1]
[4,7.1,100,21,50,0.72,0.52,200,1,0.54,1.3333333333333333,0.96296296296296291]
[4,7.6,100,21,60,0.83,0.51,200,1,0.54,1.5370370370370368,0.94444444444444442]
[4,8.1,100,21,70,0.95,0.51,200,1,0.54,1.7592592592592591,0.94444444444444442]
[4,8.6,100,21,80,1.07,0.5,200,1,0.54,1.9814814814814814,0.92592592592592582]
[4,9.1,100,21,90,1.19,0.49,200,1,0.54,2.2037037037037033,0.90740740740740733]
[4,9.5,100,21,99,1.29,0.49,200,1,0.54,2.3888888888888888,0.90740740740740733]
[4,5.6,100,21,1,0.55000000000000004,0.55000000000000004,300,0,0.55000000000000004,1,1]
[4,6.1,100,21,50,0.74,0.53,300,1,0.55000000000000004,1.3454545454545452,0.96363636363636362]
[4,6.5,100,21,60,0.86,0.53,300,1,0.55000000000000004,1.5636363636363635,0.96363636363636362]
[4,6.8,100,21,70,0.98,0.52,300,1,0.55000000000000004,1.7818181818181817,0.94545454545454544]
[4,7.2,100,21,80,1.1000000000000001,0.52,300,1,0.55000000000000004,2,0.94545454545454544]
[4,7.5,100,21,90,1.23,0.51,300,1,0.55000000000000004,2.2363636363636363,0.92727272727272725]
[4,7.8,100,21,99,1.34,0.51,300,1,0.55000000000000004,2.4363636363636365,0.92727272727272725]
[4,8.6,100,22,1,0.54,0.54,100,0,0.54,1,1]
[4,9.6999999999999993,100,22,50,0.67,0.49,100,1,0.54,1.2407407407407407,0.90740740740740733]
[4,10.7,100,22,60,0.78,0.48,100,1,0.54,1.4444444444444444,0.88888888888888884]
[4,11.6,100,22,70,0.89,0.46,100,1,0.54,1.6481481481481481,0.85185185185185186]
[4,12.5,100,22,80,0.99,0.45,100,1,0.54,1.8333333333333333,0.83333333333333326]
[4,13.4,100,22,90,1.1000000000000001,0.43,100,1,0.54,2.0370370370370372,0.79629629629629628]
[4,14.3,100,22,99,1.2,0.42,100,1,0.54,2.2222222222222219,0.77777777777777768]
[4,6.4,100,22,1,0.56999999999999995,0.56999999999999995,200,0,0.56999999999999995,1,1]
[4,7.3,100,22,50,0.78,0.55000000000000004,200,1,0.56999999999999995,1.3684210526315792,0.9649122807017545]
[4,7.9,100,22,60,0.91,0.54,200,1,0.56999999999999995,1.5964912280701757,0.94736842105263175]
[4,8.4,100,22,70,1.03,0.53,200,1,0.56999999999999995,1.8070175438596494,0.92982456140350889]
[4,9,100,22,80,1.1599999999999999,0.53,200,1,0.56999999999999995,2.0350877192982457,0.92982456140350889]
[4,9.5,100,22,90,1.28,0.52,200,{"$f":"IF(F790<>G790,1,0)","v":1},0.56999999999999995,{"$f":"F790/J790","v":2.2456140350877196},0.91228070175438603]
[4,10,100,22,99,1.39,0.51,200,1,0.56999999999999995,2.4385964912280702,{"$f":"G791/J791","v":0.89473684210526327}]
[4,5.6,100,22,1,0.57999999999999996,0.57999999999999996,300,0,0.57999999999999996,1,1]
[4,6.3,100,22,50,0.81,0.56000000000000005,300,1,{"$f":"IF(F793/G793=1,F793,J792)","v":0.57999999999999996},1.3965517241379313,0.9655172413793105]
[4,6.7,100,22,60,0.94,0.56000000000000005,300,1,0.57999999999999996,1.6206896551724139,0.9655172413793105]
[4,7,100,22,70,1.07,0.55000000000000004,300,1,0.57999999999999996,1.8448275862068968,0.94827586206896564]
[4,7.4,100,22,80,1.19,0.55000000000000004,300,1,0.57999999999999996,2.0517241379310347,0.94827586206896564]
[4,7.8,100,22,90,1.32,0.54,300,1,0.57999999999999996,2.2758620689655173,0.93103448275862077]
[4,8.1,100,22,99,1.44,0.54,300,1,0.57999999999999996,2.4827586206896552,0.93103448275862077]
[4,8.9,100,23,1,0.56999999999999995,0.56999999999999995,100,0,0.56999999999999995,1,1]
[4,10.3,100,23,50,0.73,0.52,100,1,0.56999999999999995,1.2807017543859649,0.91228070175438603]
[4,11.2,100,23,60,0.84,0.5,100,1,0.56999999999999995,1.4736842105263159,0.87719298245614041]
[4,12.2,100,23,70,0.96,0.49,100,1,0.56999999999999995,1.6842105263157896,0.85964912280701755]
[4,13.2,100,23,80,1.07,0.47,100,1,0.56999999999999995,1.8771929824561406,0.82456140350877194]
[4,14.2,100,23,90,1.18,0.46,100,1,0.56999999999999995,2.0701754385964914,0.80701754385964919]
[4,15,100,23,99,1.29,0.44,100,1,0.56999999999999995,2.2631578947368425,0.77192982456140358]
[4,6.6,100,23,1,0.6,0.6,200,0,0.6,1,1]
[4,7.6,100,23,50,0.85,0.56999999999999995,200,1,0.6,1.4166666666666667,0.95]
[4,8.1999999999999993,100,23,60,0.98,0.56999999999999995,200,1,0.6,1.6333333333333333,0.95]
[4,8.8000000000000007,100,23,70,1.1100000000000001,0.56000000000000005,200,1,0.6,1.8500000000000003,0.93333333333333346]
[4,9.3000000000000007,100,23,80,1.25,0.55000000000000004,200,1,0.6,2.0833333333333335,0.91666666666666674]
[4,9.9,100,23,90,1.38,0.55000000000000004,200,1,0.6,2.2999999999999998,0.91666666666666674]
[4,10.4,100,23,99,1.5,0.54,200,1,0.6,2.5,0.90000000000000013]
[4,5.7,100,23,1,0.61,0.61,300,0,0.61,1,1]
[4,6.5,100,23,50,0.88,0.59,300,1,0.61,1.4426229508196722,0.96721311475409832]
[4,6.9,100,23,60,1.01,0.57999999999999996,300,1,0.61,1.6557377049180328,0.95081967213114749]
[4,7.3,100,23,70,1.1499999999999999,0.57999999999999996,300,1,0.61,1.8852459016393441,0.95081967213114749]
[4,7.7,100,23,80,1.29,0.56999999999999995,300,1,0.61,2.1147540983606556,0.93442622950819665]
[4,8.1,100,23,90,1.42,0.56999999999999995,300,1,0.61,2.3278688524590163,0.93442622950819665]
[4,8.4,100,23,99,1.55,0.56000000000000005,300,1,0.61,2.540983606557377,0.91803278688524603]
[4,9.1,100,24,1,0.59,0.59,100,0,0.59,1,1]
[4,10.8,100,24,50,0.79,0.54,100,1,0.59,1.3389830508474578,0.91525423728813571]
[4,11.8,100,24,60,0.91,0.52,100,1,0.59,1.5423728813559323,0.88135593220338992]
[4,12.8,100,24,70,1.03,0.51,100,1,0.59,1.745762711864407,0.86440677966101698]
[4,13.9,100,24,80,1.1499999999999999,0.49,100,1,0.59,1.9491525423728813,0.83050847457627119]
[4,14.9,100,24,90,1.27,0.47,100,1,0.59,2.152542372881356,0.79661016949152541]
[4,15.8,100,24,99,1.38,0.46,100,1,0.59,2.3389830508474576,0.77966101694915257]
[4,6.7,100,24,1,0.63,0.63,200,0,0.63,1,1]
[4,7.9,100,24,50,0.92,0.6,200,1,0.63,1.4603174603174605,0.95238095238095233]
[4,8.5,100,24,60,1.06,0.59,200,1,0.63,1.6825396825396826,0.9365079365079364]
[4,9.1,100,24,70,1.2,0.59,200,1,0.63,1.9047619047619047,0.9365079365079364]
[4,9.6999999999999993,100,24,80,1.34,0.57999999999999996,200,1,0.63,2.126984126984127,0.92063492063492058]
[4,10.3,100,24,90,1.48,0.56999999999999995,200,1,0.63,2.3492063492063493,0.90476190476190466]
[4,10.9,100,24,99,1.61,0.56999999999999995,200,1,0.63,2.5555555555555558,0.90476190476190466]
[4,5.8,100,24,1,0.64,0.64,300,0,0.64,1,1]
[4,6.7,100,24,50,0.95,0.62,300,1,0.64,1.484375,0.96875]
[4,7.1,100,24,60,1.0900000000000001,0.61,300,1,0.64,1.703125,0.953125]
[4,7.5,100,24,70,1.24,0.61,300,1,0.64,1.9375,0.953125]
[4,8,100,24,80,1.38,0.6,300,1,0.64,2.15625,0.9375]
[4,8.4,100,24,90,1.53,0.6,300,1,0.64,2.390625,0.9375]
[4,8.6999999999999993,100,24,99,1.66,0.59,300,1,0.64,2.59375,0.92187499999999989]
[4,9.3000000000000007,100,25,1,0.62,0.62,100,0,0.62,1,1]
[4,11.3,100,25,50,0.85,0.56000000000000005,100,1,0.62,1.3709677419354838,0.90322580645161299]
[4,12.4,100,25,60,0.98,0.54,100,1,0.62,1.5806451612903225,0.87096774193548399]
[4,13.5,100,25,70,1.1100000000000001,0.53,100,1,0.62,1.7903225806451615,0.85483870967741937]
[4,14.6,100,25,80,1.23,0.51,100,1,0.62,1.9838709677419355,0.82258064516129037]
[4,15.7,100,25,90,1.36,0.49,100,1,0.62,2.1935483870967745,0.79032258064516125]
[4,16.7,100,25,99,1.48,0.48,100,1,0.62,2.3870967741935485,0.77419354838709675]
[4,6.8,100,25,1,0.66,0.66,200,0,0.66,1,1]
[4,8.1999999999999993,100,25,50,0.99,0.63,200,1,0.66,1.5,0.95454545454545447]
[4,8.9,100,25,60,1.1399999999999999,0.62,200,1,0.66,1.7272727272727271,0.93939393939393934]
[4,9.5,100,25,70,1.29,0.61,200,1,0.66,1.9545454545454546,0.9242424242424242]
[4,10.199999999999999,100,25,80,1.43,0.6,200,1,0.66,2.1666666666666665,0.90909090909090906]
[4,10.8,100,25,90,1.58,0.6,200,1,0.66,2.393939393939394,0.90909090909090906]
[4,11.4,100,25,99,1.72,0.59,200,{"$f":"IF(F854<>G854,1,0)","v":1},0.66,{"$f":"F854/J854","v":2.606060606060606},0.89393939393939381]
[4,5.9,100,25,1,0.67,0.67,300,0,0.67,1,{"$f":"G855/J855","v":1}]
[4,6.9,100,25,50,1.02,0.64,300,1,0.67,1.5223880597014925,0.95522388059701491]
[4,7.4,100,25,60,1.17,0.64,300,1,{"$f":"IF(F857/G857=1,F857,J856)","v":0.67},1.7462686567164176,0.95522388059701491]
[4,7.8,100,25,70,1.33,0.63,300,1,0.67,1.9850746268656716,0.94029850746268651]
[4,8.1999999999999993,100,25,80,1.48,0.63,300,1,0.67,2.2089552238805967,0.94029850746268651]
[4,8.6999999999999993,100,25,90,1.64,0.62,300,1,0.67,2.4477611940298503,0.9253731343283581]
[4,9.1,100,25,99,1.78,0.62,300,1,0.67,2.6567164179104474,0.9253731343283581]
[4,9.6,100,26,1,0.65,0.65,100,0,0.65,1,1]
[4,11.8,100,26,50,0.91,0.57999999999999996,100,1,0.65,1.4,0.89230769230769225]
[4,13,100,26,60,1.05,0.56999999999999995,100,1,0.65,1.6153846153846154,0.87692307692307681]
[4,14.2,100,26,70,1.18,0.55000000000000004,100,1,0.65,1.8153846153846152,0.84615384615384615]
[4,15.3,100,26,80,1.32,0.53,100,1,0.65,2.0307692307692307,0.81538461538461537]
[4,16.5,100,26,90,1.45,0.51,100,1,0.65,2.2307692307692308,0.7846153846153846]
[4,17.5,100,26,99,1.57,0.5,100,1,0.65,2.4153846153846152,0.76923076923076916]
[4,6.9,100,26,1,0.69,0.69,200,0,0.69,1,1]
[4,8.5,100,26,50,1.06,0.65,200,1,0.69,1.5362318840579712,0.94202898550724645]
[4,9.1999999999999993,100,26,60,1.22,0.65,200,1,0.69,1.7681159420289856,0.94202898550724645]
[4,9.9,100,26,70,1.38,0.64,200,1,0.69,2,0.92753623188405809]
[4,10.6,100,26,80,1.54,0.63,200,1,0.69,2.2318840579710146,0.91304347826086962]
[4,11.3,100,26,90,1.69,0.62,200,1,0.69,2.4492753623188408,0.89855072463768126]
[4,11.9,100,26,99,1.84,0.61,200,1,0.69,2.666666666666667,0.88405797101449279]
[4,6,100,26,1,0.7,0.7,300,0,0.7,1,1]
[4,7.1,100,26,50,1.1000000000000001,0.67,300,1,0.7,1.5714285714285716,0.9571428571428573]
[4,7.6,100,26,60,1.26,0.67,300,1,0.7,1.8,0.9571428571428573]
[4,8.1,100,26,70,1.42,0.66,300,1,0.7,2.0285714285714285,0.94285714285714295]
[4,8.5,100,26,80,1.58,0.65,300,1,0.7,2.2571428571428576,0.92857142857142871]
[4,9,100,26,90,1.75,0.65,300,1,0.7,2.5,0.92857142857142871]
[4,9.4,100,26,99,1.89,0.64,300,1,0.7,2.7,0.91428571428571437]
[4,9.8000000000000007,100,27,1,0.68,0.68,100,0,0.68,1,1]
[4,12.4,100,27,50,0.98,0.61,100,1,0.68,1.4411764705882351,0.89705882352941169]
[4,13.6,100,27,60,1.1200000000000001,0.59,100,1,0.68,1.6470588235294119,0.86764705882352933]
[4,14.9,100,27,70,1.26,0.56999999999999995,100,1,0.68,1.8529411764705881,0.83823529411764697]
[4,16.100000000000001,100,27,80,1.41,0.55000000000000004,100,1,0.68,2.0735294117647056,0.80882352941176472]
[4,17.3,100,27,90,1.55,0.53,100,1,0.68,2.2794117647058822,0.77941176470588236]
[4,18.399999999999999,100,27,99,1.68,0.51,100,1,0.68,2.4705882352941173,0.75]
[4,7.1,100,27,1,0.72,0.72,200,0,0.72,1,1]
[4,8.9,100,27,50,1.1399999999999999,0.68,200,1,0.72,1.5833333333333333,0.94444444444444453]
[4,9.6,100,27,60,1.3,0.67,200,1,0.72,1.8055555555555556,0.93055555555555569]
[4,10.3,100,27,70,1.47,0.66,200,1,0.72,2.0416666666666665,0.91666666666666674]
[4,11,100,27,80,1.64,0.65,200,1,0.72,2.2777777777777777,0.90277777777777779]
[4,11.7,100,27,90,1.81,0.65,200,1,0.72,2.5138888888888888,0.90277777777777779]
[4,12.4,100,27,99,1.96,0.64,200,1,0.72,2.7222222222222223,0.88888888888888895]
[4,6.1,100,27,1,0.73,0.73,300,0,0.73,1,1]
[4,7.3,100,27,50,1.17,0.7,300,1,0.73,1.6027397260273972,0.95890410958904104]
[4,7.8,100,27,60,1.35,0.69,300,1,0.73,1.8493150684931507,0.9452054794520548]
[4,8.3000000000000007,100,27,70,1.52,0.69,300,1,0.73,2.0821917808219177,0.9452054794520548]
[4,8.8000000000000007,100,27,80,1.69,0.68,300,1,0.73,2.3150684931506849,0.93150684931506855]
[4,9.3000000000000007,100,27,90,1.86,0.67,300,1,0.73,2.5479452054794525,0.91780821917808231]
[4,9.8000000000000007,100,27,99,2.02,0.67,300,1,0.73,2.7671232876712328,0.91780821917808231]
[4,10.3,170,21,1,0.74,0.74,100,0,0.74,1,1]
[4,10.8,170,21,50,0.79,0.66,100,1,0.74,1.0675675675675675,0.891891891891892]
[4,11.9,170,21,60,0.92,0.63,100,1,0.74,1.2432432432432432,0.85135135135135132]
[4,13,170,21,70,1.05,0.59,100,1,0.74,1.4189189189189191,0.79729729729729726]
[4,14.1,170,21,80,1.17,0.55000000000000004,100,1,0.74,1.5810810810810809,0.74324324324324331]
[4,15.1,170,21,90,1.3,0.52,100,1,0.74,1.7567567567567568,0.70270270270270274]
[4,16.100000000000001,170,21,99,1.41,0.48,100,1,0.74,1.9054054054054053,0.64864864864864868]
[4,7.6,170,21,1,0.83,0.83,200,0,0.83,1,1]
[4,8.5,170,21,50,1.04,0.78,200,1,0.83,1.2530120481927711,0.93975903614457834]
[4,9.1999999999999993,170,21,60,1.22,0.76,200,1,0.83,1.4698795180722892,0.9156626506024097]
[4,10,170,21,70,1.39,0.74,200,1,0.83,1.6746987951807228,0.89156626506024095]
[4,10.7,170,21,80,1.56,0.72,200,1,0.83,1.8795180722891567,0.86746987951807231]
[4,11.4,170,21,90,1.73,0.7,200,1,0.83,2.0843373493975905,0.84337349397590355]
[4,12.1,170,21,99,1.89,0.68,200,1,0.83,2.2771084337349397,0.81927710843373502]
[4,6.5,170,21,1,0.86,0.86,300,{"$f":"IF(F918<>G918,1,0)","v":0},0.86,{"$f":"F918/J918","v":1},1]
[4,7.2,170,21,50,1.1299999999999999,0.82,300,1,0.86,1.3139534883720929,{"$f":"G919/J919","v":0.95348837209302317}]
[4,7.8,170,21,60,1.31,0.81,300,1,0.86,1.5232558139534884,0.94186046511627919]
[4,8.3000000000000007,170,21,70,1.5,0.8,300,1,{"$f":"IF(F921/G921=1,F921,J920)","v":0.86},1.7441860465116279,0.93023255813953498]
[4,8.8000000000000007,170,21,80,1.68,0.78,300,1,0.86,1.9534883720930232,0.90697674418604657]
[4,9.3000000000000007,170,21,90,1.87,0.77,300,1,0.86,2.1744186046511631,0.89534883720930236]
[4,9.8000000000000007,170,21,99,2.04,0.75,300,1,0.86,2.3720930232558142,0.87209302325581395]
[4,10.7,170,22,1,0.78,0.78,100,0,0.78,1,1]
[4,11.4,170,22,50,0.86,0.69,100,1,0.78,1.1025641025641024,0.88461538461538447]
[4,12.6,170,22,60,1,0.65,100,1,0.78,1.2820512820512819,0.83333333333333337]
[4,13.7,170,22,70,1.1299999999999999,0.61,100,1,0.78,1.4487179487179485,0.78205128205128205]
[4,14.9,170,22,80,1.27,0.57999999999999996,100,1,0.78,1.6282051282051282,0.7435897435897435]
[4,16,170,22,90,1.4,0.54,100,1,0.78,1.7948717948717947,0.69230769230769229]
[4,17,170,22,99,1.52,0.5,100,1,0.78,1.9487179487179487,0.64102564102564097]
[4,7.8,170,22,1,0.88,0.88,200,0,0.88,1,1]
[4,8.9,170,22,50,1.1399999999999999,0.82,200,1,0.88,1.2954545454545454,0.93181818181818177]
[4,9.6999999999999993,170,22,60,1.32,0.8,200,1,0.88,1.5,0.90909090909090917]
[4,10.5,170,22,70,1.51,0.78,200,1,0.88,1.7159090909090908,0.88636363636363635]
[4,11.2,170,22,80,1.69,0.76,200,1,0.88,1.9204545454545454,0.86363636363636365]
[4,12,170,22,90,1.87,0.74,200,1,0.88,2.125,0.84090909090909094]
[4,12.7,170,22,99,2.0299999999999998,0.72,200,1,0.88,2.3068181818181817,0.81818181818181812]
[4,6.6,170,22,1,0.91,0.91,300,0,0.91,1,1]
[4,7.5,170,22,50,1.23,0.87,300,1,0.91,1.3516483516483515,0.95604395604395598]
[4,8.1,170,22,60,1.43,0.85,300,1,0.91,1.5714285714285714,0.93406593406593397]
[4,8.6,170,22,70,1.63,0.84,300,1,0.91,1.7912087912087911,0.92307692307692302]
[4,9.1999999999999993,170,22,80,1.82,0.82,300,1,0.91,2,0.90109890109890101]
[4,9.8000000000000007,170,22,90,2.02,0.81,300,1,0.91,2.2197802197802199,0.89010989010989017]
[4,10.3,170,22,99,2.2000000000000002,0.79,300,1,0.91,2.4175824175824179,0.86813186813186816]
[4,11.1,170,23,1,0.82,0.82,100,0,0.82,1,1]
[4,12,170,23,50,0.94,0.72,100,1,0.82,1.1463414634146341,0.87804878048780488]
[4,13.3,170,23,60,1.08,0.68,100,1,0.82,1.3170731707317074,0.8292682926829269]
[4,14.5,170,23,70,1.22,0.64,100,1,0.82,1.4878048780487805,0.78048780487804881]
[4,15.7,170,23,80,1.37,0.6,100,1,0.82,1.6707317073170733,0.73170731707317072]
[4,16.899999999999999,170,23,90,1.5,0.56000000000000005,100,1,0.82,1.8292682926829269,0.68292682926829273]
[4,18,170,23,99,1.63,0.52,100,1,0.82,1.9878048780487805,0.63414634146341464]
[4,8,170,23,1,0.93,0.93,200,0,0.93,1,1]
[4,9.3000000000000007,170,23,50,1.24,0.86,200,1,0.93,1.3333333333333333,0.92473118279569888]
[4,10.1,170,23,60,1.43,0.84,200,1,0.93,1.5376344086021503,0.90322580645161277]
[4,11,170,23,70,1.63,0.82,200,1,0.93,1.7526881720430105,0.88172043010752676]
[4,11.8,170,23,80,1.82,0.79,200,1,0.93,1.956989247311828,0.84946236559139787]
[4,12.6,170,23,90,2.0099999999999998,0.77,200,1,0.93,2.161290322580645,0.82795698924731176]
[4,13.4,170,23,99,2.19,0.75,200,1,0.93,2.354838709677419,0.80645161290322576]
[4,6.7,170,23,1,0.96,0.96,300,0,0.96,1,1]
[4,7.8,170,23,50,1.34,0.91,300,1,0.96,1.3958333333333335,0.94791666666666674]
[4,8.4,170,23,60,1.55,0.89,300,1,0.96,1.6145833333333335,0.92708333333333337]
[4,9,170,23,70,1.75,0.88,300,1,0.96,1.8229166666666667,0.91666666666666674]
[4,9.6,170,23,80,1.97,0.86,300,1,0.96,2.0520833333333335,0.89583333333333337]
[4,10.199999999999999,170,23,90,2.17,0.85,300,1,0.96,2.2604166666666665,0.88541666666666663]
[4,10.8,170,23,99,2.36,0.83,300,1,0.96,2.4583333333333335,0.86458333333333337]
[4,11.4,170,24,1,0.87,0.87,100,0,0.87,1,1]
[4,12.7,170,24,50,1.01,0.75,100,1,0.87,1.1609195402298851,0.86206896551724144]
[4,14,170,24,60,1.17,0.71,100,1,0.87,1.3448275862068966,0.81609195402298851]
[4,15.3,170,24,70,1.32,0.66,100,1,0.87,1.517241379310345,0.75862068965517249]
[4,16.600000000000001,170,24,80,1.47,0.62,100,1,0.87,1.6896551724137931,0.71264367816091956]
[4,17.8,170,24,90,1.61,0.57999999999999996,100,1,0.87,1.8505747126436782,0.66666666666666663]
[4,19,170,24,99,1.74,0.54,100,1,0.87,2,0.62068965517241381]
[4,8.1999999999999993,170,24,1,0.97,0.97,200,0,0.97,1,1]
[4,9.8000000000000007,170,24,50,1.34,0.9,200,1,0.97,1.3814432989690724,0.92783505154639179]
[4,10.6,170,24,60,1.55,0.88,200,1,0.97,1.597938144329897,0.90721649484536082]
[4,11.5,170,24,70,1.75,0.85,200,1,0.97,1.8041237113402062,0.87628865979381443]
[4,12.4,170,24,80,1.96,0.83,200,1,0.97,2.0206185567010309,0.85567010309278346]
[4,13.3,170,24,90,2.16,0.8,200,1,0.97,2.2268041237113403,0.82474226804123718]
[4,14.1,170,24,99,2.34,0.78,200,1,0.97,2.4123711340206184,0.80412371134020622]
[4,6.9,170,24,1,1.01,1.01,300,0,1.01,1,1]
[4,8.1,170,24,50,1.45,0.95,300,{"$f":"IF(F982<>G982,1,0)","v":1},1.01,{"$f":"F982/J982","v":1.4356435643564356},0.94059405940594054]
[4,8.8000000000000007,170,24,60,1.67,0.93,300,1,1.01,1.6534653465346534,{"$f":"G983/J983","v":0.92079207920792083}]
[4,9.4,170,24,70,1.89,0.92,300,1,1.01,1.8712871287128712,0.91089108910891092]
[4,10,170,24,80,2.11,0.9,300,1,{"$f":"IF(F985/G985=1,F985,J984)","v":1.01},2.0891089108910892,0.8910891089108911]
[4,10.7,170,24,90,2.34,0.88,300,1,1.01,2.3168316831683167,0.87128712871287128]
[4,11.2,170,24,99,2.5299999999999998,0.87,300,1,1.01,2.504950495049505,0.86138613861386137]
[4,11.8,170,25,1,0.91,0.91,100,0,0.91,1,1]
[4,13.4,170,25,50,1.0900000000000001,0.78,100,1,0.91,1.1978021978021978,0.8571428571428571]
[4,14.7,170,25,60,1.25,0.73,100,1,0.91,1.3736263736263736,0.80219780219780212]
[4,16.100000000000001,170,25,70,1.41,0.69,100,1,0.91,1.5494505494505493,0.75824175824175821]
[4,17.5,170,25,80,1.57,0.64,100,1,0.91,1.7252747252747254,0.70329670329670324]
[4,18.8,170,25,90,1.72,0.6,100,1,0.91,1.8901098901098901,0.65934065934065933]
[4,20,170,25,99,1.86,0.56000000000000005,100,1,0.91,2.0439560439560438,0.61538461538461542]
[4,8.4,170,25,1,1.02,1.02,200,0,1.02,1,1]
[4,10.199999999999999,170,25,50,1.45,0.94,200,1,1.02,1.4215686274509802,0.92156862745098034]
[4,11.1,170,25,60,1.66,0.91,200,1,1.02,1.6274509803921569,0.89215686274509809]
[4,12.1,170,25,70,1.88,0.89,200,1,1.02,1.8431372549019607,0.87254901960784315]
[4,13,170,25,80,2.1,0.86,200,1,1.02,2.0588235294117649,0.84313725490196079]
[4,13.9,170,25,90,2.31,0.84,200,1,1.02,2.2647058823529411,0.82352941176470584]
[4,14.8,170,25,99,2.5099999999999998,0.81,200,1,1.02,2.4607843137254899,0.79411764705882359]
[4,7,170,25,1,1.05,1.05,300,0,1.05,1,1]
[4,8.5,170,25,50,1.56,0.99,300,1,1.05,1.4857142857142858,0.94285714285714284]
[4,9.1,170,25,60,1.79,0.97,300,1,1.05,1.7047619047619047,0.92380952380952375]
[4,9.8000000000000007,170,25,70,2.0299999999999998,0.96,300,1,1.05,1.9333333333333331,0.91428571428571426]
[4,10.5,170,25,80,2.2599999999999998,0.94,300,1,1.05,2.1523809523809523,0.89523809523809517]
[4,11.1,170,25,90,2.5,0.92,300,1,1.05,2.3809523809523809,0.87619047619047619]
[4,11.8,170,25,99,2.71,0.9,300,1,1.05,2.5809523809523807,0.8571428571428571]
[4,12.1,170,26,1,0.95,0.95,100,0,0.95,1,1]
[4,14.1,170,26,50,1.17,0.81,100,1,0.95,1.2315789473684211,0.85263157894736852]
[4,15.5,170,26,60,1.34,0.76,100,1,0.95,1.4105263157894739,0.8]
[4,16.899999999999999,170,26,70,1.51,0.71,100,1,0.95,1.5894736842105264,0.74736842105263157]
[4,18.399999999999999,170,26,80,1.67,0.66,100,1,0.95,1.7578947368421052,0.69473684210526321]
[4,19.8,170,26,90,1.84,0.61,100,1,0.95,1.9368421052631581,0.64210526315789473]
[4,21,170,26,99,1.98,0.56999999999999995,100,1,0.95,2.0842105263157897,0.6]
[4,8.6,170,26,1,1.07,1.07,200,0,1.07,1,1]
[4,10.7,170,26,50,1.55,0.98,200,1,1.07,1.4485981308411215,0.9158878504672896]
[4,11.6,170,26,60,1.78,0.95,200,1,1.07,1.6635514018691588,0.8878504672897195]
[4,12.6,170,26,70,2.0099999999999998,0.92,200,1,1.07,1.8785046728971959,0.85981308411214952]
[4,13.6,170,26,80,2.2400000000000002,0.89,200,1,1.07,2.0934579439252339,0.83177570093457942]
[4,14.6,170,26,90,2.4700000000000002,0.87,200,1,1.07,2.3084112149532712,0.81308411214953269]
[4,15.5,170,26,99,2.68,0.84,200,1,1.07,2.5046728971962615,0.78504672897196259]
[4,7.1,170,26,1,1.1000000000000001,1.1000000000000001,300,0,1.1000000000000001,1,1]
[4,8.8000000000000007,170,26,50,1.67,1.03,300,1,1.1000000000000001,1.5181818181818181,0.93636363636363629]
[4,9.5,170,26,60,1.92,1.01,300,1,1.1000000000000001,1.7454545454545451,0.9181818181818181]
[4,10.199999999999999,170,26,70,2.17,0.99,300,1,1.1000000000000001,1.9727272727272724,0.89999999999999991]
[4,10.9,170,26,80,2.42,0.98,300,1,1.1000000000000001,2.1999999999999997,0.89090909090909087]
[4,11.6,170,26,90,2.67,0.96,300,1,1.1000000000000001,2.4272727272727268,0.87272727272727257]
[4,12.3,170,26,99,2.9,0.94,300,1,1.1000000000000001,2.6363636363636362,0.85454545454545439]
[4,12.5,170,27,1,0.99,0.99,100,0,0.99,1,1]
[4,14.8,170,27,50,1.25,0.83,100,1,0.99,1.2626262626262625,0.83838383838383834]
[4,16.3,170,27,60,1.43,0.78,100,1,0.99,1.4444444444444444,0.78787878787878796]
[4,17.8,170,27,70,1.61,0.73,100,1,0.99,1.6262626262626263,0.73737373737373735]
[4,19.3,170,27,80,1.78,0.68,100,1,0.99,1.797979797979798,0.68686868686868696]
[4,20.8,170,27,90,1.95,0.63,100,1,0.99,1.9696969696969697,0.63636363636363635]
[4,22,170,27,99,2.1,0.59,100,1,0.99,2.1212121212121211,0.59595959595959591]
[4,8.8000000000000007,170,27,1,1.1100000000000001,1.1100000000000001,200,0,1.1100000000000001,1,1]
[4,11.1,170,27,50,1.66,1.01,200,1,1.1100000000000001,1.4954954954954953,0.90990990990990983]
[4,12.2,170,27,60,1.91,0.98,200,1,1.1100000000000001,1.7207207207207205,0.88288288288288275]
[4,13.2,170,27,70,2.15,0.96,200,1,1.1100000000000001,1.9369369369369367,0.8648648648648648]
[4,14.3,170,27,80,2.39,0.93,200,1,1.1100000000000001,2.1531531531531529,0.83783783783783783]
[4,15.3,170,27,90,2.63,0.9,200,1,1.1100000000000001,2.3693693693693691,0.81081081081081074]
[4,16.2,170,27,99,2.85,0.87,200,1,1.1100000000000001,2.5675675675675675,0.78378378378378366]
[4,7.3,170,27,1,1.1499999999999999,1.1499999999999999,300,0,1.1499999999999999,1,1]
[4,9.1,170,27,50,1.79,1.07,300,1,1.1499999999999999,1.5565217391304349,0.93043478260869583]
[4,9.9,170,27,60,2.06,1.05,300,{"$f":"IF(F1046<>G1046,1,0)","v":1},1.1499999999999999,{"$f":"F1046/J1046","v":1.7913043478260871},0.91304347826086962]
[4,10.6,170,27,70,2.3199999999999998,1.03,300,1,1.1499999999999999,2.017391304347826,{"$f":"G1047/J1047","v":0.89565217391304353}]
[4,11.4,170,27,80,2.59,1.01,300,1,1.1499999999999999,2.2521739130434781,0.87826086956521743]
[4,12.1,170,27,90,2.85,0.99,300,1,{"$f":"IF(F1049/G1049=1,F1049,J1048)","v":1.1499999999999999},2.4782608695652177,0.86086956521739133]
[4,12.8,170,27,99,3.09,0.97,300,1,1.1499999999999999,2.6869565217391305,0.84347826086956523]
[4,11.7,240,21,1,0.9,0.9,100,0,0.9,1,1]
[4,11.6,240,21,50,0.88,0.81,100,1,0.9,0.97777777777777775,0.9]
[4,12.8,240,21,60,1.02,0.75,100,1,0.9,1.1333333333333333,0.83333333333333326]
[4,14,240,21,70,1.1599999999999999,0.69,100,1,0.9,1.2888888888888888,0.76666666666666661]
[4,15.2,240,21,80,1.3,0.63,100,1,0.9,1.4444444444444444,0.7]
[4,16.3,240,21,90,1.44,0.56999999999999995,100,1,0.9,1.5999999999999999,0.6333333333333333]
[4,17.399999999999999,240,21,99,1.56,0.52,100,1,0.9,1.7333333333333334,0.57777777777777783]
[4,8.6,240,21,1,1.07,1.07,200,0,1.07,1,1]
[4,9.4,240,21,50,1.27,0.99,200,1,1.07,1.1869158878504673,0.92523364485981308]
[4,10.3,240,21,60,1.48,0.95,200,1,1.07,1.3831775700934579,0.8878504672897195]
[4,11.2,240,21,70,1.68,0.91,200,1,1.07,1.5700934579439252,0.85046728971962615]
[4,12.1,240,21,80,1.89,0.87,200,1,1.07,1.7663551401869158,0.81308411214953269]
[4,13,240,21,90,2.1,0.83,200,1,1.07,1.9626168224299065,0.77570093457943912]
[4,13.8,240,21,99,2.2799999999999998,0.8,200,1,1.07,2.1308411214953269,0.74766355140186913]
[4,7.2,240,21,1,1.1200000000000001,1.1200000000000001,300,0,1.1200000000000001,1,1]
[4,8.1,240,21,50,1.42,1.06,300,1,1.1200000000000001,1.2678571428571426,0.9464285714285714]
[4,8.6999999999999993,240,21,60,1.65,1.03,300,1,1.1200000000000001,1.4732142857142856,0.9196428571428571]
[4,9.4,240,21,70,1.89,1,300,1,1.1200000000000001,1.6874999999999998,0.89285714285714279]
[4,10.1,240,21,80,2.12,0.98,300,1,1.1200000000000001,1.8928571428571428,0.87499999999999989]
[4,10.7,240,21,90,2.36,0.95,300,1,1.1200000000000001,2.1071428571428568,0.84821428571428559]
[4,11.3,240,21,99,2.56,0.92,300,1,1.1200000000000001,2.2857142857142856,0.8214285714285714]
[4,12.1,240,22,1,0.95,0.95,100,0,0.95,1,1]
[4,12.3,240,22,50,0.96,0.85,100,1,0.95,1.0105263157894737,0.89473684210526316]
[4,13.5,240,22,60,1.1100000000000001,0.78,100,1,0.95,1.168421052631579,0.82105263157894748]
[4,14.8,240,22,70,1.26,0.72,100,1,0.95,1.3263157894736843,0.75789473684210529]
[4,16.100000000000001,240,22,80,1.41,0.65,100,1,0.95,1.4842105263157894,0.68421052631578949]
[4,17.3,240,22,90,1.55,0.59,100,1,0.95,1.6315789473684212,0.62105263157894741]
[4,18.399999999999999,240,22,99,1.67,0.53,100,1,0.95,1.7578947368421052,0.55789473684210533]
[4,8.8000000000000007,240,22,1,1.1299999999999999,1.1299999999999999,200,0,1.1299999999999999,1,1]
[4,9.9,240,22,50,1.39,1.03,200,1,1.1299999999999999,1.2300884955752214,0.91150442477876115]
[4,10.9,240,22,60,1.61,0.99,200,1,1.1299999999999999,1.4247787610619471,0.87610619469026552]
[4,11.8,240,22,70,1.83,0.95,200,1,1.1299999999999999,1.6194690265486729,0.84070796460177]
[4,12.8,240,22,80,2.04,0.91,200,1,1.1299999999999999,1.8053097345132745,0.80530973451327448]
[4,13.7,240,22,90,2.2599999999999998,0.87,200,1,1.1299999999999999,2,0.76991150442477885]
[4,14.5,240,22,99,2.46,0.83,200,1,1.1299999999999999,2.1769911504424782,0.73451327433628322]
[4,7.4,240,22,1,1.19,1.19,300,0,1.19,1,1]
[4,8.4,240,22,50,1.55,1.1100000000000001,300,1,1.19,1.3025210084033614,0.93277310924369761]
[4,9.1,240,22,60,1.8,1.08,300,1,1.19,1.5126050420168069,0.90756302521008414]
[4,9.8000000000000007,240,22,70,2.0499999999999998,1.05,300,1,1.19,1.722689075630252,0.88235294117647067]
[4,10.6,240,22,80,2.2999999999999998,1.02,300,1,1.19,1.9327731092436975,0.85714285714285721]
[4,11.3,240,22,90,2.54,0.99,300,1,1.19,2.134453781512605,0.83193277310924374]
[4,11.9,240,22,99,2.77,0.97,300,1,1.19,2.327731092436975,0.81512605042016806]
[4,12.6,240,23,1,1,1,100,0,1,1,1]
[4,13,240,23,50,1.05,0.88,100,1,1,1.05,0.88]
[4,14.3,240,23,60,1.2,0.81,100,1,1,1.2,0.81]
[4,15.6,240,23,70,1.36,0.74,100,1,1,1.36,0.74]
[4,17,240,23,80,1.51,0.68,100,1,1,1.51,0.68]
[4,18.2,240,23,90,1.66,0.61,100,1,1,1.66,0.61]
[4,19.399999999999999,240,23,99,1.79,0.55000000000000004,100,1,1,1.79,0.55000000000000004]
[4,9.1,240,23,1,1.19,1.19,200,0,1.19,1,1]
[4,10.5,240,23,50,1.51,1.08,200,1,1.19,1.2689075630252102,0.90756302521008414]
[4,11.5,240,23,60,1.74,1.04,200,1,1.19,1.46218487394958,0.87394957983193289]
[4,12.5,240,23,70,1.97,0.99,200,1,1.19,1.6554621848739497,0.83193277310924374]
[4,13.4,240,23,80,2.2000000000000002,0.95,200,1,1.19,1.8487394957983196,0.79831932773109249]
[4,14.4,240,23,90,2.4300000000000002,0.91,200,1,1.19,2.0420168067226894,0.76470588235294124]
[4,15.3,240,23,99,2.64,0.87,200,1,1.19,2.2184873949579833,0.73109243697478998]
[4,7.6,240,23,1,1.25,1.25,300,0,1.25,1,1]
[4,8.8000000000000007,240,23,50,1.69,1.1599999999999999,300,1,1.25,1.3519999999999999,0.92799999999999994]
[4,9.6,240,23,60,1.95,1.1299999999999999,300,1,1.25,1.56,0.90399999999999991]
[4,10.3,240,23,70,2.21,1.1000000000000001,300,{"$f":"IF(F1110<>G1110,1,0)","v":1},1.25,{"$f":"F1110/J1110","v":1.768},0.88000000000000012]
[4,11.1,240,23,80,2.48,1.07,300,1,1.25,1.984,{"$f":"G1111/J1111","v":0.85600000000000009}]
[4,11.8,240,23,90,2.74,1.04,300,1,1.25,2.1920000000000002,0.83200000000000007]
[4,12.5,240,23,99,2.97,1.01,300,1,{"$f":"IF(F1113/G1113=1,F1113,J1112)","v":1.25},2.3760000000000003,0.80800000000000005]
[4,13,240,24,1,1.05,1.05,100,0,1.05,1,1]
[4,13.7,240,24,50,1.1299999999999999,0.91,100,1,1.05,1.0761904761904761,0.8666666666666667]
[4,15.1,240,24,60,1.29,0.84,100,1,1.05,1.2285714285714286,0.79999999999999993]
[4,16.5,240,24,70,1.46,0.77,100,1,1.05,1.3904761904761904,0.73333333333333328]
[4,17.899999999999999,240,24,80,1.62,0.7,100,1,1.05,1.5428571428571429,0.66666666666666663]
[4,19.2,240,24,90,1.77,0.63,100,1,1.05,1.6857142857142857,0.6]
[4,20.399999999999999,240,24,99,1.91,0.56999999999999995,100,1,1.05,1.8190476190476188,0.54285714285714282]
[4,9.4,240,24,1,1.25,1.25,200,0,1.25,1,1]
[4,11,240,24,50,1.63,1.1299999999999999,200,1,1.25,1.3039999999999998,0.90399999999999991]
[4,12,240,24,60,1.88,1.08,200,1,1.25,1.504,0.8640000000000001]
[4,13.1,240,24,70,2.12,1.04,200,1,1.25,1.6960000000000002,0.83200000000000007]
[4,14.2,240,24,80,2.37,0.99,200,1,1.25,1.8960000000000001,0.79200000000000004]
[4,15.2,240,24,90,2.61,0.94,200,1,1.25,2.0880000000000001,0.752]
[4,16.100000000000001,240,24,99,2.83,0.9,200,1,1.25,2.2640000000000002,0.72]
[4,7.8,240,24,1,1.31,1.31,300,0,1.31,1,1]
[4,9.1999999999999993,240,24,50,1.82,1.22,300,1,1.31,1.3893129770992367,0.93129770992366412]
[4,10,240,24,60,2.1,1.18,300,1,1.31,1.6030534351145038,0.9007633587786259]
[4,10.8,240,24,70,2.38,1.1499999999999999,300,1,1.31,1.8167938931297709,0.87786259541984724]
[4,11.6,240,24,80,2.66,1.1200000000000001,300,1,1.31,2.0305343511450382,0.85496183206106879]
[4,12.4,240,24,90,2.94,1.08,300,1,1.31,2.2442748091603053,0.82442748091603058]
[4,13.1,240,24,99,3.19,1.05,300,1,1.31,2.4351145038167936,0.80152671755725191]
[4,13.5,240,25,1,1.1100000000000001,1.1100000000000001,100,0,1.1100000000000001,1,1]
[4,14.4,240,25,50,1.21,0.94,100,1,1.1100000000000001,1.0900900900900901,0.84684684684684675]
[4,15.9,240,25,60,1.39,0.87,100,1,1.1100000000000001,1.2522522522522521,0.78378378378378366]
[4,17.399999999999999,240,25,70,1.56,0.79,100,1,1.1100000000000001,1.4054054054054053,0.71171171171171166]
[4,18.8,240,25,80,1.73,0.72,100,1,1.1100000000000001,1.5585585585585584,0.64864864864864857]
[4,20.2,240,25,90,1.89,0.64,100,1,1.1100000000000001,1.7027027027027024,0.57657657657657657]
[4,21.5,240,25,99,2.0299999999999998,0.57999999999999996,100,1,1.1100000000000001,1.8288288288288286,0.5225225225225224]
[4,9.6,240,25,1,1.31,1.31,200,0,1.31,1,1]
[4,11.5,240,25,50,1.75,1.17,200,1,1.31,1.3358778625954197,0.89312977099236635]
[4,12.6,240,25,60,2.02,1.1200000000000001,200,1,1.31,1.5419847328244274,0.85496183206106879]
[4,13.8,240,25,70,2.2799999999999998,1.07,200,1,1.31,1.7404580152671754,0.81679389312977102]
[4,14.9,240,25,80,2.54,1.03,200,1,1.31,1.9389312977099236,0.7862595419847328]
[4,16,240,25,90,2.79,0.98,200,1,1.31,2.1297709923664123,0.74809160305343503]
[4,17,240,25,99,3.02,0.94,200,1,1.31,2.3053435114503817,0.71755725190839692]
[4,7.9,240,25,1,1.38,1.38,300,0,1.38,1,1]
[4,9.6,240,25,50,1.97,1.27,300,1,1.38,1.4275362318840581,0.92028985507246386]
[4,10.5,240,25,60,2.2599999999999998,1.23,300,1,1.38,1.6376811594202898,0.89130434782608703]
[4,11.3,240,25,70,2.56,1.2,300,1,1.38,1.8550724637681162,0.86956521739130443]
[4,12.2,240,25,80,2.85,1.1599999999999999,300,1,1.38,2.0652173913043481,0.84057971014492749]
[4,13,240,25,90,3.15,1.1200000000000001,300,1,1.38,2.2826086956521738,0.81159420289855089]
[4,13.8,240,25,99,3.41,1.0900000000000001,300,1,1.38,2.4710144927536235,0.78985507246376818]
[4,13.9,240,26,1,1.1599999999999999,1.1599999999999999,100,0,1.1599999999999999,1,1]
[4,15.2,240,26,50,1.3,0.97,100,1,1.1599999999999999,1.1206896551724139,0.8362068965517242]
[4,16.7,240,26,60,1.48,0.89,100,1,1.1599999999999999,1.2758620689655173,0.76724137931034486]
[4,18.3,240,26,70,1.66,0.81,100,1,1.1599999999999999,1.4310344827586208,0.69827586206896564]
[4,19.8,240,26,80,1.84,0.74,100,1,1.1599999999999999,1.5862068965517244,0.63793103448275867]
[4,21.2,240,26,90,2.0099999999999998,0.66,100,1,1.1599999999999999,1.732758620689655,0.56896551724137934]
[4,22.5,240,26,99,2.16,0.59,100,1,1.1599999999999999,1.8620689655172415,0.50862068965517238]
[4,9.9,240,26,1,1.37,1.37,200,0,1.37,1,1]
[4,12.1,240,26,50,1.88,1.22,200,1,1.37,1.3722627737226276,0.8905109489051094]
[4,13.3,240,26,60,2.16,1.1599999999999999,200,1,1.37,1.5766423357664234,0.84671532846715314]
[4,14.5,240,26,70,2.44,1.1100000000000001,200,1,1.37,1.7810218978102188,0.81021897810218979]
[4,15.6,240,26,80,2.71,1.06,200,1,1.37,1.9781021897810218,0.77372262773722622]
[4,16.8,240,26,90,2.98,1.01,200,1,1.37,2.1751824817518246,0.73722627737226276]
[4,17.899999999999999,240,26,99,3.23,0.97,200,1,1.37,2.3576642335766422,0.70802919708029188]
[4,8.1,240,26,1,1.44,1.44,300,0,1.44,1,1]
[4,10,240,26,50,2.11,1.32,300,1,1.44,1.4652777777777777,0.91666666666666674]
[4,10.9,240,26,60,2.42,1.28,300,1,1.44,1.6805555555555556,0.88888888888888895]
[4,11.8,240,26,70,2.74,1.24,300,1,1.44,1.9027777777777779,0.86111111111111116]
[4,12.7,240,26,80,3.05,1.2,300,{"$f":"IF(F1174<>G1174,1,0)","v":1},1.44,{"$f":"F1174/J1174","v":2.1180555555555554},0.83333333333333337]
[4,13.6,240,26,90,3.36,1.17,300,1,1.44,2.3333333333333335,{"$f":"G1175/J1175","v":0.8125}]
[4,14.4,240,26,99,3.65,1.1299999999999999,300,1,1.44,2.5347222222222223,0.78472222222222221]
[4,14.4,240,27,1,1.21,1.21,100,0,{"$f":"IF(F1177/G1177=1,F1177,J1176)","v":1.21},1,1]
[4,15.9,240,27,50,1.39,1,100,1,1.21,1.1487603305785123,0.82644628099173556]
[4,17.600000000000001,240,27,60,1.58,0.92,100,1,1.21,1.3057851239669422,0.76033057851239672]
[4,19.2,240,27,70,1.77,0.84,100,1,1.21,1.4628099173553719,0.69421487603305787]
[4,20.8,240,27,80,1.95,0.76,100,1,1.21,1.6115702479338843,0.62809917355371903]
[4,22.3,240,27,90,2.13,0.67,100,1,1.21,1.7603305785123966,0.55371900826446285]
[4,23.6,240,27,99,2.2799999999999998,0.6,100,1,1.21,1.884297520661157,0.49586776859504134]
[4,10.1,240,27,1,1.43,1.43,200,0,1.43,1,1]
[4,12.7,240,27,50,2.02,1.26,200,1,1.43,1.4125874125874127,0.88111888111888115]
[4,13.9,240,27,60,2.31,1.2,200,1,1.43,1.6153846153846154,0.83916083916083917]
[4,15.2,240,27,70,2.6,1.1499999999999999,200,1,1.43,1.8181818181818183,0.80419580419580416]
[4,16.399999999999999,240,27,80,2.89,1.1000000000000001,200,1,1.43,2.0209790209790213,0.76923076923076927]
[4,17.600000000000001,240,27,90,3.18,1.04,200,1,1.43,2.2237762237762242,0.72727272727272729]
[4,18.8,240,27,99,3.43,0.99,200,1,1.43,2.3986013986013988,0.69230769230769229]
[4,8.3000000000000007,240,27,1,1.5,1.5,300,0,1.5,1,1]
[4,10.5,240,27,50,2.2599999999999998,1.37,300,1,1.5,1.5066666666666666,0.91333333333333344]
[4,11.4,240,27,60,2.59,1.33,300,1,1.5,1.7266666666666666,0.88666666666666671]
[4,12.4,240,27,70,2.92,1.29,300,1,1.5,1.9466666666666665,0.86]
[4,13.3,240,27,80,3.26,1.25,300,1,1.5,2.1733333333333333,0.83333333333333337]
[4,14.3,240,27,90,3.59,1.21,300,1,1.5,2.3933333333333331,0.80666666666666664]
[4,15.1,240,27,99,3.89,1.17,300,1,1.5,2.5933333333333333,0.77999999999999992]
[4,12.7,310,21,1,1.01,1.01,100,0,1.01,1,1]
[4,12.6,310,21,50,1.01,1.01,100,0,1.01,1,1]
[4,13.3,310,21,60,1.0900000000000001,0.85,100,1,1.01,1.0792079207920793,0.84158415841584155]
[4,14.6,310,21,70,1.23,0.77,100,1,1.01,1.2178217821782178,0.76237623762376239]
[4,15.8,310,21,80,1.38,0.69,100,1,1.01,1.3663366336633662,0.68316831683168311]
[4,17,310,21,90,1.52,0.6,100,1,1.01,1.504950495049505,0.59405940594059403]
[4,18.100000000000001,310,21,99,1.64,0.53,100,1,1.01,1.6237623762376237,0.52475247524752477]
[4,9.4,310,21,1,1.26,1.26,200,0,1.26,1,1]
[4,10.1,310,21,50,1.43,1.1499999999999999,200,1,1.26,1.1349206349206349,0.91269841269841268]
[4,11.1,310,21,60,1.66,1.0900000000000001,200,1,1.26,1.3174603174603174,0.86507936507936511]
[4,12.1,310,21,70,1.89,1.04,200,1,1.26,1.5,0.82539682539682546]
[4,13.1,310,21,80,2.12,0.98,200,1,1.26,1.6825396825396826,0.77777777777777779]
[4,14.1,310,21,90,2.35,0.92,200,1,1.26,1.8650793650793651,0.73015873015873023]
[4,15,310,21,99,2.5499999999999998,0.87,200,1,1.26,2.0238095238095237,0.69047619047619047]
[4,7.8,310,21,1,1.34,1.34,300,0,1.34,1,1]
[4,8.6999999999999993,310,21,50,1.65,1.25,300,1,1.34,1.2313432835820894,0.93283582089552231]
[4,9.5,310,21,60,1.92,1.21,300,1,1.34,1.4328358208955223,0.90298507462686561]
[4,10.3,310,21,70,2.19,1.17,300,1,1.34,1.6343283582089552,0.87313432835820881]
[4,11,310,21,80,2.46,1.1200000000000001,300,1,1.34,1.835820895522388,0.83582089552238814]
[4,11.8,310,21,90,2.73,1.08,300,1,1.34,2.0373134328358207,0.80597014925373134]
[4,12.5,310,21,99,2.97,1.04,300,1,1.34,2.216417910447761,0.77611940298507465]
[4,13.2,310,22,1,1.07,1.07,100,0,1.07,1,1]
[4,13.1,310,22,50,1.07,1.07,100,0,1.07,1,1]
[4,14.1,310,22,60,1.18,0.89,100,1,1.07,1.1028037383177569,0.83177570093457942]
[4,15.4,310,22,70,1.33,0.8,100,1,1.07,1.2429906542056075,0.74766355140186913]
[4,16.7,310,22,80,1.48,0.71,100,1,1.07,1.3831775700934579,0.66355140186915884]
[4,18,310,22,90,1.63,0.62,100,1,1.07,1.5233644859813082,0.57943925233644855]
[4,19.100000000000001,310,22,99,1.76,0.55000000000000004,100,1,1.07,1.6448598130841121,0.5140186915887851]
[4,9.6999999999999993,310,22,1,1.33,1.33,200,0,1.33,1,1]
[4,10.7,310,22,50,1.56,1.2,200,1,1.33,1.1729323308270676,0.90225563909774431]
[4,11.7,310,22,60,1.8,1.1399999999999999,200,1,1.33,1.3533834586466165,0.85714285714285698]
[4,12.8,310,22,70,2.0499999999999998,1.08,200,1,1.33,1.5413533834586464,0.81203007518796988]
[4,13.8,310,22,80,2.29,1.02,200,1,1.33,1.7218045112781954,0.76691729323308266]
[4,14.9,310,22,90,2.5299999999999998,0.96,200,1,1.33,1.9022556390977441,0.72180451127819545]
[4,15.8,310,22,99,2.75,0.91,200,1,1.33,2.0676691729323307,0.68421052631578949]
[4,8.1,310,22,1,1.42,1.42,300,0,1.42,1,1]
[4,9.1,310,22,50,1.8,1.31,300,1,1.42,1.267605633802817,0.92253521126760574]
[4,10,310,22,60,2.09,1.27,300,1,1.42,1.471830985915493,0.89436619718309862]
[4,10.8,310,22,70,2.37,1.22,300,1,1.42,1.6690140845070425,0.85915492957746487]
[4,11.6,310,22,80,2.66,1.18,300,1,1.42,1.8732394366197185,0.83098591549295775]
[4,12.4,310,22,90,2.94,1.1299999999999999,300,{"$f":"IF(F1238<>G1238,1,0)","v":1},1.42,{"$f":"F1238/J1238","v":2.0704225352112675},0.79577464788732388]
[4,13.2,310,22,99,3.2,1.0900000000000001,300,1,1.42,2.2535211267605635,{"$f":"G1239/J1239","v":0.76760563380281699}]
[4,13.7,310,23,1,1.1299999999999999,1.1299999999999999,100,0,1.1299999999999999,1,1]
[4,13.5,310,23,50,1.1100000000000001,1.01,100,1,{"$f":"IF(F1241/G1241=1,F1241,J1240)","v":1.1299999999999999},0.98230088495575241,0.89380530973451333]
[4,14.9,310,23,60,1.27,0.92,100,1,1.1299999999999999,1.1238938053097347,0.81415929203539839]
[4,16.3,310,23,70,1.43,0.82,100,1,1.1299999999999999,1.2654867256637168,0.72566371681415931]
[4,17.7,310,23,80,1.59,0.73,100,1,1.1299999999999999,1.4070796460176993,0.64601769911504425]
[4,19,310,23,90,1.75,0.64,100,1,1.1299999999999999,1.5486725663716816,0.56637168141592931]
[4,20.100000000000001,310,23,99,1.88,0.56999999999999995,100,1,1.1299999999999999,1.6637168141592922,0.50442477876106195]
[4,10,310,23,1,1.4,1.4,200,0,1.4,1,1]
[4,11.3,310,23,50,1.69,1.26,200,1,1.4,1.2071428571428571,0.9]
[4,12.4,310,23,60,1.95,1.19,200,1,1.4,1.392857142857143,0.85]
[4,13.5,310,23,70,2.21,1.1299999999999999,200,1,1.4,1.5785714285714287,0.80714285714285716]
[4,14.6,310,23,80,2.4700000000000002,1.06,200,1,1.4,1.7642857142857145,0.75714285714285723]
[4,15.7,310,23,90,2.72,1,200,1,1.4,1.9428571428571431,0.7142857142857143]
[4,16.7,310,23,99,2.95,0.94,200,1,1.4,2.1071428571428572,0.67142857142857149]
[4,8.3000000000000007,310,23,1,1.5,1.5,300,0,1.5,1,1]
[4,9.6,310,23,50,1.96,1.37,300,1,1.5,1.3066666666666666,0.91333333333333344]
[4,10.5,310,23,60,2.2599999999999998,1.32,300,1,1.5,1.5066666666666666,0.88]
[4,11.3,310,23,70,2.56,1.28,300,1,1.5,1.7066666666666668,0.85333333333333339]
[4,12.2,310,23,80,2.87,1.23,300,1,1.5,1.9133333333333333,0.82]
[4,13.1,310,23,90,3.17,1.18,300,1,1.5,2.1133333333333333,0.78666666666666663]
[4,13.8,310,23,99,3.44,1.1299999999999999,300,1,1.5,2.2933333333333334,0.7533333333333333]
[4,14.2,310,24,1,1.19,1.19,100,0,1.19,1,1]
[4,14.3,310,24,50,1.2,1.05,100,1,1.19,1.0084033613445378,0.88235294117647067]
[4,15.7,310,24,60,1.37,0.95,100,1,1.19,1.1512605042016808,0.79831932773109249]
[4,17.2,310,24,70,1.54,0.85,100,1,1.19,1.2941176470588236,0.7142857142857143]
[4,18.600000000000001,310,24,80,1.7,0.76,100,1,1.19,1.4285714285714286,0.63865546218487401]
[4,20,310,24,90,1.86,0.66,100,1,1.19,1.5630252100840338,0.55462184873949583]
[4,21.2,310,24,99,2,0.57999999999999996,100,1,1.19,1.680672268907563,0.48739495798319327]
[4,10.3,310,24,1,1.48,1.48,200,0,1.48,1,1]
[4,11.9,310,24,50,1.83,1.31,200,1,1.48,1.2364864864864866,0.8851351351351352]
[4,13,310,24,60,2.11,1.24,200,1,1.48,1.4256756756756757,0.83783783783783783]
[4,14.2,310,24,70,2.38,1.17,200,1,1.48,1.6081081081081081,0.79054054054054046]
[4,15.4,310,24,80,2.65,1.1000000000000001,200,1,1.48,1.7905405405405406,0.74324324324324331]
[4,16.5,310,24,90,2.92,1.04,200,1,1.48,1.972972972972973,0.70270270270270274]
[4,17.600000000000001,310,24,99,3.16,0.98,200,1,1.48,2.1351351351351351,0.66216216216216217]
[4,8.5,310,24,1,1.57,1.57,300,0,1.57,1,1]
[4,10,310,24,50,2.12,1.43,300,1,1.57,1.3503184713375795,0.91082802547770692]
[4,11,310,24,60,2.44,1.38,300,1,1.57,1.5541401273885349,0.87898089171974514]
[4,11.9,310,24,70,2.76,1.33,300,1,1.57,1.7579617834394903,0.84713375796178347]
[4,12.8,310,24,80,3.08,1.28,300,1,1.57,1.9617834394904459,0.81528662420382159]
[4,13.7,310,24,90,3.4,1.23,300,1,1.57,2.1656050955414012,0.78343949044585981]
[4,14.6,310,24,99,3.69,1.18,300,1,1.57,2.3503184713375793,0.75159235668789803]
[4,14.7,310,25,1,1.25,1.25,100,0,1.25,1,1]
[4,15,310,25,50,1.29,1.08,100,1,1.25,1.032,0.8640000000000001]
[4,16.600000000000001,310,25,60,1.47,0.98,100,1,1.25,1.1759999999999999,0.78400000000000003]
[4,18.100000000000001,310,25,70,1.64,0.87,100,1,1.25,1.3119999999999998,0.69599999999999995]
[4,19.600000000000001,310,25,80,1.81,0.77,100,1,1.25,1.448,0.61599999999999999]
[4,21,310,25,90,1.98,0.68,100,1,1.25,1.5840000000000001,0.54400000000000004]
[4,22.3,310,25,99,2.13,0.59,100,1,1.25,1.704,0.47199999999999998]
[4,10.6,310,25,1,1.55,1.55,200,0,1.55,1,1]
[4,12.5,310,25,50,1.97,1.36,200,1,1.55,1.2709677419354839,0.8774193548387097]
[4,13.7,310,25,60,2.2599999999999998,1.29,200,1,1.55,1.458064516129032,0.83225806451612905]
[4,14.9,310,25,70,2.5499999999999998,1.21,200,1,1.55,1.6451612903225805,0.78064516129032258]
[4,16.2,310,25,80,2.84,1.1399999999999999,200,1,1.55,1.8322580645161288,0.73548387096774182]
[4,17.399999999999999,310,25,90,3.12,1.07,200,1,1.55,2.0129032258064514,0.69032258064516128]
[4,18.5,310,25,99,3.37,1.01,200,1,1.55,2.1741935483870969,0.65161290322580645]
[4,8.6999999999999993,310,25,1,1.65,1.65,300,0,1.65,1,1]
[4,10.5,310,25,50,2.2799999999999998,1.49,300,1,1.65,1.3818181818181818,0.90303030303030307]
[4,11.5,310,25,60,2.62,1.44,300,1,1.65,1.5878787878787881,0.8727272727272728]
[4,12.5,310,25,70,2.96,1.38,300,1,1.65,1.7939393939393939,0.83636363636363631]
[4,13.4,310,25,80,3.3,1.33,300,1,1.65,2,0.80606060606060614]
[4,14.4,310,25,90,3.64,1.27,300,1,1.65,2.2060606060606061,0.76969696969696977]
[4,15.3,310,25,99,3.95,1.22,300,{"$f":"IF(F1302<>G1302,1,0)","v":1},1.65,{"$f":"F1302/J1302","v":2.393939393939394},0.73939393939393938]
[4,15.2,310,26,1,1.31,1.31,100,0,1.31,1,{"$f":"G1303/J1303","v":1}]
[4,15.8,310,26,50,1.38,1.1200000000000001,100,1,1.31,1.0534351145038168,0.85496183206106879]
[4,17.399999999999999,310,26,60,1.57,1.01,100,1,{"$f":"IF(F1305/G1305=1,F1305,J1304)","v":1.31},1.1984732824427482,0.77099236641221369]
[4,19,310,26,70,1.75,0.9,100,1,1.31,1.3358778625954197,0.68702290076335881]
[4,20.6,310,26,80,1.93,0.79,100,1,1.31,1.4732824427480915,0.60305343511450382]
[4,22,310,26,90,2.1,0.69,100,1,1.31,1.6030534351145038,0.52671755725190839]
[4,23.3,310,26,99,2.25,0.6,100,1,1.31,1.7175572519083968,0.4580152671755725]
[4,10.9,310,26,1,1.62,1.62,200,0,1.62,1,1]
[4,13.1,310,26,50,2.12,1.41,200,1,1.62,1.308641975308642,0.87037037037037024]
[4,14.4,310,26,60,2.42,1.33,200,1,1.62,1.4938271604938269,0.82098765432098764]
[4,15.7,310,26,70,2.73,1.25,200,1,1.62,1.6851851851851851,0.77160493827160492]
[4,17,310,26,80,3.03,1.18,200,1,1.62,1.87037037037037,0.72839506172839497]
[4,18.3,310,26,90,3.33,1.1000000000000001,200,1,1.62,2.0555555555555554,0.67901234567901236]
[4,19.399999999999999,310,26,99,3.59,1.04,200,1,1.62,2.216049382716049,0.64197530864197527]
[4,8.9,310,26,1,1.73,1.73,300,0,1.73,1,1]
[4,11,310,26,50,2.4500000000000002,1.55,300,1,1.73,1.4161849710982659,0.89595375722543358]
[4,12,310,26,60,2.81,1.49,300,1,1.73,1.624277456647399,0.86127167630057799]
[4,13.1,310,26,70,3.17,1.43,300,1,1.73,1.8323699421965318,0.82658959537572252]
[4,14.1,310,26,80,3.53,1.38,300,1,1.73,2.0404624277456644,0.79768786127167624]
[4,15.1,310,26,90,3.89,1.32,300,1,1.73,2.248554913294798,0.76300578034682087]
[4,16.100000000000001,310,26,99,4.22,1.27,300,1,1.73,2.4393063583815029,0.73410404624277459]
[4,15.7,310,27,1,1.37,1.37,100,0,1.37,1,1]
[4,16.600000000000001,310,27,50,1.47,1.1499999999999999,100,1,1.37,1.0729927007299269,0.83941605839416045]
[4,18.3,310,27,60,1.67,1.03,100,1,1.37,1.218978102189781,0.75182481751824815]
[4,20,310,27,70,1.86,0.92,100,1,1.37,1.3576642335766422,0.67153284671532842]
[4,21.6,310,27,80,2.04,0.81,100,1,1.37,1.4890510948905109,0.5912408759124087]
[4,23.1,310,27,90,2.2200000000000002,0.7,100,1,1.37,1.6204379562043796,0.51094890510948898]
[4,24.4,310,27,99,2.38,0.61,100,1,1.37,1.7372262773722627,0.4452554744525547]
[4,11.2,310,27,1,1.69,1.69,200,0,1.69,1,1]
[4,13.7,310,27,50,2.27,1.46,200,1,1.69,1.3431952662721893,0.86390532544378695]
[4,15.1,310,27,60,2.59,1.37,200,1,1.69,1.5325443786982249,0.81065088757396464]
[4,16.5,310,27,70,2.91,1.29,200,1,1.69,1.7218934911242605,0.76331360946745563]
[4,17.8,310,27,80,3.23,1.21,200,1,1.69,1.9112426035502958,0.71597633136094674]
[4,19.2,310,27,90,3.54,1.1299999999999999,200,1,1.69,2.0946745562130178,0.66863905325443784]
[4,20.399999999999999,310,27,99,3.82,1.06,200,1,1.69,2.2603550295857988,0.6272189349112427]
[4,9.1,310,27,1,1.8,1.8,300,0,1.8,1,1]
[4,11.5,310,27,50,2.62,1.61,300,1,1.8,1.4555555555555555,0.89444444444444449]
[4,12.6,310,27,60,3.01,1.54,300,1,1.8,1.6722222222222221,0.85555555555555551]
[4,13.7,310,27,70,3.39,1.48,300,1,1.8,1.8833333333333333,0.82222222222222219]
[4,14.8,310,27,80,3.77,1.42,300,1,1.8,2.0944444444444446,0.78888888888888886]
[4,15.9,310,27,90,4.1500000000000004,1.36,300,1,1.8,2.3055555555555558,0.75555555555555554]
[4,16.8,310,27,99,4.49,1.31,300,1,1.8,2.4944444444444445,0.72777777777777775]
[4,13.4,380,21,1,1.1000000000000001,1.1000000000000001,100,0,1.1000000000000001,1,1]
[4,13.4,380,21,50,1.0900000000000001,1.0900000000000001,100,0,1.0900000000000001,1,1]
[4,13.7,380,21,60,1.1299999999999999,0.94,100,1,1.0900000000000001,1.0366972477064218,0.86238532110091737]
[4,15,380,21,70,1.28,0.84,100,1,1.0900000000000001,1.1743119266055044,0.77064220183486232]
[4,16.2,380,21,80,1.42,0.73,100,1,1.0900000000000001,1.3027522935779814,0.66972477064220182]
[4,17.5,380,21,90,1.57,0.63,100,1,1.0900000000000001,1.4403669724770642,0.57798165137614677]
[4,18.5,380,21,99,1.69,0.54,100,1,1.0900000000000001,1.5504587155963301,0.49541284403669722]
[4,10.1,380,21,1,1.42,1.42,200,0,1.42,1,1]
[4,10.6,380,21,50,1.55,1.29,200,1,1.42,1.091549295774648,0.90845070422535223]
[4,11.7,380,21,60,1.8,1.22,200,1,1.42,1.267605633802817,0.85915492957746487]
[4,12.8,380,21,70,2.04,1.1399999999999999,200,1,1.42,1.4366197183098592,0.80281690140845063]
[4,13.8,380,21,80,2.29,1.06,200,1,1.42,1.6126760563380282,0.74647887323943674]
[4,14.9,380,21,90,2.5299999999999998,0.99,200,1,1.42,1.7816901408450703,0.69718309859154937]
[4,15.8,380,21,99,2.75,0.92,200,1,1.42,1.9366197183098592,0.647887323943662]
[4,8.4,380,21,1,1.53,1.53,300,0,1.53,1,1]
[4,9.1999999999999993,380,21,50,1.83,1.42,300,1,1.53,1.196078431372549,0.92810457516339862]
[4,10.1,380,21,60,2.13,1.36,300,1,1.53,1.392156862745098,0.88888888888888895]
[4,10.9,380,21,70,2.42,1.3,300,1,1.53,1.5816993464052287,0.84967320261437906]
[4,11.8,380,21,80,2.72,1.24,300,1,1.53,1.7777777777777779,0.81045751633986929]
[4,12.6,380,21,90,3.02,1.18,300,1,1.53,1.9738562091503267,0.7712418300653594]
[4,13.4,380,21,99,3.29,1.1299999999999999,300,1,1.53,2.1503267973856208,0.7385620915032679]
[4,14,380,22,1,1.1599999999999999,1.1599999999999999,100,{"$f":"IF(F1366<>G1366,1,0)","v":0},1.1599999999999999,{"$f":"F1366/J1366","v":1},1]
[4,13.9,380,22,50,1.1599999999999999,1.1599999999999999,100,0,1.1599999999999999,1,{"$f":"G1367/J1367","v":1}]
[4,14.5,380,22,60,1.22,0.98,100,1,1.1599999999999999,1.0517241379310345,0.84482758620689657]
[4,15.8,380,22,70,1.38,0.87,100,1,{"$f":"IF(F1369/G1369=1,F1369,J1368)","v":1.1599999999999999},1.1896551724137931,0.75]
[4,17.2,380,22,80,1.53,0.76,100,1,1.1599999999999999,1.3189655172413794,0.65517241379310354]
[4,18.399999999999999,380,22,90,1.68,0.65,100,1,1.1599999999999999,1.4482758620689655,0.56034482758620696]
[4,19.600000000000001,380,22,99,1.81,0.56000000000000005,100,1,1.1599999999999999,1.5603448275862071,0.48275862068965525]
[4,10.4,380,22,1,1.5,1.5,200,0,1.5,1,1]
[4,11.2,380,22,50,1.69,1.35,200,1,1.5,1.1266666666666667,0.9]
[4,12.4,380,22,60,1.95,1.27,200,1,1.5,1.3,0.84666666666666668]
[4,13.5,380,22,70,2.21,1.19,200,1,1.5,1.4733333333333334,0.79333333333333333]
[4,14.6,380,22,80,2.4700000000000002,1.1100000000000001,200,1,1.5,1.6466666666666667,0.7400000000000001]
[4,15.7,380,22,90,2.73,1.03,200,1,1.5,1.82,0.68666666666666665]
[4,16.7,380,22,99,2.96,0.96,200,1,1.5,1.9733333333333334,0.64]
[4,8.6,380,22,1,1.62,1.62,300,0,1.62,1,1]
[4,9.6999999999999993,380,22,50,2,1.49,300,1,1.62,1.2345679012345678,0.91975308641975306]
[4,10.6,380,22,60,2.31,1.42,300,1,1.62,1.4259259259259258,0.87654320987654311]
[4,11.5,380,22,70,2.63,1.36,300,1,1.62,1.6234567901234567,0.83950617283950613]
[4,12.4,380,22,80,2.94,1.3,300,1,1.62,1.8148148148148147,0.80246913580246915]
[4,13.3,380,22,90,3.26,1.24,300,1,1.62,2.0123456790123453,0.76543209876543206]
[4,14.1,380,22,99,3.54,1.18,300,1,1.62,2.1851851851851851,0.72839506172839497]
[4,14.5,380,23,1,1.23,1.23,100,0,1.23,1,1]
[4,14.5,380,23,50,1.22,1.22,100,0,1.22,1,1]
[4,15.3,380,23,60,1.32,1.01,100,1,1.22,1.0819672131147542,0.82786885245901642]
[4,16.7,380,23,70,1.48,0.89,100,1,1.22,1.2131147540983607,0.72950819672131151]
[4,18.100000000000001,380,23,80,1.64,0.78,100,1,1.22,1.3442622950819672,0.63934426229508201]
[4,19.399999999999999,380,23,90,1.8,0.67,100,1,1.22,1.4754098360655739,0.54918032786885251]
[4,20.6,380,23,99,1.93,0.56999999999999995,100,1,1.22,1.5819672131147542,0.46721311475409832]
[4,10.8,380,23,1,1.58,1.58,200,0,1.58,1,1]
[4,11.9,380,23,50,1.83,1.41,200,1,1.58,1.1582278481012658,0.89240506329113911]
[4,13.1,380,23,60,2.11,1.32,200,1,1.58,1.3354430379746833,0.83544303797468356]
[4,14.2,380,23,70,2.39,1.24,200,1,1.58,1.5126582278481013,0.78481012658227844]
[4,15.4,380,23,80,2.66,1.1499999999999999,200,1,1.58,1.6835443037974684,0.72784810126582267]
[4,16.600000000000001,380,23,90,2.93,1.07,200,1,1.58,1.8544303797468356,0.67721518987341778]
[4,17.600000000000001,380,23,99,3.17,0.99,200,1,1.58,2.0063291139240507,0.62658227848101267]
[4,8.9,380,23,1,1.71,1.71,300,0,1.71,1,1]
[4,10.199999999999999,380,23,50,2.17,1.55,300,1,1.71,1.2690058479532162,0.9064327485380117]
[4,11.2,380,23,60,2.5,1.49,300,1,1.71,1.4619883040935673,0.87134502923976609]
[4,12.1,380,23,70,2.84,1.42,300,1,1.71,1.6608187134502923,0.83040935672514615]
[4,13.1,380,23,80,3.17,1.35,300,1,1.71,1.8538011695906433,0.78947368421052644]
[4,14,380,23,90,3.51,1.29,300,1,1.71,2.0526315789473681,0.75438596491228072]
[4,14.9,380,23,99,3.8,1.23,300,1,1.71,2.2222222222222223,0.7192982456140351]
[4,15.1,380,24,1,1.29,1.29,100,0,1.29,1,1]
[4,14.6,380,24,50,1.24,1.17,100,1,1.29,0.96124031007751931,0.90697674418604646]
[4,16.2,380,24,60,1.42,1.04,100,1,1.29,1.1007751937984496,0.80620155038759689]
[4,17.600000000000001,380,24,70,1.59,0.92,100,1,1.29,1.2325581395348837,0.71317829457364346]
[4,19.100000000000001,380,24,80,1.75,0.8,100,1,1.29,1.3565891472868217,0.62015503875968991]
[4,20.5,380,24,90,1.92,0.69,100,1,1.29,1.4883720930232558,0.53488372093023251]
[4,21.7,380,24,99,2.06,0.59,100,1,1.29,1.5968992248062015,0.4573643410852713]
[4,11.1,380,24,1,1.66,1.66,200,0,1.66,1,1]
[4,12.5,380,24,50,1.98,1.46,200,1,1.66,1.1927710843373494,0.87951807228915668]
[4,13.8,380,24,60,2.27,1.37,200,1,1.66,1.3674698795180724,0.82530120481927727]
[4,15,380,24,70,2.57,1.28,200,1,1.66,1.5481927710843373,0.77108433734939763]
[4,16.2,380,24,80,2.85,1.19,200,1,1.66,1.7168674698795181,0.7168674698795181]
[4,17.5,380,24,90,3.14,1.1000000000000001,200,1,1.66,1.8915662650602412,0.66265060240963869]
[4,18.600000000000001,380,24,99,3.39,1.02,200,1,1.66,2.0421686746987953,0.6144578313253013]
[4,9.1,380,24,1,1.8,1.8,300,0,1.8,1,1]
[4,10.7,380,24,50,2.35,1.62,300,1,1.8,1.3055555555555556,0.9]
[4,11.7,380,24,60,2.7,1.55,300,1,1.8,1.5,0.86111111111111116]
[4,12.7,380,24,70,3.06,1.48,300,1,1.8,1.7,0.82222222222222219]
[4,13.7,380,24,80,3.41,1.41,300,1,1.8,1.8944444444444444,0.78333333333333321]
[4,14.8,380,24,90,3.76,1.33,300,1,1.8,2.0888888888888886,0.73888888888888893]
[4,15.7,380,24,99,4.08,1.27,300,1,1.8,2.2666666666666666,0.7055555555555556]
[4,15.7,380,25,1,1.36,1.36,100,0,1.36,1,1]
[4,15.4,380,25,50,1.33,1.2,100,{"$f":"IF(F1430<>G1430,1,0)","v":1},1.36,{"$f":"F1430/J1430","v":0.9779411764705882},0.88235294117647045]
[4,17,380,25,60,1.52,1.07,100,1,1.36,1.1176470588235294,{"$f":"G1431/J1431","v":0.78676470588235292}]
[4,18.600000000000001,380,25,70,1.7,0.95,100,1,1.36,1.2499999999999998,0.69852941176470584]
[4,20.100000000000001,380,25,80,1.87,0.82,100,1,{"$f":"IF(F1433/G1433=1,F1433,J1432)","v":1.36},1.375,0.6029411764705882]
[4,21.5,380,25,90,2.0299999999999998,0.7,100,1,1.36,1.4926470588235292,0.51470588235294112]
[4,22.7,380,25,99,2.1800000000000002,0.6,100,1,1.36,1.6029411764705883,0.44117647058823523]
[4,11.5,380,25,1,1.74,1.74,200,0,1.74,1,1]
[4,13.1,380,25,50,2.13,1.51,200,1,1.74,1.2241379310344827,0.86781609195402298]
[4,14.5,380,25,60,2.44,1.42,200,1,1.74,1.4022988505747127,0.81609195402298851]
[4,15.8,380,25,70,2.75,1.32,200,1,1.74,1.5804597701149425,0.75862068965517249]
[4,17.100000000000001,380,25,80,3.05,1.23,200,1,1.74,1.7528735632183907,0.7068965517241379]
[4,18.399999999999999,380,25,90,3.35,1.1299999999999999,200,1,1.74,1.9252873563218391,0.64942528735632177]
[4,19.5,380,25,99,3.61,1.05,200,1,1.74,2.0747126436781609,0.60344827586206895]
[4,9.4,380,25,1,1.89,1.89,300,0,1.89,1,1]
[4,11.2,380,25,50,2.5299999999999998,1.68,300,1,1.89,1.3386243386243386,0.88888888888888895]
[4,12.3,380,25,60,2.9,1.61,300,1,1.89,1.5343915343915344,0.85185185185185197]
[4,13.4,380,25,70,3.28,1.53,300,1,1.89,1.7354497354497354,0.80952380952380953]
[4,14.4,380,25,80,3.66,1.46,300,1,1.89,1.9365079365079367,0.77248677248677255]
[4,15.5,380,25,90,4.03,1.38,300,1,1.89,2.1322751322751325,0.73015873015873012]
[4,16.5,380,25,99,4.3600000000000003,1.31,300,1,1.89,2.306878306878307,0.69312169312169314]
[4,16.2,380,26,1,1.42,1.42,100,0,1.42,1,1]
[4,16.2,380,26,50,1.43,1.24,100,1,1.42,1.0070422535211268,0.87323943661971837]
[4,17.899999999999999,380,26,60,1.62,1.1000000000000001,100,1,1.42,1.1408450704225352,0.77464788732394374]
[4,19.5,380,26,70,1.81,0.97,100,1,1.42,1.2746478873239437,0.68309859154929575]
[4,21,380,26,80,1.98,0.84,100,1,1.42,1.3943661971830987,0.59154929577464788]
[4,22.5,380,26,90,2.16,0.71,100,1,1.42,1.5211267605633805,0.5]
[4,23.8,380,26,99,2.31,0.61,100,1,1.42,1.6267605633802817,0.42957746478873243]
[4,11.8,380,26,1,1.83,1.83,200,0,1.83,1,1]
[4,13.8,380,26,50,2.29,1.57,200,1,1.83,1.2513661202185793,0.85792349726775952]
[4,15.2,380,26,60,2.61,1.46,200,1,1.83,1.4262295081967211,0.79781420765027322]
[4,16.600000000000001,380,26,70,2.94,1.36,200,1,1.83,1.6065573770491803,0.74316939890710387]
[4,18,380,26,80,3.26,1.27,200,1,1.83,1.7814207650273222,0.69398907103825136]
[4,19.3,380,26,90,3.57,1.17,200,1,1.83,1.9508196721311475,0.6393442622950819]
[4,20.5,380,26,99,3.85,1.08,200,1,1.83,2.1038251366120218,0.5901639344262295]
[4,9.6,380,26,1,1.97,1.97,300,0,1.97,1,1]
[4,11.8,380,26,50,2.72,1.75,300,1,1.97,1.3807106598984773,0.8883248730964467]
[4,12.9,380,26,60,3.11,1.66,300,1,1.97,1.5786802030456852,0.84263959390862941]
[4,14,380,26,70,3.51,1.59,300,1,1.97,1.781725888324873,0.80710659898477166]
[4,15.2,380,26,80,3.91,1.51,300,1,1.97,1.984771573604061,0.76649746192893398]
[4,16.3,380,26,90,4.3,1.43,300,1,1.97,2.1827411167512691,0.7258883248730964]
[4,17.3,380,26,99,4.6500000000000004,1.36,300,1,1.97,2.3604060913705585,0.69035532994923865]
[4,16.8,380,27,1,1.49,1.49,100,0,1.49,1,1]
[4,17,380,27,50,1.52,1.27,100,1,1.49,1.0201342281879195,0.8523489932885906]
[4,18.8,380,27,60,1.72,1.1299999999999999,100,1,1.49,1.1543624161073824,0.75838926174496635]
[4,20.399999999999999,380,27,70,1.91,0.99,100,1,1.49,1.2818791946308725,0.66442953020134232]
[4,22,380,27,80,2.1,0.86,100,1,1.49,1.4093959731543624,0.57718120805369122]
[4,23.6,380,27,90,2.2799999999999998,0.73,100,1,1.49,1.530201342281879,0.48993288590604028]
[4,24.9,380,27,99,2.4300000000000002,0.61,100,1,1.49,1.6308724832214767,0.40939597315436244]
[4,12.2,380,27,1,1.91,1.91,200,0,1.91,1,1]
[4,14.5,380,27,50,2.4500000000000002,1.62,200,1,1.91,1.2827225130890054,0.84816753926701582]
[4,16,380,27,60,2.79,1.51,200,1,1.91,1.4607329842931938,0.79057591623036649]
[4,17.399999999999999,380,27,70,3.13,1.41,200,1,1.91,1.6387434554973823,0.73821989528795806]
[4,18.899999999999999,380,27,80,3.46,1.3,200,1,1.91,1.8115183246073299,0.68062827225130895]
[4,20.3,380,27,90,3.79,1.2,200,1,1.91,1.9842931937172776,0.62827225130890052]
[4,21.5,380,27,99,4.08,1.1000000000000001,200,1,1.91,2.1361256544502618,0.5759162303664922]
[4,9.9,380,27,1,2.06,2.06,300,0,2.06,1,1]
[4,12.3,380,27,50,2.91,1.81,300,1,2.06,1.412621359223301,0.87864077669902918]
[4,13.5,380,27,60,3.33,1.72,300,1,2.06,1.616504854368932,0.83495145631067957]
[4,14.7,380,27,70,3.75,1.64,300,1,2.06,1.820388349514563,0.79611650485436891]
[4,15.9,380,27,80,4.17,1.55,300,1,2.06,2.0242718446601939,0.75242718446601942]
[4,17.100000000000001,380,27,90,4.58,1.47,300,1,2.06,2.2233009708737863,0.71359223300970875]
[4,18.2,380,27,99,4.96,1.4,300,1,2.06,2.407766990291262,0.67961165048543681]
[5,9.1,100,21,1,0.48,0.48,100,0,0.48,1,1]
[5,9.8000000000000007,100,21,50,0.56000000000000005,0.44,100,1,0.48,1.1666666666666667,0.91666666666666674]
[5,10.7,100,21,60,0.66,0.43,100,{"$f":"IF(F1494<>G1494,1,0)","v":1},0.48,{"$f":"F1494/J1494","v":1.3750000000000002},0.89583333333333337]
[5,11.5,100,21,70,0.76,0.42,100,1,0.48,1.5833333333333335,{"$f":"G1495/J1495","v":0.875}]
[5,12.4,100,21,80,0.86,0.4,100,1,0.48,1.7916666666666667,0.83333333333333337]
[5,13.3,100,21,90,0.96,0.39,100,1,{"$f":"IF(F1497/G1497=1,F1497,J1496)","v":0.48},2,0.81250000000000011]
[5,14,100,21,99,1.05,0.38,100,1,0.48,2.1875,0.79166666666666674]
[5,7.2,100,21,1,0.51,0.51,200,0,0.51,1,1]
[5,7.8,100,21,50,0.66,0.49,200,1,0.51,1.2941176470588236,0.96078431372549011]
[5,8.3000000000000007,100,21,60,0.77,0.48,200,1,0.51,1.5098039215686274,0.94117647058823528]
[5,8.8000000000000007,100,21,70,0.89,0.48,200,1,0.51,1.7450980392156863,0.94117647058823528]
[5,9.3000000000000007,100,21,80,1.01,0.47,200,1,0.51,1.9803921568627452,0.92156862745098034]
[5,9.8000000000000007,100,21,90,1.1299999999999999,0.47,200,1,0.51,2.2156862745098036,0.92156862745098034]
[5,10.3,100,21,99,1.23,0.46,200,1,0.51,2.4117647058823528,0.90196078431372551]
[5,6.5,100,21,1,0.51,0.51,300,0,0.51,1,1]
[5,6.9,100,21,50,0.68,0.5,300,1,0.51,1.3333333333333335,0.98039215686274506]
[5,7.3,100,21,60,0.8,0.5,300,1,0.51,1.5686274509803921,0.98039215686274506]
[5,7.6,100,21,70,0.92,0.49,300,1,0.51,1.803921568627451,0.96078431372549011]
[5,8,100,21,80,1.05,0.49,300,1,0.51,2.0588235294117649,0.96078431372549011]
[5,8.3000000000000007,100,21,90,1.17,0.48,300,1,0.51,2.2941176470588234,0.94117647058823528]
[5,8.6,100,21,99,1.28,0.48,300,1,0.51,2.5098039215686274,0.94117647058823528]
[5,9.4,100,22,1,0.51,0.51,100,0,0.51,1,1]
[5,10.3,100,22,50,0.62,0.47,100,1,0.51,1.2156862745098038,0.92156862745098034]
[5,11.2,100,22,60,0.72,0.45,100,1,0.51,1.4117647058823528,0.88235294117647056]
[5,12.1,100,22,70,0.83,0.44,100,1,0.51,1.6274509803921569,0.86274509803921573]
[5,13,100,22,80,0.94,0.42,100,1,0.51,1.8431372549019607,0.82352941176470584]
[5,14,100,22,90,1.05,0.41,100,1,0.51,2.0588235294117649,0.8039215686274509]
[5,14.8,100,22,99,1.1399999999999999,0.4,100,1,0.51,2.2352941176470584,0.78431372549019607]
[5,7.3,100,22,1,0.54,0.54,200,0,0.54,1,1]
[5,8.1,100,22,50,0.72,0.52,200,1,0.54,1.3333333333333333,0.96296296296296291]
[5,8.6,100,22,60,0.85,0.51,200,1,0.54,1.574074074074074,0.94444444444444442]
[5,9.1999999999999993,100,22,70,0.97,0.5,200,1,0.54,1.7962962962962961,0.92592592592592582]
[5,9.6999999999999993,100,22,80,1.1000000000000001,0.5,200,1,0.54,2.0370370370370372,0.92592592592592582]
[5,10.199999999999999,100,22,90,1.22,0.49,200,1,0.54,2.2592592592592591,0.90740740740740733]
[5,10.7,100,22,99,1.33,0.49,200,1,0.54,2.4629629629629628,0.90740740740740733]
[5,6.6,100,22,1,0.54,0.54,300,0,0.54,1,1]
[5,7.1,100,22,50,0.75,0.53,300,1,0.54,1.3888888888888888,0.98148148148148151]
[5,7.5,100,22,60,0.88,0.53,300,1,0.54,1.6296296296296295,0.98148148148148151]
[5,7.9,100,22,70,1.01,0.52,300,1,0.54,1.8703703703703702,0.96296296296296291]
[5,8.1999999999999993,100,22,80,1.1299999999999999,0.52,300,1,0.54,2.0925925925925921,0.96296296296296291]
[5,8.6,100,22,90,1.26,0.51,300,1,0.54,2.333333333333333,0.94444444444444442]
[5,8.9,100,22,99,1.38,0.51,300,1,0.54,2.5555555555555554,0.94444444444444442]
[5,9.6,100,23,1,0.54,0.54,100,0,0.54,1,1]
[5,10.8,100,23,50,0.68,0.49,100,1,0.54,1.2592592592592593,0.90740740740740733]
[5,11.8,100,23,60,0.79,0.48,100,1,0.54,1.462962962962963,0.88888888888888884]
[5,12.7,100,23,70,0.9,0.46,100,1,0.54,1.6666666666666665,0.85185185185185186]
[5,13.7,100,23,80,1.02,0.45,100,1,0.54,1.8888888888888888,0.83333333333333326]
[5,14.7,100,23,90,1.1299999999999999,0.43,100,1,0.54,2.0925925925925921,0.79629629629629628]
[5,15.6,100,23,99,1.23,0.42,100,1,0.54,2.2777777777777777,0.77777777777777768]
[5,7.4,100,23,1,0.56999999999999995,0.56999999999999995,200,0,0.56999999999999995,1,1]
[5,8.4,100,23,50,0.79,0.54,200,1,0.56999999999999995,1.3859649122807018,0.94736842105263175]
[5,9,100,23,60,0.92,0.54,200,1,0.56999999999999995,1.6140350877192984,0.94736842105263175]
[5,9.5,100,23,70,1.05,0.53,200,1,0.56999999999999995,1.8421052631578949,0.92982456140350889]
[5,10.1,100,23,80,1.19,0.52,200,1,0.56999999999999995,2.0877192982456143,0.91228070175438603]
[5,10.7,100,23,90,1.32,0.52,200,1,0.56999999999999995,2.3157894736842106,0.91228070175438603]
[5,11.2,100,23,99,1.44,0.51,200,1,0.56999999999999995,2.5263157894736845,0.89473684210526327]
[5,6.6,100,23,1,0.56999999999999995,0.56999999999999995,300,0,0.56999999999999995,1,1]
[5,7.3,100,23,50,0.82,0.56000000000000005,300,1,0.56999999999999995,1.4385964912280702,0.98245614035087736]
[5,7.7,100,23,60,0.95,0.55000000000000004,300,1,0.56999999999999995,1.6666666666666667,0.9649122807017545]
[5,8.1,100,23,70,1.0900000000000001,0.55000000000000004,300,1,0.56999999999999995,1.9122807017543864,0.9649122807017545]
[5,8.5,100,23,80,1.23,0.54,300,1,0.56999999999999995,2.1578947368421053,0.94736842105263175]
[5,8.9,100,23,90,1.36,0.54,300,1,0.56999999999999995,2.3859649122807021,0.94736842105263175]
[5,9.3000000000000007,100,23,99,1.49,0.54,300,1,0.56999999999999995,2.6140350877192984,0.94736842105263175]
[5,9.9,100,24,1,0.56999999999999995,0.56999999999999995,100,0,0.56999999999999995,1,1]
[5,11.3,100,24,50,0.74,0.51,100,1,0.56999999999999995,1.2982456140350878,0.89473684210526327]
[5,12.3,100,24,60,0.86,0.5,100,1,0.56999999999999995,1.5087719298245614,0.87719298245614041]
[5,13.4,100,24,70,0.98,0.48,100,{"$f":"IF(F1558<>G1558,1,0)","v":1},0.56999999999999995,{"$f":"F1558/J1558","v":1.7192982456140351},0.8421052631578948]
[5,14.4,100,24,80,1.1000000000000001,0.47,100,1,0.56999999999999995,1.929824561403509,{"$f":"G1559/J1559","v":0.82456140350877194}]
[5,15.4,100,24,90,1.22,0.45,100,1,0.56999999999999995,2.1403508771929824,0.78947368421052644]
[5,16.399999999999999,100,24,99,1.32,0.44,100,1,{"$f":"IF(F1561/G1561=1,F1561,J1560)","v":0.56999999999999995},2.3157894736842106,0.77192982456140358]
[5,7.6,100,24,1,0.6,0.6,200,0,0.6,1,1]
[5,8.6999999999999993,100,24,50,0.86,0.56999999999999995,200,1,0.6,1.4333333333333333,0.95]
[5,9.3000000000000007,100,24,60,1,0.56000000000000005,200,1,0.6,1.6666666666666667,0.93333333333333346]
[5,9.9,100,24,70,1.1399999999999999,0.56000000000000005,200,1,0.6,1.9,0.93333333333333346]
[5,10.5,100,24,80,1.28,0.55000000000000004,200,1,0.6,2.1333333333333333,0.91666666666666674]
[5,11.1,100,24,90,1.42,0.54,200,1,0.6,2.3666666666666667,0.90000000000000013]
[5,11.6,100,24,99,1.55,0.54,200,1,0.6,2.5833333333333335,0.90000000000000013]
[5,6.7,100,24,1,0.6,0.6,300,0,0.6,1,1]
[5,7.5,100,24,50,0.89,0.59,300,1,0.6,1.4833333333333334,0.98333333333333328]
[5,8,100,24,60,1.03,0.57999999999999996,300,1,0.6,1.7166666666666668,0.96666666666666667]
[5,8.4,100,24,70,1.18,0.57999999999999996,300,1,0.6,1.9666666666666666,0.96666666666666667]
[5,8.8000000000000007,100,24,80,1.32,0.56999999999999995,300,1,0.6,2.2000000000000002,0.95]
[5,9.1999999999999993,100,24,90,1.47,0.56999999999999995,300,1,0.6,2.4500000000000002,0.95]
[5,9.6,100,24,99,1.6,0.56000000000000005,300,1,0.6,2.666666666666667,0.93333333333333346]
[5,10.1,100,25,1,0.59,0.59,100,0,0.59,1,1]
[5,11.8,100,25,50,0.8,0.54,100,1,0.59,1.3559322033898307,0.91525423728813571]
[5,12.9,100,25,60,0.92,0.52,100,1,0.59,1.5593220338983051,0.88135593220338992]
[5,14,100,25,70,1.05,0.5,100,1,0.59,1.7796610169491527,0.84745762711864414]
[5,15.1,100,25,80,1.18,0.49,100,1,0.59,2,0.83050847457627119]
[5,16.2,100,25,90,1.31,0.47,100,1,0.59,2.2203389830508478,0.79661016949152541]
[5,17.2,100,25,99,1.42,0.45,100,1,0.59,2.406779661016949,0.76271186440677974]
[5,7.7,100,25,1,0.63,0.63,200,0,0.63,1,1]
[5,9,100,25,50,0.93,0.6,200,1,0.63,1.4761904761904763,0.95238095238095233]
[5,9.6,100,25,60,1.08,0.59,200,1,0.63,1.7142857142857144,0.9365079365079364]
[5,10.3,100,25,70,1.23,0.57999999999999996,200,1,0.63,1.9523809523809523,0.92063492063492058]
[5,10.9,100,25,80,1.38,0.57999999999999996,200,1,0.63,2.1904761904761902,0.92063492063492058]
[5,11.5,100,25,90,1.53,0.56999999999999995,200,1,0.63,2.4285714285714284,0.90476190476190466]
[5,12.1,100,25,99,1.66,0.56000000000000005,200,1,0.63,2.6349206349206349,0.88888888888888895]
[5,6.8,100,25,1,0.63,0.63,300,0,0.63,1,1]
[5,7.7,100,25,50,0.96,0.61,300,1,0.63,1.5238095238095237,0.96825396825396826]
[5,8.1999999999999993,100,25,60,1.1100000000000001,0.61,300,1,0.63,1.7619047619047621,0.96825396825396826]
[5,8.6,100,25,70,1.27,0.6,300,1,0.63,2.0158730158730158,0.95238095238095233]
[5,9.1,100,25,80,1.42,0.6,300,1,0.63,2.253968253968254,0.95238095238095233]
[5,9.5,100,25,90,1.58,0.59,300,1,0.63,2.5079365079365079,0.9365079365079364]
[5,9.9,100,25,99,1.71,0.59,300,1,0.63,2.7142857142857144,0.9365079365079364]
[5,10.3,100,26,1,0.62,0.62,100,0,0.62,1,1]
[5,12.4,100,26,50,0.86,0.56000000000000005,100,1,0.62,1.3870967741935483,0.90322580645161299]
[5,13.5,100,26,60,0.99,0.54,100,1,0.62,1.596774193548387,0.87096774193548399]
[5,14.7,100,26,70,1.1299999999999999,0.52,100,1,0.62,1.8225806451612903,0.83870967741935487]
[5,15.8,100,26,80,1.26,0.51,100,1,0.62,2.032258064516129,0.82258064516129037]
[5,17,100,26,90,1.4,0.49,100,1,0.62,2.258064516129032,0.79032258064516125]
[5,18,100,26,99,1.52,0.47,100,1,0.62,2.4516129032258065,0.75806451612903225]
[5,7.8,100,26,1,0.66,0.66,200,0,0.66,1,1]
[5,9.3000000000000007,100,26,50,1,0.63,200,1,0.66,1.5151515151515151,0.95454545454545447]
[5,10,100,26,60,1.1599999999999999,0.62,200,1,0.66,1.7575757575757573,0.93939393939393934]
[5,10.6,100,26,70,1.32,0.61,200,1,0.66,2,0.9242424242424242]
[5,11.3,100,26,80,1.48,0.6,200,1,0.66,2.2424242424242422,0.90909090909090906]
[5,12,100,26,90,1.63,0.59,200,1,0.66,2.4696969696969693,0.89393939393939381]
[5,12.6,100,26,99,1.78,0.59,200,1,0.66,2.6969696969696968,0.89393939393939381]
[5,6.9,100,26,1,0.66,0.66,300,0,0.66,1,1]
[5,8,100,26,50,1.04,0.64,300,1,0.66,1.5757575757575757,0.96969696969696972]
[5,8.4,100,26,60,1.2,0.64,300,1,0.66,1.8181818181818181,0.96969696969696972]
[5,8.9,100,26,70,1.36,0.63,300,1,0.66,2.0606060606060606,0.95454545454545447]
[5,9.4,100,26,80,1.52,0.62,300,1,0.66,2.3030303030303028,0.93939393939393934]
[5,9.8000000000000007,100,26,90,1.69,0.62,300,1,0.66,2.5606060606060606,0.93939393939393934]
[5,10.199999999999999,100,26,99,1.84,0.61,300,1,0.66,2.7878787878787881,0.9242424242424242]
[5,10.6,100,27,1,0.65,0.65,100,0,0.65,1,1]
[5,12.9,100,27,50,0.92,0.57999999999999996,100,1,0.65,1.4153846153846155,0.89230769230769225]
[5,14.2,100,27,60,1.07,0.56000000000000005,100,1,0.65,1.6461538461538463,0.86153846153846159]
[5,15.4,100,27,70,1.21,0.54,100,1,0.65,1.8615384615384614,0.83076923076923082]
[5,16.600000000000001,100,27,80,1.35,0.52,100,{"$f":"IF(F1622<>G1622,1,0)","v":1},0.65,{"$f":"F1622/J1622","v":2.0769230769230771},0.8]
[5,17.8,100,27,90,1.49,0.51,100,1,0.65,2.2923076923076922,{"$f":"G1623/J1623","v":0.7846153846153846}]
[5,18.899999999999999,100,27,99,1.62,0.49,100,1,0.65,2.4923076923076923,0.75384615384615383]
[5,7.9,100,27,1,0.69,0.69,200,0,{"$f":"IF(F1625/G1625=1,F1625,J1624)","v":0.69},1,1]
[5,9.6,100,27,50,1.08,0.65,200,1,0.69,1.5652173913043481,0.94202898550724645]
[5,10.3,100,27,60,1.24,0.64,200,1,0.69,1.7971014492753625,0.92753623188405809]
[5,11.1,100,27,70,1.41,0.63,200,1,0.69,2.0434782608695654,0.91304347826086962]
[5,11.8,100,27,80,1.58,0.63,200,1,0.69,2.2898550724637685,0.91304347826086962]
[5,12.5,100,27,90,1.75,0.62,200,1,0.69,2.5362318840579712,0.89855072463768126]
[5,13.1,100,27,99,1.9,0.61,200,1,0.69,2.7536231884057973,0.88405797101449279]
[5,7,100,27,1,0.69,0.69,300,0,0.69,1,1]
[5,8.1999999999999993,100,27,50,1.1100000000000001,0.67,300,1,0.69,1.6086956521739133,0.97101449275362328]
[5,8.6999999999999993,100,27,60,1.28,0.66,300,1,0.69,1.8550724637681162,0.95652173913043492]
[5,9.1999999999999993,100,27,70,1.46,0.66,300,1,0.69,2.1159420289855073,0.95652173913043492]
[5,9.6999999999999993,100,27,80,1.63,0.65,300,1,0.69,2.36231884057971,0.94202898550724645]
[5,10.199999999999999,100,27,90,1.8,0.64,300,1,0.69,2.6086956521739135,0.92753623188405809]
[5,10.6,100,27,99,1.96,0.64,300,1,0.69,2.8405797101449277,0.92753623188405809]
[5,11,170,21,1,0.7,0.7,100,0,0.7,1,1]
[5,11.2,170,21,50,0.72,0.63,100,1,0.7,1.0285714285714287,0.9]
[5,12.3,170,21,60,0.85,0.6,100,1,0.7,1.2142857142857144,0.85714285714285721]
[5,13.4,170,21,70,0.97,0.56000000000000005,100,1,0.7,1.3857142857142857,0.80000000000000016]
[5,14.4,170,21,80,1.1000000000000001,0.52,100,1,0.7,1.5714285714285716,0.74285714285714288]
[5,15.5,170,21,90,1.22,0.49,100,1,0.7,1.7428571428571429,0.70000000000000007]
[5,16.5,170,21,99,1.34,0.45,100,1,0.7,1.9142857142857146,0.6428571428571429]
[5,8.4,170,21,1,0.79,0.79,200,0,0.79,1,1]
[5,9.1,170,21,50,0.96,0.74,200,1,0.79,1.2151898734177213,0.93670886075949367]
[5,9.8000000000000007,170,21,60,1.1299999999999999,0.72,200,1,0.79,1.4303797468354429,0.91139240506329111]
[5,10.6,170,21,70,1.3,0.7,200,1,0.79,1.6455696202531644,0.88607594936708856]
[5,11.3,170,21,80,1.47,0.68,200,1,0.79,1.860759493670886,0.86075949367088611]
[5,12,170,21,90,1.64,0.66,200,1,0.79,2.0759493670886076,0.83544303797468356]
[5,12.7,170,21,99,1.79,0.64,200,1,0.79,2.2658227848101267,0.810126582278481]
[5,7.3,170,21,1,0.81,0.81,300,0,0.81,1,1]
[5,8,170,21,50,1.03,0.78,300,1,0.81,1.2716049382716048,0.96296296296296291]
[5,8.5,170,21,60,1.22,0.76,300,1,0.81,1.5061728395061726,0.93827160493827155]
[5,9,170,21,70,1.41,0.75,300,1,0.81,1.7407407407407405,0.92592592592592582]
[5,9.5,170,21,80,1.59,0.74,300,1,0.81,1.962962962962963,0.9135802469135802]
[5,10.1,170,21,90,1.78,0.72,300,1,0.81,2.1975308641975309,0.88888888888888884]
[5,10.6,170,21,99,1.94,0.71,300,1,0.81,2.3950617283950617,0.87654320987654311]
[5,11.3,170,22,1,0.74,0.74,100,0,0.74,1,1]
[5,11.8,170,22,50,0.79,0.66,100,1,0.74,1.0675675675675675,0.891891891891892]
[5,13,170,22,60,0.93,0.62,100,1,0.74,1.2567567567567568,0.83783783783783783]
[5,14.1,170,22,70,1.06,0.57999999999999996,100,1,0.74,1.4324324324324325,0.78378378378378377]
[5,15.2,170,22,80,1.19,0.55000000000000004,100,1,0.74,1.6081081081081081,0.74324324324324331]
[5,16.399999999999999,170,22,90,1.33,0.51,100,1,0.74,1.7972972972972974,0.68918918918918926]
[5,17.399999999999999,170,22,99,1.44,0.47,100,1,0.74,1.9459459459459458,0.63513513513513509]
[5,8.6,170,22,1,0.83,0.83,200,0,0.83,1,1]
[5,9.5,170,22,50,1.05,0.78,200,1,0.83,1.2650602409638556,0.93975903614457834]
[5,10.3,170,22,60,1.23,0.76,200,1,0.83,1.4819277108433735,0.9156626506024097]
[5,11.1,170,22,70,1.42,0.74,200,1,0.83,1.7108433734939759,0.89156626506024095]
[5,11.8,170,22,80,1.6,0.72,200,1,0.83,1.9277108433734942,0.86746987951807231]
[5,12.6,170,22,90,1.78,0.7,200,1,0.83,2.1445783132530121,0.84337349397590355]
[5,13.3,170,22,99,1.94,0.68,200,1,0.83,2.3373493975903616,0.81927710843373502]
[5,7.5,170,22,1,0.86,0.86,300,0,0.86,1,1]
[5,8.3000000000000007,170,22,50,1.1399999999999999,0.82,300,1,0.86,1.3255813953488371,0.95348837209302317]
[5,8.8000000000000007,170,22,60,1.33,0.81,300,1,0.86,1.5465116279069768,0.94186046511627919]
[5,9.4,170,22,70,1.53,0.79,300,1,0.86,1.7790697674418605,0.91860465116279078]
[5,9.9,170,22,80,1.73,0.78,300,1,0.86,2.0116279069767442,0.90697674418604657]
[5,10.5,170,22,90,1.92,0.76,300,1,0.86,2.2325581395348837,0.88372093023255816]
[5,11,170,22,99,2.1,0.75,300,1,0.86,2.4418604651162794,0.87209302325581395]
[5,11.7,170,23,1,0.78,0.78,100,0,0.78,1,1]
[5,12.4,170,23,50,0.87,0.69,100,1,0.78,1.1153846153846154,0.88461538461538447]
[5,13.7,170,23,60,1.01,0.65,100,1,0.78,1.2948717948717949,0.83333333333333337]
[5,14.9,170,23,70,1.1499999999999999,0.61,100,1,0.78,1.4743589743589742,0.78205128205128205]
[5,16.100000000000001,170,23,80,1.29,0.56999999999999995,100,1,0.78,1.6538461538461537,0.73076923076923073]
[5,17.3,170,23,90,1.43,0.53,100,{"$f":"IF(F1686<>G1686,1,0)","v":1},0.78,{"$f":"F1686/J1686","v":1.8333333333333333},0.67948717948717952]
[5,18.3,170,23,99,1.55,0.49,100,1,0.78,1.9871794871794872,{"$f":"G1687/J1687","v":0.62820512820512819}]
[5,8.8000000000000007,170,23,1,0.88,0.88,200,0,0.88,1,1]
[5,9.9,170,23,50,1.1499999999999999,0.82,200,1,{"$f":"IF(F1689/G1689=1,F1689,J1688)","v":0.88},1.3068181818181817,0.93181818181818177]
[5,10.8,170,23,60,1.34,0.8,200,1,0.88,1.5227272727272727,0.90909090909090917]
[5,11.6,170,23,70,1.54,0.77,200,1,0.88,1.75,0.875]
[5,12.4,170,23,80,1.73,0.75,200,1,0.88,1.9659090909090908,0.85227272727272729]
[5,13.2,170,23,90,1.92,0.73,200,1,0.88,2.1818181818181817,0.82954545454545447]
[5,14,170,23,99,2.09,0.71,200,1,0.88,2.375,0.80681818181818177]
[5,7.6,170,23,1,0.91,0.91,300,0,0.91,1,1]
[5,8.6,170,23,50,1.24,0.86,300,1,0.91,1.3626373626373627,0.94505494505494503]
[5,9.1999999999999993,170,23,60,1.45,0.85,300,1,0.91,1.5934065934065933,0.93406593406593397]
[5,9.6999999999999993,170,23,70,1.66,0.83,300,1,0.91,1.8241758241758241,0.91208791208791207]
[5,10.3,170,23,80,1.87,0.82,300,1,0.91,2.0549450549450552,0.90109890109890101]
[5,10.9,170,23,90,2.08,0.8,300,1,0.91,2.2857142857142856,0.87912087912087911]
[5,11.5,170,23,99,2.27,0.79,300,1,0.91,2.4945054945054945,0.86813186813186816]
[5,12.1,170,24,1,0.82,0.82,100,0,0.82,1,1]
[5,13.1,170,24,50,0.94,0.72,100,1,0.82,1.1463414634146341,0.87804878048780488]
[5,14.4,170,24,60,1.0900000000000001,0.68,100,1,0.82,1.3292682926829269,0.8292682926829269]
[5,15.7,170,24,70,1.24,0.63,100,1,0.82,1.5121951219512195,0.76829268292682928]
[5,16.899999999999999,170,24,80,1.39,0.59,100,1,0.82,1.6951219512195121,0.71951219512195119]
[5,18.2,170,24,90,1.54,0.55000000000000004,100,1,0.82,1.878048780487805,0.67073170731707321]
[5,19.3,170,24,99,1.66,0.51,100,1,0.82,2.024390243902439,0.62195121951219512]
[5,9,170,24,1,0.93,0.93,200,0,0.93,1,1]
[5,10.4,170,24,50,1.25,0.86,200,1,0.93,1.3440860215053763,0.92473118279569888]
[5,11.2,170,24,60,1.46,0.83,200,1,0.93,1.5698924731182795,0.89247311827956977]
[5,12.1,170,24,70,1.66,0.81,200,1,0.93,1.7849462365591395,0.87096774193548387]
[5,13,170,24,80,1.86,0.79,200,1,0.93,2,0.84946236559139787]
[5,13.9,170,24,90,2.0699999999999998,0.76,200,1,0.93,2.225806451612903,0.81720430107526876]
[5,14.7,170,24,99,2.25,0.74,200,1,0.93,2.4193548387096775,0.79569892473118276]
[5,7.7,170,24,1,0.96,0.96,300,0,0.96,1,1]
[5,8.9,170,24,50,1.35,0.91,300,1,0.96,1.4062500000000002,0.94791666666666674]
[5,9.5,170,24,60,1.57,0.89,300,1,0.96,1.6354166666666667,0.92708333333333337]
[5,10.1,170,24,70,1.8,0.87,300,1,0.96,1.8750000000000002,0.90625]
[5,10.8,170,24,80,2.02,0.86,300,1,0.96,2.104166666666667,0.89583333333333337]
[5,11.4,170,24,90,2.2400000000000002,0.84,300,1,0.96,2.3333333333333335,0.875]
[5,12,170,24,99,2.44,0.82,300,1,0.96,2.5416666666666665,0.85416666666666663]
[5,12.4,170,25,1,0.87,0.87,100,0,0.87,1,1]
[5,13.7,170,25,50,1.02,0.75,100,1,0.87,1.1724137931034484,0.86206896551724144]
[5,15.1,170,25,60,1.18,0.7,100,1,0.87,1.3563218390804597,0.80459770114942519]
[5,16.5,170,25,70,1.34,0.66,100,1,0.87,1.5402298850574714,0.75862068965517249]
[5,17.8,170,25,80,1.49,0.61,100,1,0.87,1.7126436781609196,0.70114942528735635]
[5,19.100000000000001,170,25,90,1.64,0.56999999999999995,100,1,0.87,1.8850574712643677,0.65517241379310343]
[5,20.3,170,25,99,1.78,0.53,100,1,0.87,2.0459770114942528,0.60919540229885061]
[5,9.1999999999999993,170,25,1,0.97,0.97,200,0,0.97,1,1]
[5,10.8,170,25,50,1.36,0.9,200,1,0.97,1.4020618556701032,0.92783505154639179]
[5,11.7,170,25,60,1.57,0.87,200,1,0.97,1.6185567010309279,0.89690721649484539]
[5,12.7,170,25,70,1.79,0.85,200,1,0.97,1.8453608247422681,0.87628865979381443]
[5,13.6,170,25,80,2,0.82,200,1,0.97,2.061855670103093,0.84536082474226804]
[5,14.5,170,25,90,2.2200000000000002,0.8,200,1,0.97,2.2886597938144333,0.82474226804123718]
[5,15.4,170,25,99,2.41,0.77,200,1,0.97,2.4845360824742269,0.79381443298969079]
[5,7.9,170,25,1,1,1,300,0,1,1,1]
[5,9.1999999999999993,170,25,50,1.47,0.95,300,1,1,1.47,0.95]
[5,9.9,170,25,60,1.7,0.93,300,1,1,1.7,0.93]
[5,10.5,170,25,70,1.93,0.91,300,1,1,1.93,0.91]
[5,11.2,170,25,80,2.17,0.89,300,1,1,2.17,0.89]
[5,11.9,170,25,90,2.4,0.88,300,1,1,2.4,0.88]
[5,12.5,170,25,99,2.61,0.86,300,1,1,2.61,0.86]
[5,12.8,170,26,1,0.91,0.91,100,0,0.91,1,1]
[5,14.4,170,26,50,1.1000000000000001,0.78,100,1,0.91,1.2087912087912089,0.8571428571428571]
[5,15.9,170,26,60,1.27,0.73,100,1,0.91,1.3956043956043955,0.80219780219780212]
[5,17.3,170,26,70,1.43,0.68,100,1,0.91,1.5714285714285714,0.74725274725274726]
[5,18.7,170,26,80,1.59,0.63,100,1,0.91,1.7472527472527473,0.69230769230769229]
[5,20.100000000000001,170,26,90,1.76,0.59,100,1,0.91,1.9340659340659341,0.64835164835164827]
[5,21.3,170,26,99,1.9,0.54,100,{"$f":"IF(F1750<>G1750,1,0)","v":1},0.91,{"$f":"F1750/J1750","v":2.0879120879120876},0.59340659340659341]
[5,9.4,170,26,1,1.02,1.02,200,0,1.02,1,{"$f":"G1751/J1751","v":1}]
[5,11.3,170,26,50,1.46,0.93,200,1,1.02,1.4313725490196079,0.91176470588235292]
[5,12.3,170,26,60,1.69,0.91,200,1,{"$f":"IF(F1753/G1753=1,F1753,J1752)","v":1.02},1.6568627450980391,0.89215686274509809]
[5,13.2,170,26,70,1.92,0.88,200,1,1.02,1.8823529411764706,0.86274509803921573]
[5,14.2,170,26,80,2.15,0.85,200,1,1.02,2.107843137254902,0.83333333333333326]
[5,15.2,170,26,90,2.38,0.83,200,1,1.02,2.333333333333333,0.81372549019607843]
[5,16.100000000000001,170,26,99,2.58,0.8,200,1,1.02,2.5294117647058822,0.78431372549019607]
[5,8,170,26,1,1.05,1.05,300,0,1.05,1,1]
[5,9.5,170,26,50,1.58,0.99,300,1,1.05,1.5047619047619047,0.94285714285714284]
[5,10.199999999999999,170,26,60,1.83,0.97,300,1,1.05,1.7428571428571429,0.92380952380952375]
[5,10.9,170,26,70,2.08,0.95,300,1,1.05,1.980952380952381,0.90476190476190466]
[5,11.7,170,26,80,2.33,0.93,300,1,1.05,2.2190476190476192,0.88571428571428568]
[5,12.4,170,26,90,2.58,0.91,300,1,1.05,2.4571428571428573,0.8666666666666667]
[5,13,170,26,99,2.8,0.9,300,1,1.05,2.6666666666666665,0.8571428571428571]
[5,13.2,170,27,1,0.95,0.95,100,0,0.95,1,1]
[5,15.1,170,27,50,1.18,0.8,100,1,0.95,1.2421052631578948,0.8421052631578948]
[5,16.600000000000001,170,27,60,1.36,0.75,100,1,0.95,1.4315789473684213,0.78947368421052633]
[5,18.100000000000001,170,27,70,1.53,0.7,100,1,0.95,1.6105263157894738,0.73684210526315785]
[5,19.600000000000001,170,27,80,1.7,0.65,100,1,0.95,1.7894736842105263,0.68421052631578949]
[5,21.1,170,27,90,1.87,0.6,100,1,0.95,1.9684210526315791,0.63157894736842102]
[5,22.3,170,27,99,2.02,0.56000000000000005,100,1,0.95,2.1263157894736842,0.58947368421052637]
[5,9.6,170,27,1,1.07,1.07,200,0,1.07,1,1]
[5,11.7,170,27,50,1.57,0.97,200,1,1.07,1.4672897196261683,0.90654205607476623]
[5,12.8,170,27,60,1.82,0.94,200,1,1.07,1.7009345794392523,0.87850467289719614]
[5,13.8,170,27,70,2.06,0.91,200,1,1.07,1.9252336448598131,0.85046728971962615]
[5,14.9,170,27,80,2.2999999999999998,0.89,200,1,1.07,2.1495327102803734,0.83177570093457942]
[5,15.9,170,27,90,2.54,0.86,200,1,1.07,2.3738317757009346,0.80373831775700932]
[5,16.8,170,27,99,2.76,0.83,200,1,1.07,2.5794392523364484,0.77570093457943912]
[5,8.1,170,27,1,1.1000000000000001,1.1000000000000001,300,0,1.1000000000000001,1,1]
[5,9.9,170,27,50,1.7,1.03,300,1,1.1000000000000001,1.5454545454545452,0.93636363636363629]
[5,10.6,170,27,60,1.96,1.01,300,1,1.1000000000000001,1.7818181818181817,0.9181818181818181]
[5,11.4,170,27,70,2.23,0.99,300,1,1.1000000000000001,2.0272727272727269,0.89999999999999991]
[5,12.1,170,27,80,2.4900000000000002,0.97,300,1,1.1000000000000001,2.2636363636363637,0.88181818181818172]
[5,12.9,170,27,90,2.76,0.95,300,1,1.1000000000000001,2.5090909090909088,0.86363636363636354]
[5,13.6,170,27,99,2.99,0.93,300,1,1.1000000000000001,2.7181818181818183,0.84545454545454546]
[5,12.3,240,21,1,0.85,0.85,100,0,0.85,1,1]
[5,12.2,240,21,50,0.84,0.84,100,0,0.84,1,1]
[5,13.1,240,21,60,0.94,0.72,100,1,0.84,1.1190476190476191,0.8571428571428571]
[5,14.3,240,21,70,1.08,0.66,100,1,0.84,1.2857142857142858,0.78571428571428581]
[5,15.5,240,21,80,1.22,0.6,100,1,0.84,1.4523809523809523,0.7142857142857143]
[5,16.600000000000001,240,21,90,1.35,0.54,100,1,0.84,1.6071428571428572,0.6428571428571429]
[5,17.600000000000001,240,21,99,1.47,0.48,100,1,0.84,1.75,0.5714285714285714]
[5,9.3000000000000007,240,21,1,1.01,1.01,200,0,1.01,1,1]
[5,10,240,21,50,1.1599999999999999,0.94,200,1,1.01,1.1485148514851484,0.93069306930693063]
[5,10.9,240,21,60,1.36,0.9,200,1,1.01,1.3465346534653466,0.8910891089108911]
[5,11.7,240,21,70,1.57,0.86,200,1,1.01,1.5544554455445545,0.85148514851485146]
[5,12.6,240,21,80,1.78,0.82,200,1,1.01,1.7623762376237624,0.81188118811881183]
[5,13.5,240,21,90,1.98,0.78,200,1,1.01,1.9603960396039604,0.7722772277227723]
[5,14.3,240,21,99,2.16,0.75,200,1,1.01,2.1386138613861387,0.74257425742574257]
[5,8,240,21,1,1.06,1.06,300,0,1.06,1,1]
[5,8.6999999999999993,240,21,50,1.3,1,300,1,1.06,1.2264150943396226,0.94339622641509424]
[5,9.4,240,21,60,1.53,0.97,300,1,1.06,1.4433962264150944,0.91509433962264142]
[5,10,240,21,70,1.77,0.95,300,1,1.06,1.6698113207547169,0.89622641509433953]
[5,10.7,240,21,80,2,0.92,300,1,1.06,1.8867924528301885,0.86792452830188682]
[5,11.4,240,21,90,2.23,0.89,300,1,1.06,2.1037735849056602,0.83962264150943389]
[5,12,240,21,99,2.44,0.87,300,1,1.06,2.3018867924528301,0.820754716981132]
[5,12.7,240,22,1,0.9,0.9,100,0,0.9,1,1]
[5,12.6,240,22,50,0.88,0.81,100,1,0.9,0.97777777777777775,0.9]
[5,13.8,240,22,60,1.03,0.75,100,1,0.9,1.1444444444444444,0.83333333333333326]
[5,15.1,240,22,70,1.18,0.68,100,1,0.9,1.3111111111111111,0.75555555555555554]
[5,16.3,240,22,80,1.32,0.62,100,1,0.9,1.4666666666666668,0.68888888888888888]
[5,17.5,240,22,90,1.46,0.56000000000000005,100,1,0.9,1.6222222222222222,0.62222222222222223]
[5,18.600000000000001,240,22,99,1.59,0.5,100,1,0.9,1.7666666666666666,0.55555555555555558]
[5,9.6,240,22,1,1.07,1.07,200,{"$f":"IF(F1814<>G1814,1,0)","v":0},1.07,{"$f":"F1814/J1814","v":1},1]
[5,10.5,240,22,50,1.27,0.98,200,1,1.07,1.1869158878504673,{"$f":"G1815/J1815","v":0.9158878504672896}]
[5,11.4,240,22,60,1.49,0.94,200,1,1.07,1.3925233644859811,0.87850467289719614]
[5,12.3,240,22,70,1.71,0.9,200,1,{"$f":"IF(F1817/G1817=1,F1817,J1816)","v":1.07},1.5981308411214952,0.84112149532710279]
[5,13.3,240,22,80,1.93,0.86,200,1,1.07,1.8037383177570092,0.80373831775700932]
[5,14.2,240,22,90,2.15,0.82,200,1,1.07,2.009345794392523,0.76635514018691575]
[5,15,240,22,99,2.34,0.79,200,1,1.07,2.1869158878504669,0.73831775700934577]
[5,8.1999999999999993,240,22,1,1.1200000000000001,1.1200000000000001,300,0,1.1200000000000001,1,1]
[5,9.1,240,22,50,1.43,1.06,300,1,1.1200000000000001,1.2767857142857142,0.9464285714285714]
[5,9.8000000000000007,240,22,60,1.68,1.02,300,1,1.1200000000000001,1.4999999999999998,0.9107142857142857]
[5,10.5,240,22,70,1.92,1,300,1,1.1200000000000001,1.714285714285714,0.89285714285714279]
[5,11.2,240,22,80,2.17,0.97,300,1,1.1200000000000001,1.9374999999999998,0.86607142857142849]
[5,11.9,240,22,90,2.42,0.94,300,1,1.1200000000000001,2.1607142857142856,0.83928571428571419]
[5,12.6,240,22,99,2.64,0.91,300,1,1.1200000000000001,2.3571428571428572,0.8125]
[5,13.2,240,23,1,0.95,0.95,100,0,0.95,1,1]
[5,13.3,240,23,50,0.96,0.85,100,1,0.95,1.0105263157894737,0.89473684210526316]
[5,14.6,240,23,60,1.1200000000000001,0.78,100,1,0.95,1.1789473684210527,0.82105263157894748]
[5,15.9,240,23,70,1.27,0.71,100,1,0.95,1.3368421052631581,0.74736842105263157]
[5,17.2,240,23,80,1.42,0.64,100,1,0.95,1.4947368421052631,0.67368421052631589]
[5,18.5,240,23,90,1.57,0.57999999999999996,100,1,0.95,1.6526315789473687,0.61052631578947369]
[5,19.600000000000001,240,23,99,1.7,0.52,100,1,0.95,1.7894736842105263,0.54736842105263162]
[5,9.8000000000000007,240,23,1,1.1299999999999999,1.1299999999999999,200,0,1.1299999999999999,1,1]
[5,11,240,23,50,1.39,1.03,200,1,1.1299999999999999,1.2300884955752214,0.91150442477876115]
[5,12,240,23,60,1.63,0.99,200,1,1.1299999999999999,1.4424778761061947,0.87610619469026552]
[5,13,240,23,70,1.86,0.95,200,1,1.1299999999999999,1.6460176991150446,0.84070796460177]
[5,14,240,23,80,2.09,0.9,200,1,1.1299999999999999,1.8495575221238938,0.79646017699115057]
[5,14.9,240,23,90,2.3199999999999998,0.86,200,1,1.1299999999999999,2.0530973451327434,0.76106194690265494]
[5,15.8,240,23,99,2.52,0.82,200,1,1.1299999999999999,2.2300884955752216,0.72566371681415931]
[5,8.4,240,23,1,1.19,1.19,300,0,1.19,1,1]
[5,9.5,240,23,50,1.57,1.1100000000000001,300,1,1.19,1.3193277310924372,0.93277310924369761]
[5,10.199999999999999,240,23,60,1.83,1.08,300,1,1.19,1.5378151260504203,0.90756302521008414]
[5,11,240,23,70,2.09,1.05,300,1,1.19,1.7563025210084033,0.88235294117647067]
[5,11.7,240,23,80,2.35,1.02,300,1,1.19,1.9747899159663866,0.85714285714285721]
[5,12.5,240,23,90,2.61,0.98,300,1,1.19,2.1932773109243699,0.82352941176470595]
[5,13.1,240,23,99,2.85,0.96,300,1,1.19,2.3949579831932777,0.80672268907563027]
[5,13.6,240,24,1,1,1,100,0,1,1,1]
[5,14,240,24,50,1.05,0.88,100,1,1,1.05,0.88]
[5,15.4,240,24,60,1.21,0.81,100,1,1,1.21,0.81]
[5,16.8,240,24,70,1.37,0.74,100,1,1,1.37,0.74]
[5,18.100000000000001,240,24,80,1.53,0.67,100,1,1,1.53,0.67]
[5,19.5,240,24,90,1.68,0.6,100,1,1,1.68,0.6]
[5,20.6,240,24,99,1.82,0.54,100,1,1,1.82,0.54]
[5,10.1,240,24,1,1.19,1.19,200,0,1.19,1,1]
[5,11.5,240,24,50,1.52,1.08,200,1,1.19,1.277310924369748,0.90756302521008414]
[5,12.6,240,24,60,1.76,1.03,200,1,1.19,1.4789915966386555,0.86554621848739499]
[5,13.6,240,24,70,2.0099999999999998,0.99,200,1,1.19,1.6890756302521008,0.83193277310924374]
[5,14.7,240,24,80,2.25,0.94,200,1,1.19,1.8907563025210086,0.78991596638655459]
[5,15.7,240,24,90,2.4900000000000002,0.9,200,1,1.19,2.0924369747899161,0.75630252100840345]
[5,16.600000000000001,240,24,99,2.71,0.86,200,1,1.19,2.2773109243697478,0.72268907563025209]
[5,8.6,240,24,1,1.25,1.25,300,0,1.25,1,1]
[5,9.9,240,24,50,1.7,1.1599999999999999,300,1,1.25,1.3599999999999999,0.92799999999999994]
[5,10.7,240,24,60,1.98,1.1299999999999999,300,1,1.25,1.5840000000000001,0.90399999999999991]
[5,11.5,240,24,70,2.2599999999999998,1.0900000000000001,300,1,1.25,1.8079999999999998,0.87200000000000011]
[5,12.3,240,24,80,2.54,1.06,300,1,1.25,2.032,0.84800000000000009]
[5,13,240,24,90,2.81,1.03,300,1,1.25,2.2480000000000002,0.82400000000000007]
[5,13.8,240,24,99,3.06,1,300,1,1.25,2.448,0.8]
[5,14.1,240,25,1,1.06,1.06,100,0,1.06,1,1]
[5,14.7,240,25,50,1.1299999999999999,0.91,100,1,1.06,1.0660377358490565,0.85849056603773588]
[5,16.2,240,25,60,1.3,0.84,100,1,1.06,1.2264150943396226,0.79245283018867918]
[5,17.600000000000001,240,25,70,1.47,0.76,100,1,1.06,1.3867924528301885,0.71698113207547165]
[5,19.100000000000001,240,25,80,1.64,0.69,100,1,1.06,1.5471698113207546,0.65094339622641506]
[5,20.5,240,25,90,1.8,0.61,100,1,1.06,1.6981132075471699,0.57547169811320753]
[5,21.7,240,25,99,1.94,0.55000000000000004,100,1,1.06,1.8301886792452828,0.51886792452830188]
[5,10.4,240,25,1,1.25,1.25,200,0,1.25,1,1]
[5,12,240,25,50,1.64,1.1200000000000001,200,{"$f":"IF(F1878<>G1878,1,0)","v":1},1.25,{"$f":"F1878/J1878","v":1.3119999999999998},0.89600000000000013]
[5,13.2,240,25,60,1.9,1.07,200,1,1.25,1.52,{"$f":"G1879/J1879","v":0.85600000000000009}]
[5,14.3,240,25,70,2.16,1.03,200,1,1.25,1.7280000000000002,0.82400000000000007]
[5,15.4,240,25,80,2.42,0.98,200,1,{"$f":"IF(F1881/G1881=1,F1881,J1880)","v":1.25},1.9359999999999999,0.78400000000000003]
[5,16.5,240,25,90,2.67,0.93,200,1,1.25,2.1360000000000001,0.74399999999999999]
[5,17.5,240,25,99,2.9,0.89,200,1,1.25,2.3199999999999998,0.71199999999999997]
[5,8.6999999999999993,240,25,1,1.31,1.31,300,0,1.31,1,1]
[5,10.3,240,25,50,1.84,1.21,300,1,1.31,1.4045801526717556,0.92366412213740456]
[5,11.1,240,25,60,2.14,1.18,300,1,1.31,1.633587786259542,0.9007633587786259]
[5,12,240,25,70,2.4300000000000002,1.1399999999999999,300,1,1.31,1.8549618320610688,0.87022900763358768]
[5,12.8,240,25,80,2.73,1.1100000000000001,300,1,1.31,2.0839694656488548,0.84732824427480924]
[5,13.6,240,25,90,3.02,1.07,300,1,1.31,2.3053435114503817,0.81679389312977102]
[5,14.4,240,25,99,3.29,1.04,300,1,1.31,2.5114503816793894,0.79389312977099236]
[5,14.5,240,26,1,1.1100000000000001,1.1100000000000001,100,0,1.1100000000000001,1,1]
[5,15.4,240,26,50,1.22,0.94,100,1,1.1100000000000001,1.099099099099099,0.84684684684684675]
[5,17,240,26,60,1.4,0.86,100,1,1.1100000000000001,1.261261261261261,0.77477477477477474]
[5,18.5,240,26,70,1.58,0.78,100,1,1.1100000000000001,1.4234234234234233,0.70270270270270263]
[5,20,240,26,80,1.75,0.71,100,1,1.1100000000000001,1.5765765765765765,0.63963963963963955]
[5,21.5,240,26,90,1.92,0.63,100,1,1.1100000000000001,1.7297297297297296,0.56756756756756754]
[5,22.7,240,26,99,2.06,0.56000000000000005,100,1,1.1100000000000001,1.8558558558558558,0.50450450450450446]
[5,10.6,240,26,1,1.31,1.31,200,0,1.31,1,1]
[5,12.6,240,26,50,1.77,1.17,200,1,1.31,1.3511450381679388,0.89312977099236635]
[5,13.8,240,26,60,2.0499999999999998,1.1200000000000001,200,1,1.31,1.5648854961832059,0.85496183206106879]
[5,15,240,26,70,2.3199999999999998,1.06,200,1,1.31,1.7709923664122136,0.80916030534351147]
[5,16.100000000000001,240,26,80,2.59,1.01,200,1,1.31,1.9770992366412212,0.77099236641221369]
[5,17.3,240,26,90,2.86,0.96,200,1,1.31,2.1832061068702289,0.73282442748091592]
[5,18.3,240,26,99,3.11,0.92,200,1,1.31,2.3740458015267172,0.70229007633587781]
[5,8.9,240,26,1,1.37,1.37,300,0,1.37,1,1]
[5,10.7,240,26,50,1.99,1.26,300,1,1.37,1.4525547445255473,0.91970802919708028]
[5,11.6,240,26,60,2.2999999999999998,1.22,300,1,1.37,1.6788321167883209,0.8905109489051094]
[5,12.5,240,26,70,2.62,1.19,300,1,1.37,1.9124087591240875,0.86861313868613133]
[5,13.4,240,26,80,2.93,1.1499999999999999,300,1,1.37,2.1386861313868613,0.83941605839416045]
[5,14.3,240,26,90,3.24,1.1100000000000001,300,1,1.37,2.3649635036496348,0.81021897810218979]
[5,15.1,240,26,99,3.52,1.08,300,1,1.37,2.5693430656934306,0.78832116788321172]
[5,15,240,27,1,1.1599999999999999,1.1599999999999999,100,0,1.1599999999999999,1,1]
[5,16.2,240,27,50,1.31,0.97,100,1,1.1599999999999999,1.1293103448275863,0.8362068965517242]
[5,17.8,240,27,60,1.5,0.89,100,1,1.1599999999999999,1.2931034482758621,0.76724137931034486]
[5,19.399999999999999,240,27,70,1.68,0.8,100,1,1.1599999999999999,1.4482758620689655,0.68965517241379315]
[5,21,240,27,80,1.86,0.73,100,1,1.1599999999999999,1.6034482758620692,0.62931034482758619]
[5,22.5,240,27,90,2.0299999999999998,0.65,100,1,1.1599999999999999,1.75,0.56034482758620696]
[5,23.8,240,27,99,2.19,0.57999999999999996,100,1,1.1599999999999999,1.8879310344827587,0.5]
[5,10.9,240,27,1,1.37,1.37,200,0,1.37,1,1]
[5,13.2,240,27,50,1.9,1.21,200,1,1.37,1.386861313868613,0.88321167883211671]
[5,14.4,240,27,60,2.19,1.1599999999999999,200,1,1.37,1.5985401459854014,0.84671532846715314]
[5,15.7,240,27,70,2.48,1.1000000000000001,200,1,1.37,1.8102189781021896,0.8029197080291971]
[5,16.899999999999999,240,27,80,2.77,1.05,200,1,1.37,2.0218978102189777,0.76642335766423353]
[5,18.100000000000001,240,27,90,3.06,1,200,1,1.37,2.2335766423357661,0.72992700729927007]
[5,19.2,240,27,99,3.31,0.95,200,1,1.37,2.4160583941605838,0.6934306569343065]
[5,9.1,240,27,1,1.44,1.44,300,0,1.44,1,1]
[5,11.1,240,27,50,2.14,1.31,300,1,1.44,1.4861111111111112,0.90972222222222232]
[5,12.1,240,27,60,2.4700000000000002,1.27,300,1,1.44,1.7152777777777779,0.88194444444444453]
[5,13,240,27,70,2.8,1.23,300,1,1.44,1.9444444444444444,0.85416666666666674]
[5,14,240,27,80,3.13,1.19,300,1,1.44,2.1736111111111112,0.82638888888888884]
[5,14.9,240,27,90,3.46,1.1599999999999999,300,1,1.44,2.4027777777777777,0.80555555555555558]
[5,15.8,240,27,99,3.76,1.1200000000000001,300,1,1.44,2.6111111111111112,0.7777777777777779]
[5,13.2,310,21,1,0.95,0.95,100,0,0.95,1,1]
[5,13.2,310,21,50,0.95,0.95,100,0,0.95,1,1]
[5,13.6,310,21,60,1,0.82,100,1,0.95,1.0526315789473684,0.86315789473684212]
[5,14.8,310,21,70,1.1399999999999999,0.73,100,1,0.95,1.2,0.768421052631579]
[5,16,310,21,80,1.29,0.65,100,1,0.95,1.3578947368421053,0.68421052631578949]
[5,17.2,310,21,90,1.43,0.56999999999999995,100,1,0.95,1.5052631578947369,0.6]
[5,18.3,310,21,99,1.55,0.5,100,1,0.95,1.6315789473684212,0.52631578947368418]
[5,10.1,310,21,1,1.19,1.19,200,0,1.19,1,1]
[5,10.6,310,21,50,1.3,1.0900000000000001,200,1,1.19,1.0924369747899161,0.91596638655462193]
[5,11.6,310,21,60,1.53,1.04,200,{"$f":"IF(F1942<>G1942,1,0)","v":1},1.19,{"$f":"F1942/J1942","v":1.2857142857142858},0.87394957983193289]
[5,12.6,310,21,70,1.76,0.98,200,1,1.19,1.4789915966386555,{"$f":"G1943/J1943","v":0.82352941176470595}]
[5,13.5,310,21,80,1.99,0.92,200,1,1.19,1.6722689075630253,0.77310924369747902]
[5,14.5,310,21,90,2.2200000000000002,0.87,200,1,{"$f":"IF(F1945/G1945=1,F1945,J1944)","v":1.19},1.8655462184873952,0.73109243697478998]
[5,15.4,310,21,99,2.42,0.82,200,1,1.19,2.0336134453781511,0.68907563025210083]
[5,8.6,310,21,1,1.27,1.27,300,0,1.27,1,1]
[5,9.3000000000000007,310,21,50,1.51,1.19,300,1,1.27,1.1889763779527558,0.93700787401574792]
[5,10.1,310,21,60,1.78,1.1499999999999999,300,1,1.27,1.4015748031496063,0.90551181102362199]
[5,10.8,310,21,70,2.04,1.1000000000000001,300,1,1.27,1.6062992125984252,0.86614173228346458]
[5,11.6,310,21,80,2.31,1.06,300,1,1.27,1.8188976377952757,0.83464566929133865]
[5,12.4,310,21,90,2.58,1.02,300,1,1.27,2.0314960629921259,0.80314960629921262]
[5,13.1,310,21,99,2.82,0.98,300,1,1.27,2.2204724409448819,0.77165354330708658]
[5,13.7,310,22,1,1.01,1.01,100,0,1.01,1,1]
[5,13.7,310,22,50,1.01,1.01,100,0,1.01,1,1]
[5,14.4,310,22,60,1.0900000000000001,0.85,100,1,1.01,1.0792079207920793,0.84158415841584155]
[5,15.7,310,22,70,1.24,0.76,100,1,1.01,1.2277227722772277,0.75247524752475248]
[5,16.899999999999999,310,22,80,1.39,0.68,100,1,1.01,1.3762376237623761,0.67326732673267331]
[5,18.2,310,22,90,1.54,0.59,100,1,1.01,1.5247524752475248,0.58415841584158412]
[5,19.3,310,22,99,1.66,0.52,100,1,1.01,1.6435643564356435,0.51485148514851486]
[5,10.4,310,22,1,1.26,1.26,200,0,1.26,1,1]
[5,11.1,310,22,50,1.43,1.1499999999999999,200,1,1.26,1.1349206349206349,0.91269841269841268]
[5,12.2,310,22,60,1.68,1.0900000000000001,200,1,1.26,1.3333333333333333,0.86507936507936511]
[5,13.2,310,22,70,1.92,1.03,200,1,1.26,1.5238095238095237,0.81746031746031744]
[5,14.3,310,22,80,2.16,0.97,200,1,1.26,1.7142857142857144,0.76984126984126977]
[5,15.3,310,22,90,2.4,0.91,200,1,1.26,1.9047619047619047,0.72222222222222221]
[5,16.2,310,22,99,2.61,0.86,200,1,1.26,2.0714285714285712,0.68253968253968256]
[5,8.8000000000000007,310,22,1,1.34,1.34,300,0,1.34,1,1]
[5,9.6999999999999993,310,22,50,1.66,1.25,300,1,1.34,1.2388059701492535,0.93283582089552231]
[5,10.6,310,22,60,1.94,1.2,300,1,1.34,1.4477611940298507,0.89552238805970141]
[5,11.4,310,22,70,2.23,1.1599999999999999,300,1,1.34,1.6641791044776117,0.86567164179104461]
[5,12.2,310,22,80,2.5099999999999998,1.1100000000000001,300,1,1.34,1.8731343283582087,0.82835820895522394]
[5,13,310,22,90,2.8,1.07,300,1,1.34,2.08955223880597,0.79850746268656714]
[5,13.7,310,22,99,3.05,1.03,300,1,1.34,2.2761194029850742,0.76865671641791045]
[5,14.2,310,23,1,1.07,1.07,100,0,1.07,1,1]
[5,14.2,310,23,50,1.07,1.07,100,0,1.07,1,1]
[5,15.2,310,23,60,1.18,0.88,100,1,1.07,1.1028037383177569,0.82242990654205606]
[5,16.5,310,23,70,1.34,0.79,100,1,1.07,1.2523364485981308,0.73831775700934577]
[5,17.899999999999999,310,23,80,1.5,0.7,100,1,1.07,1.4018691588785046,0.65420560747663548]
[5,19.2,310,23,90,1.65,0.61,100,1,1.07,1.542056074766355,0.57009345794392519]
[5,20.3,310,23,99,1.79,0.53,100,1,1.07,1.6728971962616821,0.49532710280373832]
[5,10.7,310,23,1,1.33,1.33,200,0,1.33,1,1]
[5,11.7,310,23,50,1.57,1.2,200,1,1.33,1.1804511278195489,0.90225563909774431]
[5,12.8,310,23,60,1.82,1.1399999999999999,200,1,1.33,1.368421052631579,0.85714285714285698]
[5,13.9,310,23,70,2.08,1.07,200,1,1.33,1.5639097744360901,0.80451127819548873]
[5,15,310,23,80,2.34,1.01,200,1,1.33,1.7593984962406013,0.75939849624060152]
[5,16.100000000000001,310,23,90,2.59,0.95,200,1,1.33,1.9473684210526314,0.71428571428571419]
[5,17.100000000000001,310,23,99,2.81,0.89,200,1,1.33,2.1127819548872178,0.66917293233082709]
[5,9.1,310,23,1,1.42,1.42,300,0,1.42,1,1]
[5,10.199999999999999,310,23,50,1.81,1.31,300,1,1.42,1.2746478873239437,0.92253521126760574]
[5,11,310,23,60,2.12,1.26,300,1,1.42,1.4929577464788735,0.88732394366197187]
[5,11.9,310,23,70,2.42,1.21,300,1,1.42,1.704225352112676,0.852112676056338]
[5,12.8,310,23,80,2.72,1.17,300,1,1.42,1.9154929577464792,0.823943661971831]
[5,13.6,310,23,90,3.02,1.1200000000000001,300,1,1.42,2.126760563380282,0.78873239436619724]
[5,14.4,310,23,99,3.29,1.08,300,1,1.42,2.3169014084507045,0.76056338028169024]
[5,14.7,310,24,1,1.1299999999999999,1.1299999999999999,100,0,1.1299999999999999,1,1]
[5,14.5,310,24,50,1.1100000000000001,1.01,100,1,1.1299999999999999,0.98230088495575241,0.89380530973451333]
[5,16,310,24,60,1.28,0.91,100,1,1.1299999999999999,1.1327433628318586,0.80530973451327448]
[5,17.399999999999999,310,24,70,1.45,0.82,100,1,1.1299999999999999,1.2831858407079646,0.72566371681415931]
[5,18.8,310,24,80,1.61,0.72,100,1,1.1299999999999999,1.4247787610619471,0.63716814159292035]
[5,13,310,25,70,2.82,1.32,300,1,1.57,1.7961783439490444,0.84076433121019112]
[5,14.3,310,27,70,3.24,1.42,300,1,1.72,1.8837209302325584,0.82558139534883723]
[5,11.6,380,22,50,1.55,1.29,200,1,1.42,1.091549295774648,0.90845070422535223]
[5,16.899999999999999,380,23,70,1.39,0.86,100,1,1.1599999999999999,1.1982758620689655,0.74137931034482762]
[5,16.2,380,24,99,3.91,1.21,300,1,1.71,2.2865497076023393,0.70760233918128657]
[6,11.2,100,21,60,0.61,0.41,100,1,0.45,1.3555555555555554,0.91111111111111098]
[6,8.8000000000000007,100,21,80,0.98,0.46,300,1,0.48,2.0416666666666665,0.95833333333333337]
[6,9.6999999999999993,100,23,60,0.86,0.51,200,1,0.54,1.5925925925925926,0.94444444444444442]
[6,12.9,100,26,50,0.8,0.53,100,1,0.59,1.3559322033898307,0.89830508474576276]
[6,10.199999999999999,100,26,80,1.46,0.59,300,1,0.63,2.3174603174603172,0.9365079365079364]
[6,14.5,170,22,70,0.99,0.55000000000000004,100,1,0.7,1.4142857142857144,0.78571428571428581]
[6,10.199999999999999,170,24,60,1.48,0.84,300,1,0.91,1.6263736263736264,0.92307692307692302]
[6,10.199999999999999,170,26,1,0.97,0.97,200,0,0.97,1,1]
[6,13.6,170,27,90,2.66,0.91,300,1,1.05,2.5333333333333332,{"$f":"G2519/J2519","v":0.8666666666666667}]
[6,15.4,240,23,90,2.2000000000000002,0.81,200,1,1.07,2.0560747663551404,0.7570093457943925]
[6,15,240,25,50,1.05,0.88,100,1,1.01,1.0396039603960396,0.87128712871287128]
[6,12.6,240,25,70,2.31,1.0900000000000001,300,1,1.25,1.8480000000000001,0.87200000000000011]
[6,18.399999999999999,310,22,90,1.44,0.56000000000000005,100,1,0.95,1.5157894736842106,0.58947368421052637]
[6,12.5,310,23,70,2.27,1.1499999999999999,300,1,1.34,1.6940298507462686,0.85820895522388052]
[6,15.8,310,25,70,2.2799999999999998,1.1100000000000001,200,1,1.4,1.6285714285714286,0.79285714285714293]
[6,18,310,27,99,4.18,1.19,300,1,1.65,2.5333333333333332,0.72121212121212119]
[6,10.3,380,21,50,1.51,1.28,300,1,1.36,1.1102941176470587,0.94117647058823528]
[6,20.9,380,23,99,1.74,0.51,100,1,1.1000000000000001,1.5818181818181818,0.46363636363636362]
[6,14.8,380,24,80,3.07,1.27,300,1,1.62,1.8950617283950615,0.78395061728395055]
[6,15.2,380,27,50,2.15,1.5,200,1,1.75,1.2285714285714284,0.8571428571428571]
[7,10.9,100,22,1,0.45,0.45,100,0,0.45,1,1]
[7,12.1,100,23,90,1.2,0.46,200,1,0.5,2.4,0.92]
[7,16.899999999999999,100,26,80,1.1499999999999999,0.46,100,1,0.56999999999999995,2.0175438596491229,0.80701754385964919]
[7,10.3,100,27,60,1.1599999999999999,0.6,300,1,0.63,1.8412698412698412,0.95238095238095233]
[7,18,170,22,99,1.29,0.41,100,1,0.66,1.9545454545454546,0.6212121212121211]
[7,12.8,170,24,90,2.04,0.75,300,1,0.86,2.3720930232558142,0.87209302325581395]
[7,14.4,170,26,70,1.73,0.8,200,1,0.92,1.8804347826086956,0.86956521739130432]
[7,14.4,240,22,60,0.86,0.68,100,1,0.79,1.0886075949367089,0.86075949367088611]
[7,10,240,23,1,1.05,1.05,300,0,1.05,1,1]
[7,11.6,240,25,50,1.59,1.1000000000000001,300,1,1.18,1.3474576271186443,0.93220338983050854]
[7,15.7,240,25,99,3.03,0.93,300,1,1.18,2.5677966101694913,0.7881355932203391]
[7,12,310,22,50,1.17,1.04,200,1,1.1100000000000001,1.0540540540540539,0.93693693693693691]
[7,17,310,23,70,1.1599999999999999,0.73,100,1,0.96,1.2083333333333333,0.76041666666666663]
[7,11.8,310,24,50,1.68,1.24,300,1,{"$f":"IF(F3481/G3481=1,F3481,J3480)","v":1.34},1.2537313432835819,0.9253731343283581]
[7,21.5,310,27,99,3.38,0.92,200,{"$f":"IF(F3542<>G3542,1,0)","v":1},1.48,{"$f":"F3542/J3542","v":2.2837837837837838},0.6216216216216216]
[7,13.4,380,21,80,2.2200000000000002,1.03,300,1,1.27,1.7480314960629924,0.8110236220472441]
[7,14.2,380,23,60,1.68,1.1499999999999999,200,1,1.34,1.2537313432835819,0.85820895522388052]
[7,17.600000000000001,380,26,50,1.24,1.24,100,0,1.24,1,1]
[7,22.5,380,27,99,3.6,0.95,200,1,1.67,2.1556886227544911,0.56886227544910184]
[8,11.9,100,22,80,0.91,0.41,200,1,0.44,2.0681818181818183,0.93181818181818177]
[8,10.4,100,24,60,0.84,0.49,300,1,0.51,1.6470588235294117,0.96078431372549011]
[8,10.4,100,26,1,0.56000000000000005,0.56000000000000005,200,0,0.56000000000000005,1,1]
[8,12.6,100,27,90,1.61,0.56000000000000005,300,1,0.6,2.6833333333333336,0.93333333333333346]
[8,13.4,170,23,70,1.25,0.65,200,1,0.74,1.6891891891891893,0.8783783783783784]
[8,14.8,170,25,50,0.8,0.66,100,1,{"$f":"IF(F3929/G3929=1,F3929,J3928)","v":0.74},1.0810810810810811,0.891891891891892]
[8,12.7,170,25,70,1.63,0.78,300,1,0.85,1.9176470588235293,0.91764705882352948]
[8,18.3,240,22,90,1.2,0.46,100,1,0.74,1.6216216216216215,0.6216216216216216]
[8,12.9,240,23,70,1.7,0.88,300,1,0.99,1.7171717171717171,0.88888888888888895]
[8,13.5,240,25,50,1.29,0.98,200,1,1.07,1.205607476635514,0.9158878504672896]
[8,17.8,240,26,60,1.1399999999999999,0.77,100,1,0.96,1.1875,0.80208333333333337]
[8,11,310,21,50,1.06,0.99,300,1,1.03,1.029126213592233,0.96116504854368934]
[8,20.9,310,23,99,1.5,0.44,100,1,0.9,1.6666666666666665,0.48888888888888887]
[8,15.1,310,24,80,2.4700000000000002,1.03,300,1,1.26,1.9603174603174605,0.81746031746031744]
[8,25,310,27,99,1.97,0.5,100,1,1.1499999999999999,1.7130434782608697,0.43478260869565222]
[8,15.9,380,22,1,0.92,0.92,100,0,0.92,1,1]
[8,18,380,23,90,2.3199999999999998,0.85,200,1,1.26,1.8412698412698412,0.67460317460317454]
[8,21.6,380,26,80,1.58,0.72,100,1,1.18,1.3389830508474578,0.61016949152542377]
[8,15.6,380,27,60,2.64,1.45,300,1,1.71,1.5438596491228072,0.84795321637426901]
[9,15.1,100,22,80,0.71,0.33,100,1,0.39,1.8205128205128203,0.84615384615384615]
[9,12.5,100,24,90,1.21,0.45,300,1,0.48,2.5208333333333335,0.93750000000000011]
[9,13.6,100,26,70,1.06,0.49,200,1,0.53,2,0.92452830188679236]
[9,19.7,100,27,90,1.25,0.41,100,1,0.54,2.3148148148148149,0.75925925925925919]
[9,11,170,23,1,0.71,0.71,300,0,0.71,1,1]
[9,17.600000000000001,170,25,99,2.0099999999999998,0.61,200,1,0.78,2.5769230769230766,0.78205128205128205]
[9,15.3,170,25,99,2.2000000000000002,0.69,300,1,0.8,2.75,0.86249999999999993]
[9,17.2,170,27,80,1.9,0.73,200,1,0.88,2.1590909090909092,0.82954545454545447]
[9,17,240,23,70,0.93,0.57999999999999996,100,1,0.74,1.2567567567567568,0.78378378378378377]
[9,12.4,240,24,50,1.19,0.94,300,1,0.99,1.202020202020202,0.9494949494949495]
[9,18.7,240,27,80,2.27,0.86,200,1,1.1299999999999999,2.0088495575221241,0.76106194690265494]
[9,13.9,310,21,80,1.7,0.81,300,1,0.95,1.7894736842105263,0.85263157894736852]
[9,14.5,310,23,60,1.28,0.92,200,1,1.04,1.2307692307692308,0.88461538461538458]
[9,17.8,310,26,50,1.02,1.02,100,0,1.02,1,1]
[9,22.2,310,27,99,3.07,0.82,200,1,1.33,2.3082706766917291,0.61654135338345861]
[9,14.3,380,22,60,1.23,0.98,200,1,1.0900000000000001,1.128440366972477,0.89908256880733939]
[9,14.3,380,24,60,1.85,1.21,300,1,1.36,1.3602941176470589,0.88970588235294112]
[9,15.1,380,26,1,1.42,1.42,200,0,1.42,1,1]
[9,19.5,380,27,90,3.67,1.1599999999999999,300,1,1.62,2.2654320987654319,0.71604938271604923]
[10,13.7,100,23,80,0.86,0.38,200,1,0.41,2.0975609756097562,0.92682926829268297]
[10,11.9,100,24,1,0.44,0.44,200,0,0.44,1,1]
[10,12.7,100,25,70,0.94,0.45,300,1,0.48,1.9583333333333333,0.93750000000000011]
[10,13.3,100,27,50,0.76,0.51,200,1,0.53,1.4339622641509433,0.96226415094339623]
[10,13.3,170,23,70,1.1499999999999999,0.61,300,1,0.66,1.7424242424242422,0.9242424242424242]
[10,16.7,170,24,90,1.57,0.56000000000000005,200,1,0.69,2.27536231884058,0.81159420289855089]
[10,21.5,170,26,90,1.34,0.44,100,1,0.7,1.9142857142857146,0.62857142857142867]
[10,12.4,170,27,1,0.85,0.85,300,0,0.85,1,1]
[10,20.7,240,23,99,1.25,0.37,100,1,0.69,1.8115942028985508,0.53623188405797106]
[10,15.3,240,24,80,1.87,0.79,300,1,0.92,2.0326086956521738,0.85869565217391308]
[10,22,240,27,80,1.4,0.57999999999999996,100,1,0.91,1.5384615384615383,{"$f":"G5591/J5591","v":0.63736263736263732}]
[10,16.3,310,22,1,0.73,0.73,100,0,0.73,1,1]
[10,18.100000000000001,310,23,90,1.88,0.69,200,1,0.96,1.9583333333333333,0.71875]
[10,21.6,310,26,80,1.35,0.61,100,1,0.97,1.3917525773195878,0.62886597938144329]
[10,15.9,310,27,60,2.0699999999999998,1.18,300,1,1.34,1.5447761194029848,0.88059701492537301]
[10,16.8,380,22,60,0.79,0.79,100,0,0.79,1,1]
[10,17.7,380,24,90,2.69,0.94,300,1,1.27,2.1181102362204722,0.74015748031496054]
[10,18.7,380,26,70,2.0099999999999998,1.04,200,1,1.34,1.4999999999999998,0.77611940298507465]
[10,24.3,380,27,90,1.66,0.55000000000000004,100,1,1.1200000000000001,1.482142857142857,0.49107142857142855]
[11,12.5,100,21,70,0.52,0.31,300,1,0.32,1.625,0.96875]
[11,12.2,100,23,50,0.41,0.38,300,1,0.38,1.0789473684210527,1]
[11,14.8,100,25,99,1.31,0.41,300,1,0.44,2.9772727272727275,0.93181818181818177]
[11,16.100000000000001,100,27,80,1.18,0.46,200,1,0.5,2.36,{"$f":"G6039/J6039","v":0.92}]
[11,16.899999999999999,170,23,70,0.69,0.43,100,1,0.53,1.3018867924528301,0.81132075471698106]
[11,13.1,170,24,50,0.73,0.64,300,1,0.66,1.106060606060606,0.96969696969696972]
[11,16.2,170,27,60,1.22,0.7,200,1,0.78,1.5641025641025641,0.89743589743589736]
[11,14.4,240,21,80,1.2,0.59,300,1,0.66,1.8181818181818181,0.89393939393939381]
[11,14.9,240,23,60,0.9,0.69,200,1,0.75,1.2,0.91999999999999993]
[11,17.899999999999999,240,26,50,0.8,0.8,100,0,0.8,1,1]
[11,21.8,240,27,99,2.52,0.68,200,1,1,2.52,0.68]
[11,14.5,310,22,1,0.82,0.82,200,0,0.82,1,1]
[11,14.9,310,24,60,1.36,0.94,300,{"$f":"IF(F6422<>G6422,1,0)","v":1},1.03,{"$f":"F6422/J6422","v":1.3203883495145632},0.9126213592233009]
[11,15.8,310,26,1,1.1100000000000001,1.1100000000000001,200,0,1.1100000000000001,1,1]
[11,19.600000000000001,310,27,90,3,0.95,300,1,1.26,2.3809523809523809,0.75396825396825395]
[11,13.6,380,21,1,0.91,0.91,300,0,0.91,1,1]
[11,21.5,380,24,90,1.22,0.47,100,1,0.86,1.4186046511627908,0.54651162790697672]
[11,16.899999999999999,380,25,70,2.04,1.06,300,1,1.27,1.6062992125984252,0.83464566929133865]
[11,17,380,27,50,1.39,1.23,200,1,1.34,1.0373134328358207,0.91791044776119401]
[12,14.3,100,21,99,0.8,0.27,300,1,0.28999999999999998,2.7586206896551726,0.93103448275862077]
[12,16.100000000000001,100,24,90,0.95,0.34,200,1,0.38,2.5,0.89473684210526316]
[12,18.100000000000001,100,26,70,0.71,0.35,100,1,{"$f":"IF(F6745/G6745=1,F6745,J6744)","v":0.42},1.6904761904761905,0.83333333333333326]
[12,13.4,100,27,1,0.47,0.47,300,0,0.47,1,1]
[12,20.399999999999999,170,23,99,0.98,0.28999999999999998,100,1,0.48,2.0416666666666665,0.60416666666666663]
[12,15.6,170,24,80,1.27,0.55000000000000004,300,1,0.6,2.1166666666666667,0.91666666666666674]
[12,17.8,170,27,70,1.34,0.63,200,1,0.73,1.8356164383561646,0.86301369863013699]
[12,16.2,240,21,50,0.48,0.48,100,0,0.48,1,1]
[12,18.2,240,23,90,1.43,0.53,200,1,0.69,2.0724637681159419,0.76811594202898559]
[12,21.5,240,26,80,1.1000000000000001,0.5,100,1,0.75,1.4666666666666668,0.66666666666666663]
[12,16.3,240,27,60,1.52,0.9,300,1,0.98,1.5510204081632653,0.91836734693877553]
[12,16.399999999999999,310,21,80,1.01,0.55000000000000004,200,1,0.67,1.5074626865671641,0.82089552238805974]
[12,15.4,310,24,60,1.19,0.88,300,1,0.94,1.2659574468085106,0.93617021276595747]
[12,18.8,310,26,70,1.59,0.84,200,1,{"$f":"IF(F7193/G7193=1,F7193,J7192)","v":1.03},1.5436893203883495,0.81553398058252424]
[12,24.2,310,27,90,1.42,0.47,100,1,0.91,1.5604395604395602,0.51648351648351642]
[12,15,380,21,70,1.04,0.75,300,1,0.81,1.2839506172839505,0.92592592592592582]
[12,20.2,380,23,99,1.91,0.56000000000000005,200,1,0.92,2.0760869565217388,0.60869565217391308]
[12,20.2,380,25,99,2.87,0.81,300,1,1.17,2.4529914529914532,0.6923076923076924]
[12,21.4,380,27,80,2.1800000000000002,0.88,200,1,1.26,1.7301587301587302,0.69841269841269837]
[13,16.600000000000001,100,23,70,0.42,0.27,100,1,0.3,1.4,0.90000000000000013]
[13,14,100,24,50,0.35,0.35,300,0,0.35,1,1]
[13,14.9,100,27,1,0.44,0.44,200,0,0.44,1,1]
[13,15.1,170,21,80,0.73,0.38,300,1,0.4,1.825,0.95]
[13,15.3,170,23,60,0.54,0.47,200,1,0.49,1.1020408163265307,0.95918367346938771]
[13,17.899999999999999,170,26,50,0.56999999999999995,0.56999999999999995,100,0,0.56999999999999995,1,1]
[13,21.2,170,27,99,1.9,0.52,200,1,0.68,2.7941176470588234,0.76470588235294112]
[13,19.399999999999999,240,22,90,0.74,0.31,100,1,0.48,1.5416666666666667,0.64583333333333337]
[13,16.8,240,22,90,1.31,0.5,300,1,0.59,2.2203389830508478,0.84745762711864414]
[13,16.5,240,26,1,0.82,0.82,200,0,0.82,1,1]
[13,19.600000000000001,240,27,90,2.3199999999999998,0.74,300,1,0.92,2.5217391304347823,0.80434782608695643]
[13,14.8,310,21,1,0.64,0.64,300,0,0.64,1,1]
[13,18.899999999999999,310,24,70,0.69,0.56000000000000005,100,1,0.67,1.0298507462686566,0.83582089552238814]
[13,17.3,310,25,70,1.52,0.83,300,1,0.94,1.6170212765957448,0.88297872340425532]
[13,17.399999999999999,310,27,50,1.03,1.03,200,0,1.03,1,1]
[13,17.8,380,21,99,1.66,0.53,300,1,0.72,2.3055555555555554,0.73611111111111116]
[13,20.399999999999999,380,24,90,1.71,0.62,200,1,0.92,1.8586956521739129,0.67391304347826086]
[13,20.399999999999999,380,26,50,0.86,0.86,100,0,0.86,1,1]
[13,16.600000000000001,380,27,1,1.26,1.26,300,0,1.26,1,1]
[14,19.7,100,23,99,0.67,0.2,100,1,0.27,2.4814814814814814,0.7407407407407407]
[14,16,100,24,80,0.69,0.3,300,1,0.31,2.225806451612903,0.96774193548387089]
[14,17.399999999999999,100,27,70,0.79,0.38,200,1,0.41,1.9268292682926831,0.92682926829268297]
[14,17.8,100,27,99,1.33,0.38,300,1,0.41,3.2439024390243905,0.92682926829268297]
[14,18.2,170,23,90,0.98,0.37,200,1,0.44,2.2272727272727271,0.84090909090909094]
[14,16.100000000000001,170,24,1,0.49,0.49,200,0,0.49,1,1]
[14,16.8,170,27,60,0.98,0.61,300,1,0.65,1.5076923076923077,0.93846153846153846]
[14,16.8,240,21,80,0.65,0.39,200,1,0.44,1.4772727272727273,0.88636363636363635]
[14,15.9,240,24,1,0.66,0.66,300,0,0.66,1,1]
[14,19,240,26,70,1.1599999999999999,0.64,200,1,0.75,1.5466666666666666,0.85333333333333339]
[14,24.1,240,27,90,1.18,0.39,100,1,0.7,1.6857142857142857,0.55714285714285716]
[14,15.7,310,21,70,0.6,0.53,300,1,0.55000000000000004,1.0909090909090908,0.96363636363636362]
[14,16.899999999999999,310,23,50,0.67,0.67,200,{"$f":"IF(F8598<>G8598,1,0)","v":0},0.67,{"$f":"F8598/J8598","v":1},1]
[14,21.9,310,26,90,1.83,0.61,200,1,{"$f":"IF(F8665/G8665=1,F8665,J8664)","v":0.89},2.0561797752808988,0.6853932584269663]
[14,21.5,310,27,80,1.74,0.72,200,1,0.96,1.8125,0.75]
[14,19.100000000000001,380,23,70,0.6,0.6,100,0,0.6,1,1]
[14,16.600000000000001,380,24,50,0.9,0.9,300,0,0.9,1,1]
[14,24.9,380,26,99,1.27,0.33,100,1,0.8,1.5874999999999999,0.41249999999999998]
[15,15.8,100,21,70,0.19,0.19,200,0,0.19,1,1]
[15,16.100000000000001,100,23,60,0.25,0.25,200,0,0.25,1,1]
[15,17.600000000000001,100,25,1,0.3,0.3,100,0,0.3,1,1]
[15,20.100000000000001,100,27,99,1.19,0.33,200,1,0.37,3.2162162162162162,0.891891891891892]
[15,17.7,170,22,70,0.31,0.31,100,0,0.31,1,1]
[15,17.3,170,22,90,0.81,0.32,300,1,0.35,2.3142857142857145,0.91428571428571437]
[15,17.7,170,24,70,0.62,0.4,200,1,0.44,1.4090909090909092,0.90909090909090917]
[15,19.7,170,27,90,1.62,0.52,300,1,0.59,2.745762711864407,0.88135593220338992]
[15,16.100000000000001,240,21,1,0.4,0.4,300,0,0.4,1,1]
[15,19.2,240,24,50,0.49,0.49,100,0,0.49,1,1]
[15,17.899999999999999,240,25,70,1.02,0.6,300,1,0.65,1.5692307692307692,0.92307692307692302]
[15,18.2,240,27,50,0.75,0.75,200,0,0.75,1,1]
[15,18.3,310,21,99,1.1499999999999999,0.37,300,1,0.47,2.4468085106382977,{"$f":"G9303/J9303","v":0.78723404255319152}]
[15,20.6,310,24,90,1.3,0.48,200,1,0.67,1.9402985074626866,0.71641791044776115]
[15,20.9,310,25,99,2.0699999999999998,0.57999999999999996,300,1,0.79,2.6202531645569618,0.73417721518987333]
[15,17.7,310,27,1,0.95,0.95,300,0,0.95,1,1]
[15,22.1,380,23,99,0.82,0.24,100,1,0.53,1.5471698113207546,0.45283018867924524]
[15,19,380,24,80,1.38,0.68,300,1,0.81,1.7037037037037035,0.83950617283950613]
[15,22.8,380,25,99,1.8,0.49,200,1,0.84,2.1428571428571428,0.58333333333333337]
[15,21,380,27,80,2.08,0.85,300,1,1.08,1.9259259259259258,0.78703703703703698]
[16,18.3,100,23,90,0.53,0.2,200,1,0.22,2.4090909090909092,0.90909090909090917]
[16,17.100000000000001,100,24,1,0.25,0.25,200,0,0.25,1,1]
[16,17.399999999999999,100,27,60,0.49,0.34,300,1,0.34,1.4411764705882351,1]
[16,17.399999999999999,170,21,80,0.32,0.23,200,1,0.24,1.3333333333333335,0.95833333333333337]
[16,16.899999999999999,170,22,60,0.3,0.3,300,0,0.3,1,1]
[16,20.6,170,24,99,1.06,0.31,200,1,0.39,2.7179487179487181,0.79487179487179482]
[16,23.9,170,27,90,0.92,0.31,100,1,0.48,1.9166666666666667,0.64583333333333337]
[16,16.899999999999999,240,21,70,0.33,0.33,300,0,0.33,1,1]
[16,17.899999999999999,240,23,50,0.44,0.44,200,0,0.44,1,1]
[16,19.8,240,26,70,0.88,0.55000000000000004,200,1,0.63,1.3968253968253967,0.87301587301587313]
[16,21.6,240,27,80,1.3,0.55000000000000004,200,1,0.69,1.8840579710144929,0.79710144927536242]
[16,19.7,310,23,70,0.43,0.43,100,0,0.43,1,1]
[16,17.8,310,24,50,0.63,0.63,300,0,0.63,1,1]
[16,24.9,310,26,99,1.04,0.27,100,1,0.61,1.7049180327868854,0.44262295081967218]
[16,17.8,380,21,50,0.42,0.42,200,0,0.42,1,1]
[16,18.5,380,23,60,0.59,0.59,200,0,0.59,1,1]
[16,21.2,380,25,1,0.6,0.6,100,0,0.6,1,1]
[16,18.3,380,25,60,0.81,0.81,300,0,{"$f":"IF(F10265/G10265=1,F10265,J10264)","v":0.81},1,1]
[17,18.600000000000001,100,22,80,0.18,0.14000000000000001,100,1,0.15,1.2,0.93333333333333346]
[17,20.9,100,23,99,0.45,0.13,100,1,0.18,2.5,0.72222222222222232]
[17,18.2,100,24,70,0.27,0.21,200,1,0.22,1.2272727272727273,0.95454545454545447]
[17,19.600000000000001,100,27,90,0.91,0.28999999999999998,300,1,{"$f":"IF(F10457/G10457=1,F10457,J10456)","v":0.31},2.935483870967742,0.93548387096774188]
[17,17.600000000000001,170,21,1,0.2,0.2,300,0,0.2,1,1]
[17,20.7,170,23,90,0.43,0.19,100,1,0.26,1.6538461538461537,0.73076923076923073]
[17,21.2,170,25,80,0.49,0.28000000000000003,100,1,0.35,1.4000000000000001,0.80000000000000016]
[17,19.100000000000001,170,27,50,0.48,0.48,200,0,0.48,1,1]
[17,19,240,21,99,0.69,0.22,300,1,0.26,2.6538461538461537,0.84615384615384615]
[17,20.8,240,24,90,0.89,0.34,200,1,0.44,2.0227272727272729,0.77272727272727282]
[17,19.8,240,25,80,0.96,0.47,300,1,0.52,1.846153846153846,0.90384615384615374]
[17,18.899999999999999,240,27,1,0.66,0.66,300,0,0.66,1,1]
[17,22.2,310,23,99,0.6,0.18,100,1,0.37,1.6216216216216215,0.48648648648648646]
[17,19.5,310,24,80,0.89,0.49,300,1,0.55000000000000004,1.6181818181818182,0.89090909090909087]
[17,22.9,310,25,99,1.38,0.37,200,1,0.59,2.3389830508474576,0.6271186440677966]
[17,19.399999999999999,310,27,60,0.82,0.75,300,1,0.78,1.0512820512820511,0.96153846153846145]
[17,20.6,380,23,90,0.84,0.37,200,1,0.5,1.68,0.74]
[17,19.600000000000001,380,24,1,0.59,0.59,200,0,0.59,1,1]
[17,21.4,380,25,90,1.52,0.55000000000000004,300,1,0.72,2.1111111111111112,0.76388888888888895]
[18,18.5,100,22,1,0.13,0.13,200,0,0.13,1,1]
[18,18.399999999999999,100,22,1,0.13,0.13,300,0,0.13,1,1]
[18,20.5,100,24,99,0.57999999999999996,0.17,200,1,0.19,3.0526315789473681,0.89473684210526316]
[18,23.4,100,27,90,0.62,0.2,100,1,0.27,2.2962962962962963,0.7407407407407407]
[18,18.399999999999999,170,21,70,0.15,0.15,300,0,0.15,1,1]
[18,19.100000000000001,170,23,50,0.24,0.24,200,0,0.24,1,1]
[18,19.7,170,26,50,0.39,0.39,200,0,0.39,1,1]
[18,21.7,170,27,80,0.86,0.38,200,1,0.43,2,0.88372093023255816]
[18,20.3,240,23,70,0.27,0.27,100,0,0.27,1,1]
[18,19.100000000000001,240,24,50,0.39,0.39,300,0,0.39,1,1]
[18,25,240,26,99,0.81,0.21,100,1,0.43,1.8837209302325584,0.48837209302325579]
[18,20.5,310,21,99,0.28999999999999998,0.1,100,1,0.18,1.6111111111111112,0.55555555555555558]
[18,19.600000000000001,310,23,60,0.37,0.37,200,0,0.37,1,1]
[18,21.7,310,25,1,0.43,0.43,100,0,0.43,1,1]
[18,19.600000000000001,310,25,60,0.55000000000000004,0.55000000000000004,300,0,0.55000000000000004,1,1]
[18,20.3,380,22,80,0.27,0.27,100,0,0.27,1,1]
[18,20.9,380,23,80,0.34,0.34,100,0,0.34,1,1]
[18,20.2,380,24,70,0.5,0.5,200,0,0.5,1,1]
[18,22.6,380,26,50,0.54,0.54,100,0,0.54,1,1]
[19,19.2,100,21,1,0.06,0.06,300,0,0.06,1,1]
[19,20.8,100,23,90,0.21,0.1,100,1,0.12,1.75,0.83333333333333337]
[19,20.5,100,25,60,0.18,0.18,100,0,0.18,1,1]
[19,20.100000000000001,100,27,50,0.25,0.25,200,0,0.25,1,1]
[19,19.8,170,21,99,0.28000000000000003,0.09,300,1,0.1,2.8000000000000003,0.89999999999999991]
[19,21.2,170,24,90,0.51,0.21,200,1,0.24,2.125,0.875]
[19,21.7,170,26,70,0.31,0.31,100,0,0.31,1,1]
[19,20,170,26,50,0.35,0.35,300,0,0.35,1,1]
[19,22.3,240,23,99,0.39,0.12,100,1,0.22,1.7727272727272727,0.54545454545454541]
[19,20.3,240,24,80,0.44,0.31,300,1,0.33,1.3333333333333333,0.93939393939393934]
[19,23.1,240,25,99,0.96,0.26,200,1,0.38,2.5263157894736841,0.68421052631578949]
[19,23.6,240,27,80,0.53,0.33,100,1,0.43,1.2325581395348839,0.76744186046511631]
[19,20.3,310,23,60,0.3,0.3,200,0,0.3,1,1]
[19,20.6,310,24,1,0.38,0.38,200,0,0.38,1,1]
[19,21.9,310,25,90,1,0.38,300,1,0.47,2.1276595744680851,0.8085106382978724]
[19,21.8,310,27,70,0.64,0.55000000000000004,200,1,0.59,1.0847457627118644,0.93220338983050854]
[19,20.399999999999999,380,22,90,0.32,0.22,200,1,0.25,1.28,0.88]
[19,22.9,380,24,99,0.9,0.25,200,1,0.42,2.1428571428571428,0.59523809523809523]
[19,25.2,380,27,90,0.71,0.31,100,1,0.54,1.3148148148148147,0.57407407407407407]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G12567/J12567","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F13529/G13529=1,F13529,J13528)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F13782<>G13782,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F13782/J13782","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G16087/J16087","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F16470<>G16470,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F16470/J16470","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F16985/G16985=1,F16985,J16984)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F17241/G17241=1,F17241,J17240)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F18646<>G18646,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F18646/J18646","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F18905/G18905=1,F18905,J18904)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G19351/J19351","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F20313/G20313=1,F20313,J20312)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F20505/G20505=1,F20505,J20504)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F22102<>G22102,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F22102/J22102","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G22615/J22615","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F23577/G23577=1,F23577,J23576)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F24022<>G24022,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F24022/J24022","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G25879/J25879","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G26135/J26135","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F26518<>G26518,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F26518/J26518","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F27225/G27225=1,F27225,J27224)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F27289/G27289=1,F27289,J27288)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F28694<>G28694,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F28694/J28694","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G29399/J29399","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F30361/G30361=1,F30361,J30360)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F30553/G30553=1,F30553,J30552)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F32342<>G32342,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F32342/J32342","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G32663/J32663","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F33625/G33625=1,F33625,J33624)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F34262<>G34262,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F34262/J34262","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G35927/J35927","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G36183/J36183","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F37337/G37337=1,F37337,J37336)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F37465/G37465=1,F37465,J37464)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F38742<>G38742,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F38742/J38742","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G39447/J39447","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F40409/G40409=1,F40409,J40408)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F40601/G40601=1,F40601,J40600)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F42582<>G42582,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F42582/J42582","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G42711/J42711","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F43673/G43673=1,F43673,J43672)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F44502<>G44502,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F44502/J44502","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G45975/J45975","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G46231/J46231","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F47385/G47385=1,F47385,J47384)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F48790<>G48790,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F48790/J48790","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G49495/J49495","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F50457/G50457=1,F50457,J50456)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F50649/G50649=1,F50649,J50648)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F52502<>G52502,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F52502/J52502","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G52759/J52759","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F53721/G53721=1,F53721,J53720)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F54742<>G54742,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F54742/J54742","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G56023/J56023","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G56279/J56279","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F56985/G56985=1,F56985,J56984)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F57433/G57433=1,F57433,J57432)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F58838<>G58838,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F58838/J58838","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G59543/J59543","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F60505/G60505=1,F60505,J60504)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F60697/G60697=1,F60697,J60696)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F62102<>G62102,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F62102/J62102","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F62550<>G62550,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F62550/J62550","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G62807/J62807","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F63769/G63769=1,F63769,J63768)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F65814<>G65814,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F65814/J65814","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G66071/J66071","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G66327/J66327","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F67033/G67033=1,F67033,J67032)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F68886<>G68886,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F68886/J68886","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G69591/J69591","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F70745/G70745=1,F70745,J70744)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F72150<>G72150,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F72150/J72150","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G72855/J72855","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F73817/G73817=1,F73817,J73816)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F75862<>G75862,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F75862/J75862","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G76119/J76119","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G76375/J76375","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F77081/G77081=1,F77081,J77080)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F78934<>G78934,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F78934/J78934","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G79383/J79383","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F79638<>G79638,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F79638/J79638","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G79639/J79639","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F79641/G79641=1,F79641,J79640)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F79702<>G79702,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F79702/J79702","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G79703/J79703","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F79705/G79705=1,F79705,J79704)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F79766<>G79766,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F79766/J79766","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G79767/J79767","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F79769/G79769=1,F79769,J79768)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F79830<>G79830,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F79830/J79830","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G79831/J79831","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F79833/G79833=1,F79833,J79832)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F79894<>G79894,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F79894/J79894","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G79895/J79895","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F79897/G79897=1,F79897,J79896)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F79958<>G79958,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F79958/J79958","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G79959/J79959","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F79961/G79961=1,F79961,J79960)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F80022<>G80022,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F80022/J80022","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G80023/J80023","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F80025/G80025=1,F80025,J80024)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(F80086<>G80086,1,0)","v":0},{"$error":"#DIV/0!"},{"$f":"F80086/J80086","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G80087/J80087","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"G80088/J80088","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F80089/G80089=1,F80089,J80088)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$f":"G80089/J80089","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F80090/G80090=1,F80090,J80089)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$f":"G80090/J80090","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,0,{"$f":"IF(F80091/G80091=1,F80091,J80090)","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$f":"G80091/J80091","v":{"$error":"#DIV/0!"}}]

{"sheet":"Eurocoil","index":9,"n_rows":12503,"n_cols":23,"rows_kept":4500,"cut":true,"hidden":true,"merged":[],"bounds":{"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0}}
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,2,3,5,null,null,4]
["TWI","TWO","QA","TAI","RH","QTOT","QSEN","QW","VA","DPA","RH","VW","GLI","DPW"]
["°C","°C","m3/h","°C","%","kW","kW","l/h","m/s","Pa","%","m/s","%","kPa",null,"TWI [°C]","TWO [°C]","QA [m³/h]","TAI [°C]","UR [%]","PT [kW]","PS [kW]","m [kg/h]"]
[1,null,2,3,5,null,null,4,null,null,null,null,null,null,null,3,7.4,100,21,1,0.51,0.51,100]
[3,7.6,100,21,1,0.54,0.54,100,0.19,0,3,0.4,0,7,null,3,8.3000000000000007,100,21,50,0.62,0.47,100]
[3,8.6999999999999993,100,21,50,0.67,0.49,100,0.19,1,98,0.4,0,7,null,3,9.1,100,21,60,0.72,0.45,100]
[3,9.6,100,21,60,0.77,0.48,100,0.19,1,98,0.4,0,7,null,3,10,100,21,70,0.81,0.44,100]
[3,10.4,100,21,70,0.87,0.47,100,0.19,1,99,0.4,0,7,null,3,10.8,100,21,80,0.91,0.42,100]
[3,11.3,100,21,80,0.97,0.45,100,0.19,1,99,0.4,0,7,null,3,11.6,100,21,90,1,0.41,100]
[3,12.2,100,21,90,1.07,0.44,100,0.19,1,100,0.4,0,7,null,3,12.3,100,21,99,1.0900000000000001,0.39,100]
[3,13,100,21,99,1.1599999999999999,0.43,100,0.19,1,100,0.4,0,7,null,3,5.3,100,21,1,0.55000000000000004,0.55000000000000004,200]
[3,5.4,100,21,1,0.56999999999999995,0.56999999999999995,200,0.19,0,3,0.8,0,24,null,3,6.2,100,21,50,0.74,0.52,200]
[3,6.3,100,21,50,0.77,0.55000000000000004,200,0.19,1,98,0.8,0,24,null,3,6.6,100,21,60,0.85,0.52,200]
[3,6.8,100,21,60,0.89,0.54,200,0.19,1,98,0.8,0,24,null,3,7.1,100,21,70,0.96,0.51,200]
[3,7.3,100,21,70,1.01,0.54,200,0.19,1,99,0.8,0,24,null,3,7.6,100,21,80,1.07,0.5,200]
[3,7.8,100,21,80,1.1299999999999999,0.53,200,0.19,1,99,0.8,0,24,null,3,8.1,100,21,90,1.19,0.49,200]
[3,8.3000000000000007,100,21,90,1.25,0.52,200,0.19,1,100,0.8,0,24,null,3,8.5,100,21,99,1.29,0.49,200]
[3,8.8000000000000007,100,21,99,1.35,0.52,200,0.19,1,100,0.8,0,24,null,3,4.5999999999999996,100,21,1,0.56000000000000005,0.56000000000000005,300]
[3,4.5999999999999996,100,21,1,0.57999999999999996,0.57999999999999996,300,0.19,0,3,1.2,0,49,null,3,5.2,100,21,50,0.77,0.54,300]
[3,5.3,100,21,50,0.8,0.56000000000000005,300,0.19,1,98,1.2,0,49,null,3,5.5,100,21,60,0.88,0.53,300]
[3,5.6,100,21,60,0.92,0.56000000000000005,300,0.19,1,98,1.2,0,49,null,3,5.9,100,21,70,1,0.53,300]
[3,6,100,21,70,1.04,0.55000000000000004,300,0.19,1,99,1.2,0,49,null,3,6.2,100,21,80,1.1200000000000001,0.52,300]
[3,6.3,100,21,80,1.1599999999999999,0.55000000000000004,300,0.19,1,99,1.2,0,48,null,3,6.5,100,21,90,1.23,0.52,300]
[3,6.7,100,21,90,1.29,0.54,300,0.19,1,100,1.2,0,48,null,3,6.8,100,21,99,1.34,0.51,300]
[3,7,100,21,99,1.4,0.54,300,0.19,1,100,1.2,0,48,null,3,7.6,100,22,1,0.54,0.54,100]
[3,7.9,100,22,1,0.56999999999999995,0.56999999999999995,100,0.19,0,3,0.4,0,7,null,3,8.8000000000000007,100,22,50,0.67,0.49,100]
[3,9.1999999999999993,100,22,50,0.72,0.52,100,0.19,1,98,0.4,0,7,null,3,9.6,100,22,60,0.78,0.47,100]
[3,10.1,100,22,60,0.83,0.5,100,0.19,1,98,0.4,0,7,null,3,10.5,100,22,70,0.88,0.46,100]
[3,11,100,22,70,0.94,0.49,100,0.19,1,99,0.4,0,7]
[3,12,100,22,80,1.05,0.47,100,0.19,1,99,0.4,0,7]
[3,12.9,100,22,90,1.1499999999999999,0.46,100,0.19,1,100,0.4,0,7]
[3,13.7,100,22,99,1.25,0.45,100,0.19,1,100,0.4,0,7]
[3,5.6,100,22,1,0.6,0.6,200,0.19,0,3,0.8,0,24]
[3,6.6,100,22,50,0.84,0.57999999999999996,200,0.19,1,98,0.8,0,24]
[3,7.1,100,22,60,0.96,0.56999999999999995,200,0.19,1,98,0.8,0,24]
[3,7.7,100,22,70,1.0900000000000001,0.56000000000000005,200,0.19,1,99,0.8,0,24]
[3,8.1999999999999993,100,22,80,1.21,0.56000000000000005,200,0.19,1,99,0.8,0,24]
[3,8.6999999999999993,100,22,90,1.34,0.55000000000000004,200,0.19,1,100,0.8,0,24]
[3,9.1999999999999993,100,22,99,1.45,0.54,200,0.19,1,100,0.8,0,24]
[3,4.7,100,22,1,0.61,0.61,300,0.19,0,3,1.2,0,49]
[3,5.5,100,22,50,0.87,0.59,300,0.19,1,98,1.2,0,49]
[3,5.8,100,22,60,0.99,0.59,300,0.19,1,98,1.2,0,49]
[3,6.2,100,22,70,1.1200000000000001,0.57999999999999996,300,0.19,1,99,1.2,0,48]
[3,6.6,100,22,80,1.25,0.57999999999999996,300,0.19,1,99,1.2,0,48]
[3,6.9,100,22,90,1.38,0.56999999999999995,300,0.19,1,100,1.2,0,48]
[3,7.3,100,22,99,1.5,0.56999999999999995,300,0.19,1,100,1.2,0,48]
[3,8.1,100,23,1,0.6,0.6,100,0.19,0,3,0.4,0,7]
[3,9.6999999999999993,100,23,50,0.78,0.54,100,0.19,1,98,0.4,0,7]
[3,10.7,100,23,60,0.9,0.53,100,0.19,1,98,0.4,0,7]
[3,11.7,100,23,70,1.01,0.51,100,0.19,1,99,0.4,0,7]
[3,12.6,100,23,80,1.1200000000000001,0.49,100,0.19,1,99,0.4,0,7]
[3,13.6,100,23,90,1.24,0.48,100,0.19,1,100,0.4,0,7]
[3,14.5,100,23,99,1.34,0.47,100,0.19,1,100,0.4,0,7]
[3,5.7,100,23,1,0.63,0.63,200,0.19,0,3,0.8,0,24]
[3,6.9,100,23,50,0.91,0.6,200,0.19,1,98,0.8,0,24]
[3,7.4,100,23,60,1.04,0.6,200,0.19,1,98,0.8,0,24]
[3,8,100,23,70,1.17,0.59,200,0.19,1,99,0.8,0,24]
[3,8.6,100,23,80,1.3,0.57999999999999996,200,0.19,1,99,0.8,0,24]
[3,9.1999999999999993,100,23,90,1.44,0.57999999999999996,200,0.19,1,100,0.8,0,24]
[3,9.6999999999999993,100,23,99,1.56,0.56999999999999995,200,0.19,1,100,0.8,0,24]
[3,4.8,100,23,1,0.64,0.64,300,0.19,0,3,1.2,0,49]
[3,5.7,100,23,50,0.94,0.62,300,0.19,1,98,1.2,0,49]
[3,6.1,100,23,60,1.07,0.61,300,0.19,1,98,1.2,0,49]
[3,6.5,100,23,70,1.21,0.61,300,0.19,1,99,1.2,0,48]
[3,6.8,100,23,80,1.35,0.6,300,0.19,1,99,1.2,0,48]
[3,7.2,100,23,90,1.48,0.6,300,0.19,1,100,1.2,0,48]
[3,7.6,100,23,99,1.61,0.59,300,0.19,1,100,1.2,0,48]
[3,8.3000000000000007,100,24,1,0.62,0.62,100,0.19,0,3,0.4,0,7]
[3,10.199999999999999,100,24,50,0.84,0.56000000000000005,100,0.19,1,98,0.4,0,7]
[3,11.2,100,24,60,0.96,0.55000000000000004,100,0.19,1,98,0.4,0,7]
[3,12.3,100,24,70,1.08,0.53,100,0.19,1,99,0.4,0,7]
[3,13.3,100,24,80,1.21,0.51,100,0.19,1,99,0.4,0,7]
[3,14.4,100,24,90,1.33,0.5,100,0.19,1,100,0.4,0,7]
[3,15.3,100,24,99,1.43,0.48,100,0.19,1,100,0.4,0,7]
[3,5.8,100,24,1,0.66,0.66,200,0.19,0,3,0.8,0,24]
[3,7.2,100,24,50,0.98,0.63,200,0.19,1,98,0.8,0,24]
[3,7.8,100,24,60,1.1200000000000001,0.62,200,0.19,1,98,0.8,0,24]
[3,8.4,100,24,70,1.26,0.62,200,0.19,1,99,0.8,0,24]
[3,9,100,24,80,1.4,0.61,200,0.19,1,99,0.8,0,24]
[3,9.6,100,24,90,1.54,0.6,200,0.19,1,100,0.8,0,24]
[3,10.1,100,24,99,1.66,0.59,200,0.19,1,100,0.8,0,24]
[3,4.9000000000000004,100,24,1,0.67,0.67,300,0.19,0,3,1.2,0,49]
[3,5.9,100,24,50,1.01,0.65,300,0.19,1,98,1.2,0,49]
[3,6.3,100,24,60,1.1499999999999999,0.64,300,0.19,1,98,1.2,0,48]
[3,6.7,100,24,70,1.3,0.64,300,0.19,1,99,1.2,0,48]
[3,7.1,100,24,80,1.44,0.63,300,0.19,1,99,1.2,0,48]
[3,7.5,100,24,90,1.59,0.63,300,0.19,1,100,1.2,0,48]
[3,7.9,100,24,99,1.72,0.62,300,0.19,1,100,1.2,0,48]
[3,8.6,100,25,1,0.65,0.65,100,0.19,0,3,0.4,0,7]
[3,10.7,100,25,50,0.9,0.59,100,0.19,1,98,0.4,0,7]
[3,11.8,100,25,60,1.03,0.56999999999999995,100,0.19,1,98,0.4,0,7]
[3,12.9,100,25,70,1.1599999999999999,0.55000000000000004,100,0.19,1,99,0.4,0,7]
[3,14,100,25,80,1.29,0.53,100,0.19,1,99,0.4,0,7]
[3,15.1,100,25,90,1.42,0.52,100,0.19,1,100,0.4,0,7]
[3,16.100000000000001,100,25,99,1.53,0.5,100,0.19,1,100,0.4,0,7]
[3,6,100,25,1,0.69,0.69,200,0.19,0,4,0.8,0,24]
[3,7.5,100,25,50,1.05,0.66,200,0.19,1,98,0.8,0,24]
[3,8.1,100,25,60,1.2,0.65,200,0.19,1,98,0.8,0,24]
[3,8.8000000000000007,100,25,70,1.34,0.64,200,0.19,1,99,0.8,0,24]
[3,9.4,100,25,80,1.49,0.63,200,0.19,1,99,0.8,0,24]
[3,10,100,25,90,1.64,0.63,200,0.19,1,100,0.8,0,24]
[3,10.6,100,25,99,1.78,0.62,200,0.19,1,100,0.8,0,24]
[3,5,100,25,1,0.7,0.7,300,0.19,0,4,1.2,0,49]
[3,6.1,100,25,50,1.08,0.67,300,0.19,1,98,1.2,0,49]
[3,6.5,100,25,60,1.23,0.67,300,0.19,1,98,1.2,0,48]
[3,7,100,25,70,1.39,0.66,300,0.19,1,99,1.2,0,48]
[3,7.4,100,25,80,1.54,0.66,300,0.19,1,99,1.2,0,48]
[3,7.8,100,25,90,1.7,0.65,300,0.19,1,100,1.2,0,48]
[3,8.1999999999999993,100,25,99,1.83,0.65,300,0.19,1,100,1.2,0,48]
[3,8.8000000000000007,100,26,1,0.68,0.68,100,0.19,0,3,0.4,0,7]
[3,11.3,100,26,50,0.97,0.61,100,0.19,1,98,0.4,0,7]
[3,12.5,100,26,60,1.1000000000000001,0.59,100,0.19,1,98,0.4,0,7]
[3,13.6,100,26,70,1.24,0.56999999999999995,100,0.19,1,99,0.4,0,7]
[3,14.8,100,26,80,1.37,0.55000000000000004,100,0.19,1,99,0.4,0,7]
[3,16,100,26,90,1.51,0.54,100,0.19,1,100,0.4,0,7]
[3,17,100,26,99,1.63,0.52,100,0.19,1,100,0.4,0,7]
[3,6.1,100,26,1,0.72,0.72,200,0.19,0,4,0.8,0,24]
[3,7.8,100,26,50,1.1200000000000001,0.68,200,0.19,1,98,0.8,0,24]
[3,8.5,100,26,60,1.28,0.68,200,0.19,1,98,0.8,0,24]
[3,9.1,100,26,70,1.43,0.67,200,0.19,1,99,0.8,0,24]
[3,9.8000000000000007,100,26,80,1.59,0.66,200,0.19,1,99,0.8,0,24]
[3,10.5,100,26,90,1.75,0.65,200,0.19,1,100,0.8,0,24]
[3,11.1,100,26,99,1.89,0.64,200,0.19,1,100,0.8,0,23]
[3,5.0999999999999996,100,26,1,0.73,0.73,300,0.19,0,4,1.2,0,49]
[3,6.3,100,26,50,1.1499999999999999,0.7,300,0.19,1,98,1.2,0,48]
[3,6.8,100,26,60,1.32,0.7,300,0.19,1,98,1.2,0,48]
[3,7.2,100,26,70,1.48,0.69,300,0.19,1,99,1.2,0,48]
[3,7.7,100,26,80,1.64,0.68,300,0.19,1,99,1.2,0,48]
[3,8.1999999999999993,100,26,90,1.81,0.68,300,0.19,1,100,1.2,0,48]
[3,8.6,100,26,99,1.95,0.67,300,0.19,1,100,1.2,0,48]
[3,9.1,100,27,1,0.71,0.71,100,0.19,0,4,0.4,0,7]
[3,11.8,100,27,50,1.03,0.63,100,0.19,1,98,0.4,0,7]
[3,13.1,100,27,60,1.18,0.61,100,0.19,1,98,0.4,0,7]
[3,14.3,100,27,70,1.32,0.59,100,0.19,1,99,0.4,0,7]
[3,15.6,100,27,80,1.46,0.56999999999999995,100,0.19,1,99,0.4,0,7]
[3,16.8,100,27,90,1.61,0.55000000000000004,100,0.19,1,100,0.4,0,7]
[3,17.899999999999999,100,27,99,1.73,0.54,100,0.19,1,100,0.4,0,7]
[3,6.2,100,27,1,0.75,0.75,200,0.19,0,4,0.8,0,24]
[3,8.1,100,27,50,1.19,0.71,200,0.19,1,98,0.8,0,24]
[3,8.8000000000000007,100,27,60,1.36,0.7,200,0.19,1,98,0.8,0,24]
[3,9.5,100,27,70,1.53,0.69,200,0.19,1,99,0.8,0,24]
[3,10.3,100,27,80,1.69,0.68,200,0.19,1,99,0.8,0,24]
[3,11,100,27,90,1.86,0.67,200,0.19,1,100,0.8,0,23]
[3,11.6,100,27,99,2.0099999999999998,0.67,200,0.19,1,100,0.8,0,23]
[3,5.2,100,27,1,0.76,0.76,300,0.19,0,4,1.2,0,49]
[3,6.5,100,27,50,1.23,0.73,300,0.19,1,98,1.2,0,48]
[3,7,100,27,60,1.4,0.72,300,0.19,1,98,1.2,0,48]
[3,7.5,100,27,70,1.58,0.72,300,0.19,1,99,1.2,0,48]
[3,8,100,27,80,1.75,0.71,300,0.19,1,99,1.2,0,48]
[3,8.5,100,27,90,1.92,0.7,300,0.19,1,100,1.2,0,48]
[3,8.9,100,27,99,2.08,0.7,300,0.19,1,100,1.2,0,48]
[3,9.6999999999999993,170,21,1,0.78,0.78,100,0.33,1,2,0.4,0,7]
[3,10.4,170,21,50,0.86,0.7,100,0.33,1,95,0.4,0,7]
[3,11.5,170,21,60,0.99,0.66,100,0.33,1,96,0.4,0,7]
[3,12.6,170,21,70,1.1200000000000001,0.62,100,0.33,1,97,0.4,0,7]
[3,13.7,170,21,80,1.25,0.57999999999999996,100,0.33,1,98,0.4,0,7]
[3,14.8,170,21,90,1.37,0.55000000000000004,100,0.33,1,99,0.4,0,7]
[3,15.8,170,21,99,1.49,0.51,100,0.33,1,100,0.4,0,7]
[3,6.8,170,21,1,0.88,0.88,200,0.33,1,3,0.8,0,24]
[3,7.8,170,21,50,1.1299999999999999,0.83,200,0.33,1,94,0.8,0,24]
[3,8.6,170,21,60,1.3,0.8,200,0.33,1,96,0.8,0,24]
[3,9.3000000000000007,170,21,70,1.48,0.78,200,0.33,1,97,0.8,0,24]
[3,10.1,170,21,80,1.65,0.76,200,0.33,1,98,0.8,0,24]
[3,10.8,170,21,90,1.82,0.74,200,0.33,1,99,0.8,0,23]
[3,11.5,170,21,99,1.98,0.72,200,0.33,1,100,0.8,0,23]
[3,5.6,170,21,1,0.91,0.91,300,0.33,1,3,1.2,0,49]
[3,6.5,170,21,50,1.22,0.87,300,0.33,1,94,1.2,0,48]
[3,7,170,21,60,1.4,0.85,300,0.33,1,95,1.2,0,48]
[3,7.5,170,21,70,1.59,0.84,300,0.33,1,97,1.2,0,48]
[3,8.1,170,21,80,1.78,0.83,300,0.33,1,98,1.2,0,48]
[3,8.6,170,21,90,1.96,0.81,300,0.33,1,99,1.2,0,48]
[3,9.1,170,21,99,2.13,0.8,300,0.33,1,100,1.2,0,48]
[3,10,170,22,1,0.82,0.82,100,0.33,1,2,0.4,0,7]
[3,11,170,22,50,0.93,0.72,100,0.33,1,95,0.4,0,7]
[3,12.2,170,22,60,1.07,0.69,100,0.33,1,96,0.4,0,7]
[3,13.3,170,22,70,1.21,0.65,100,0.33,1,97,0.4,0,7]
[3,14.5,170,22,80,1.34,0.61,100,0.33,1,98,0.4,0,7]
[3,15.7,170,22,90,1.48,0.56999999999999995,100,0.33,1,99,0.4,0,7]
[3,16.7,170,22,99,1.6,0.53,100,0.33,1,100,0.4,0,7]
[3,7,170,22,1,0.93,0.93,200,0.33,1,3,0.8,0,24]
[3,8.3000000000000007,170,22,50,1.23,0.87,200,0.33,1,94,0.8,0,24]
[3,9,170,22,60,1.41,0.84,200,0.33,1,96,0.8,0,24]
[3,9.8000000000000007,170,22,70,1.59,0.82,200,0.33,1,97,0.8,0,24]
[3,10.6,170,22,80,1.78,0.8,200,0.33,1,98,0.8,0,24]
[3,11.4,170,22,90,1.96,0.78,200,0.33,1,99,0.8,0,23]
[3,12.1,170,22,99,2.13,0.76,200,0.33,1,100,0.8,0,23]
[3,5.7,170,22,1,0.96,0.96,300,0.33,1,3,1.2,0,49]
[3,6.8,170,22,50,1.32,0.91,300,0.33,1,94,1.2,0,48]
[3,7.3,170,22,60,1.52,0.9,300,0.33,1,95,1.2,0,48]
[3,7.9,170,22,70,1.72,0.88,300,0.33,1,97,1.2,0,48]
[3,8.5,170,22,80,1.91,0.87,300,0.33,1,98,1.2,0,48]
[3,9,170,22,90,2.11,0.85,300,0.33,1,99,1.2,0,48]
[3,9.5,170,22,99,2.29,0.84,300,0.33,1,100,1.2,0,48]
[3,10.4,170,23,1,0.86,0.86,100,0.33,1,2,0.4,0,7]
[3,11.6,170,23,50,1.01,0.75,100,0.33,1,95,0.4,0,7]
[3,12.9,170,23,60,1.1499999999999999,0.71,100,0.33,1,96,0.4,0,7]
[3,14.1,170,23,70,1.3,0.67,100,0.33,1,97,0.4,0,7]
[3,15.3,170,23,80,1.44,0.63,100,0.33,1,98,0.4,0,7]
[3,16.600000000000001,170,23,90,1.58,0.59,100,0.33,1,99,0.4,0,7]
[3,17.7,170,23,99,1.71,0.55000000000000004,100,0.33,1,100,0.4,0,7]
[3,7.2,170,23,1,0.98,0.98,200,0.33,1,3,0.8,0,24]
[3,8.6999999999999993,170,23,50,1.33,0.9,200,0.33,1,94,0.8,0,24]
[3,9.5,170,23,60,1.52,0.88,200,0.33,1,96,0.8,0,24]
[3,10.4,170,23,70,1.71,0.86,200,0.33,1,97,0.8,0,24]
[3,11.2,170,23,80,1.91,0.83,200,0.33,1,98,0.8,0,23]
[3,12,170,23,90,2.1,0.81,200,0.33,1,99,0.8,0,23]
[3,12.8,170,23,99,2.2799999999999998,0.79,200,0.33,1,100,0.8,0,23]
[3,5.9,170,23,1,1.01,1.01,300,0.33,1,3,1.2,0,49]
[3,7.1,170,23,50,1.43,0.95,300,0.33,1,94,1.2,0,48]
[3,7.7,170,23,60,1.64,0.94,300,0.33,1,95,1.2,0,48]
[3,8.3000000000000007,170,23,70,1.85,0.92,300,0.33,1,97,1.2,0,48]
[3,8.9,170,23,80,2.06,0.91,300,0.33,1,98,1.2,0,48]
[3,9.5,170,23,90,2.27,0.89,300,0.33,1,99,1.2,0,48]
[3,10,170,23,99,2.46,0.87,300,0.33,1,100,1.2,0,48]
[3,10.8,170,24,1,0.91,0.91,100,0.33,1,2,0.4,0,7]
[3,12.3,170,24,50,1.08,0.78,100,0.33,1,95,0.4,0,7]
[3,13.6,170,24,60,1.24,0.74,100,0.33,1,96,0.4,0,7]
[3,14.9,170,24,70,1.39,0.69,100,0.33,1,97,0.4,0,7]
[3,16.2,170,24,80,1.54,0.65,100,0.33,1,98,0.4,0,7]
[3,17.5,170,24,90,1.69,0.61,100,0.33,1,99,0.4,0,7]
[3,18.600000000000001,170,24,99,1.82,0.56999999999999995,100,0.33,1,100,0.4,0,7]
[3,7.4,170,24,1,1.02,1.02,200,0.33,1,3,0.8,0,24]
[3,9.1,170,24,50,1.43,0.94,200,0.33,1,94,0.8,0,24]
[3,10,170,24,60,1.63,0.92,200,0.33,1,96,0.8,0,24]
[3,10.9,170,24,70,1.84,0.89,200,0.33,1,97,0.8,0,23]
[3,11.8,170,24,80,2.0499999999999998,0.87,200,0.33,1,98,0.8,0,23]
[3,12.7,170,24,90,2.25,0.84,200,0.33,1,99,0.8,0,23]
[3,13.4,170,24,99,2.44,0.82,200,0.33,1,100,0.8,0,23]
[3,6,170,24,1,1.06,1.06,300,0.33,1,3,1.2,0,49]
[3,7.4,170,24,50,1.54,1,300,0.33,1,94,1.2,0,48]
[3,8,170,24,60,1.76,0.98,300,0.33,1,95,1.2,0,48]
[3,8.6999999999999993,170,24,70,1.98,0.96,300,0.33,1,97,1.2,0,48]
[3,9.3000000000000007,170,24,80,2.2000000000000002,0.94,300,0.33,1,98,1.2,0,48]
[3,9.9,170,24,90,2.4300000000000002,0.93,300,0.33,1,99,1.2,0,48]
[3,10.5,170,24,99,2.63,0.91,300,0.33,1,100,1.2,0,48]
[3,11.1,170,25,1,0.95,0.95,100,0.33,1,2,0.4,0,7]
[3,13,170,25,50,1.1599999999999999,0.81,100,0.33,1,95,0.4,0,7]
[3,14.4,170,25,60,1.33,0.76,100,0.33,1,96,0.4,0,7]
[3,15.7,170,25,70,1.48,0.72,100,0.33,1,97,0.4,0,7]
[3,17.100000000000001,170,25,80,1.64,0.67,100,0.33,1,98,0.4,0,7]
[3,18.399999999999999,170,25,90,1.8,0.63,100,0.33,1,99,0.4,0,7]
[3,19.600000000000001,170,25,99,1.94,0.59,100,0.33,1,100,0.4,0,7]
[3,7.6,170,25,1,1.07,1.07,200,0.33,1,3,0.8,0,24]
[3,9.6,170,25,50,1.53,0.98,200,0.33,1,94,0.8,0,24]
[3,10.5,170,25,60,1.75,0.95,200,0.33,1,96,0.8,0,24]
[3,11.4,170,25,70,1.97,0.93,200,0.33,1,97,0.8,0,23]
[3,12.4,170,25,80,2.19,0.9,200,0.33,1,98,0.8,0,23]
[3,13.3,170,25,90,2.4,0.88,200,0.33,1,99,0.8,0,23]
[3,14.2,170,25,99,2.6,0.85,200,0.33,1,100,0.8,0,23]
[3,6.1,170,25,1,1.1000000000000001,1.1000000000000001,300,0.33,1,3,1.2,0,48]
[3,7.7,170,25,50,1.65,1.04,300,0.33,1,94,1.2,0,48]
[3,8.4,170,25,60,1.89,1.02,300,0.33,1,95,1.2,0,48]
[3,9.1,170,25,70,2.12,1,300,0.33,1,97,1.2,0,48]
[3,9.6999999999999993,170,25,80,2.36,0.98,300,0.33,1,98,1.2,0,48]
[3,10.4,170,25,90,2.6,0.96,300,0.33,1,99,1.2,0,48]
[3,11,170,25,99,2.81,0.95,300,0.33,1,100,1.2,0,48]
[3,11.5,170,26,1,0.99,0.99,100,0.33,1,3,0.4,0,7]
[3,13.7,170,26,50,1.24,0.84,100,0.33,1,95,0.4,0,7]
[3,15.1,170,26,60,1.41,0.79,100,0.33,1,96,0.4,0,7]
[3,16.600000000000001,170,26,70,1.58,0.74,100,0.33,1,97,0.4,0,7]
[3,18,170,26,80,1.75,0.69,100,0.33,1,98,0.4,0,7]
[3,19.399999999999999,170,26,90,1.91,0.64,100,0.33,1,99,0.4,0,7]
[3,20.7,170,26,99,2.06,0.6,100,0.33,1,100,0.4,0,7]
[3,7.8,170,26,1,1.1200000000000001,1.1200000000000001,200,0.33,1,3,0.8,0,24]
[3,10,170,26,50,1.64,1.02,200,0.33,1,94,0.8,0,24]
[3,11,170,26,60,1.87,0.99,200,0.33,1,96,0.8,0,23]
[3,12,170,26,70,2.1,0.96,200,0.33,1,97,0.8,0,23]
[3,13,170,26,80,2.33,0.93,200,0.33,1,98,0.8,0,23]
[3,14,170,26,90,2.56,0.91,200,0.33,1,99,0.8,0,23]
[3,14.9,170,26,99,2.77,0.88,200,0.33,1,100,0.8,0,23]
[3,6.3,170,26,1,1.1499999999999999,1.1499999999999999,300,0.33,1,3,1.2,0,48]
[3,8,170,26,50,1.77,1.08,300,0.33,1,94,1.2,0,48]
[3,8.8000000000000007,170,26,60,2.02,1.06,300,0.33,1,95,1.2,0,48]
[3,9.5,170,26,70,2.27,1.04,300,0.33,1,97,1.2,0,48]
[3,10.199999999999999,170,26,80,2.5099999999999998,1.02,300,0.33,1,98,1.2,0,48]
[3,10.9,170,26,90,2.77,1,300,0.33,1,99,1.2,0,48]
[3,11.5,170,26,99,2.99,0.98,300,0.33,1,100,1.2,0,48]
[3,11.8,170,27,1,1.03,1.03,100,0.33,1,3,0.4,0,7]
[3,14.4,170,27,50,1.33,0.86,100,0.33,1,95,0.4,0,7]
[3,15.9,170,27,60,1.51,0.81,100,0.33,1,96,0.4,0,7]
[3,17.5,170,27,70,1.68,0.76,100,0.33,1,97,0.4,0,7]
[3,19,170,27,80,1.86,0.71,100,0.33,1,98,0.4,0,7]
[3,20.399999999999999,170,27,90,2.0299999999999998,0.66,100,0.33,1,99,0.4,0,7]
[3,21.7,170,27,99,2.1800000000000002,0.61,100,0.33,1,100,0.4,0,7]
[3,8,170,27,1,1.1599999999999999,1.1599999999999999,200,0.33,1,3,0.8,0,24]
[3,10.5,170,27,50,1.75,1.05,200,0.33,1,94,0.8,0,24]
[3,11.6,170,27,60,2,1.02,200,0.33,1,96,0.8,0,23]
[3,12.6,170,27,70,2.2400000000000002,1,200,0.33,1,97,0.8,0,23]
[3,13.7,170,27,80,2.4900000000000002,0.97,200,0.33,1,98,0.8,0,23]
[3,14.7,170,27,90,2.73,0.94,200,0.33,1,99,0.8,0,23]
[3,15.6,170,27,99,2.95,0.91,200,0.33,1,100,0.8,0,23]
[3,6.4,170,27,1,1.2,1.2,300,0.33,1,3,1.2,0,48]
[3,8.4,170,27,50,1.89,1.1200000000000001,300,0.33,1,94,1.2,0,48]
[3,9.1,170,27,60,2.15,1.1000000000000001,300,0.33,1,95,1.2,0,48]
[3,9.9,170,27,70,2.41,1.08,300,0.33,1,97,1.2,0,48]
[3,10.7,170,27,80,2.68,1.06,300,0.33,1,98,1.2,0,48]
[3,11.4,170,27,90,2.95,1.04,300,0.33,1,99,1.2,0,48]
[3,12.1,170,27,99,3.18,1.02,300,0.33,1,100,1.2,0,48]
[3,11.1,240,21,1,0.95,0.95,100,0.46,2,2,0.4,0,7]
[3,11.2,240,21,50,0.96,0.85,100,0.46,3,92,0.4,0,7]
[3,12.5,240,21,60,1.1000000000000001,0.78,100,0.46,3,94,0.4,0,7]
[3,13.7,240,21,70,1.25,0.72,100,0.46,3,96,0.4,0,7]
[3,14.9,240,21,80,1.38,0.66,100,0.46,3,97,0.4,0,7]
[3,16.100000000000001,240,21,90,1.52,0.6,100,0.46,3,99,0.4,0,7]
[3,17.100000000000001,240,21,99,1.65,0.55000000000000004,100,0.46,3,100,0.4,0,7]
[3,7.8,240,21,1,1.1299999999999999,1.1299999999999999,200,0.46,2,2,0.8,0,24]
[3,8.9,240,21,50,1.38,1.04,200,0.46,3,91,0.8,0,24]
[3,9.8000000000000007,240,21,60,1.59,1,200,0.46,3,93,0.8,0,24]
[3,10.7,240,21,70,1.79,0.96,200,0.46,3,95,0.8,0,24]
[3,11.6,240,21,80,2,0.92,200,0.46,3,97,0.8,0,23]
[3,12.5,240,21,90,2.21,0.88,200,0.46,3,99,0.8,0,23]
[3,13.3,240,21,99,2.4,0.85,200,0.46,3,100,0.8,0,23]
[3,6.4,240,21,1,1.19,1.19,300,0.46,2,2,1.2,0,48]
[3,7.4,240,21,50,1.54,1.1100000000000001,300,0.46,3,91,1.2,0,48]
[3,8.1,240,21,60,1.77,1.0900000000000001,300,0.46,3,93,1.2,0,48]
[3,8.6999999999999993,240,21,70,2.0099999999999998,1.06,300,0.46,3,95,1.2,0,48]
[3,9.4,240,21,80,2.2400000000000002,1.03,300,0.46,3,97,1.2,0,48]
[3,10.1,240,21,90,2.48,1,300,0.46,3,98,1.2,0,48]
[3,10.7,240,21,99,2.69,0.98,300,0.46,3,100,1.2,0,48]
[3,11.5,240,22,1,1,1,100,0.46,2,2,0.4,0,7]
[3,11.9,240,22,50,1.04,0.88,100,0.46,3,92,0.4,0,7]
[3,13.2,240,22,60,1.19,0.81,100,0.46,3,94,0.4,0,7]
[3,14.5,240,22,70,1.34,0.75,100,0.46,3,96,0.4,0,7]
[3,15.8,240,22,80,1.49,0.68,100,0.46,3,97,0.4,0,7]
[3,17,240,22,90,1.63,0.62,100,0.46,3,99,0.4,0,7]
[3,18.100000000000001,240,22,99,1.76,0.56000000000000005,100,0.46,3,100,0.4,0,7]
[3,8.1,240,22,1,1.19,1.19,200,0.46,2,2,0.8,0,24]
[3,9.4,240,22,50,1.49,1.08,200,0.46,3,91,0.8,0,24]
[3,10.4,240,22,60,1.72,1.04,200,0.46,3,93,0.8,0,24]
[3,11.3,240,22,70,1.94,1,200,0.46,3,95,0.8,0,23]
[3,12.2,240,22,80,2.16,0.96,200,0.46,3,97,0.8,0,23]
[3,13.2,240,22,90,2.38,0.92,200,0.46,3,99,0.8,0,23]
[3,14,240,22,99,2.58,0.88,200,0.46,3,100,0.8,0,23]
[3,6.6,240,22,1,1.25,1.25,300,0.46,2,2,1.2,0,48]
[3,7.8,240,22,50,1.67,1.17,300,0.46,3,91,1.2,0,48]
[3,8.5,240,22,60,1.92,1.1399999999999999,300,0.46,3,93,1.2,0,48]
[3,9.1999999999999993,240,22,70,2.17,1.1100000000000001,300,0.46,3,95,1.2,0,48]
[3,9.9,240,22,80,2.42,1.08,300,0.46,3,97,1.2,0,48]
[3,10.6,240,22,90,2.67,1.05,300,0.46,3,98,1.2,0,48]
[3,11.3,240,22,99,2.89,1.02,300,0.46,3,100,1.2,0,48]
[3,12,240,23,1,1.05,1.05,100,0.46,2,2,0.4,0,7]
[3,12.7,240,23,50,1.1299999999999999,0.91,100,0.46,3,92,0.4,0,7]
[3,14,240,23,60,1.28,0.84,100,0.46,3,94,0.4,0,7]
[3,15.4,240,23,70,1.44,0.78,100,0.46,3,96,0.4,0,7]
[3,16.7,240,23,80,1.6,0.71,100,0.46,3,97,0.4,0,7]
[3,18,240,23,90,1.75,0.64,100,0.46,3,99,0.4,0,7]
[3,19.100000000000001,240,23,99,1.88,0.57999999999999996,100,0.46,3,100,0.4,0,7]
[3,8.4,240,23,1,1.25,1.25,200,0.46,2,2,0.8,0,24]
[3,9.9,240,23,50,1.61,1.1299999999999999,200,0.46,3,91,0.8,0,24]
[3,10.9,240,23,60,1.85,1.0900000000000001,200,0.46,3,93,0.8,0,23]
[3,11.9,240,23,70,2.08,1.04,200,0.46,3,95,0.8,0,23]
[3,12.9,240,23,80,2.3199999999999998,1,200,0.46,3,97,0.8,0,23]
[3,13.9,240,23,90,2.5499999999999998,0.96,200,0.46,3,99,0.8,0,23]
[3,14.8,240,23,99,2.76,0.92,200,0.46,3,100,0.8,0,23]
[3,6.8,240,23,1,1.31,1.31,300,0.46,2,3,1.2,0,48]
[3,8.1999999999999993,240,23,50,1.8,1.22,300,0.46,3,91,1.2,0,48]
[3,8.9,240,23,60,2.0699999999999998,1.19,300,0.46,3,93,1.2,0,48]
[3,9.6999999999999993,240,23,70,2.33,1.1599999999999999,300,0.46,3,95,1.2,0,48]
[3,10.4,240,23,80,2.6,1.1200000000000001,300,0.46,3,97,1.2,0,48]
[3,11.2,240,23,90,2.86,1.0900000000000001,300,0.46,3,98,1.2,0,48]
[3,11.9,240,23,99,3.1,1.06,300,0.46,3,100,1.2,0,48]
[3,12.4,240,24,1,1.1000000000000001,1.1000000000000001,100,0.46,2,2,0.4,0,7]
[3,13.4,240,24,50,1.21,0.95,100,0.46,3,92,0.4,0,7]
[3,14.8,240,24,60,1.38,0.87,100,0.46,3,94,0.4,0,7]
[3,16.2,240,24,70,1.54,0.8,100,0.46,3,96,0.4,0,7]
[3,17.600000000000001,240,24,80,1.7,0.73,100,0.46,3,97,0.4,0,7]
[3,19,240,24,90,1.86,0.66,100,0.46,3,99,0.4,0,7]
[3,20.2,240,24,99,2,0.6,100,0.46,3,100,0.4,0,7]
[3,8.6,240,24,1,1.31,1.31,200,0.46,2,2,0.8,0,24]
[3,10.5,240,24,50,1.74,1.18,200,0.46,3,91,0.8,0,24]
[3,11.5,240,24,60,1.99,1.1299999999999999,200,0.46,3,93,0.8,0,23]
[3,12.6,240,24,70,2.23,1.08,200,0.46,3,95,0.8,0,23]
[3,13.6,240,24,80,2.48,1.04,200,0.46,3,97,0.8,0,23]
[3,14.7,240,24,90,2.73,0.99,200,0.46,3,99,0.8,0,23]
[3,15.6,240,24,99,2.95,0.95,200,0.46,3,100,0.8,0,23]
[3,6.9,240,24,1,1.38,1.38,300,0.46,2,3,1.2,0,48]
[3,8.5,240,24,50,1.94,1.27,300,0.46,3,91,1.2,0,48]
[3,9.3000000000000007,240,24,60,2.2200000000000002,1.24,300,0.46,3,93,1.2,0,48]
[3,10.1,240,24,70,2.5,1.2,300,0.46,3,95,1.2,0,48]
[3,11,240,24,80,2.78,1.17,300,0.46,3,97,1.2,0,48]
[3,11.8,240,24,90,3.06,1.1399999999999999,300,0.46,3,98,1.2,0,48]
[3,12.5,240,24,99,3.32,1.1000000000000001,300,0.46,3,100,1.2,0,48]
[3,12.9,240,25,1,1.1499999999999999,1.1499999999999999,100,0.46,2,2,0.4,0,7]
[3,14.1,240,25,50,1.3,0.98,100,0.46,3,92,0.4,0,7]
[3,15.6,240,25,60,1.47,0.9,100,0.46,3,94,0.4,0,7]
[3,17.100000000000001,240,25,70,1.64,0.82,100,0.46,3,96,0.4,0,7]
[3,18.600000000000001,240,25,80,1.81,0.75,100,0.46,3,97,0.4,0,7]
[3,20,240,25,90,1.98,0.68,100,0.46,3,99,0.4,0,7]
[3,21.2,240,25,99,2.12,0.61,100,0.46,3,100,0.4,0,7]
[3,8.9,240,25,1,1.37,1.37,200,0.46,2,3,0.8,0,24]
[3,11,240,25,50,1.86,1.22,200,0.46,3,91,0.8,0,23]
[3,12.1,240,25,60,2.13,1.17,200,0.46,3,93,0.8,0,23]
[3,13.2,240,25,70,2.39,1.1200000000000001,200,0.46,3,95,0.8,0,23]
[3,14.4,240,25,80,2.65,1.08,200,0.46,3,97,0.8,0,23]
[3,15.5,240,25,90,2.91,1.03,200,0.46,3,99,0.8,0,23]
[3,16.5,240,25,99,3.14,0.98,200,0.46,3,100,0.8,0,23]
[3,7.1,240,25,1,1.44,1.44,300,0.46,2,3,1.2,0,48]
[3,9,240,25,50,2.08,1.32,300,0.46,3,91,1.2,0,48]
[3,9.8000000000000007,240,25,60,2.38,1.29,300,0.46,3,93,1.2,0,48]
[3,10.7,240,25,70,2.68,1.25,300,0.46,3,95,1.2,0,48]
[3,11.5,240,25,80,2.97,1.21,300,0.46,3,97,1.2,0,48]
[3,12.4,240,25,90,3.27,1.18,300,0.46,3,98,1.2,0,48]
[3,13.1,240,25,99,3.54,1.1499999999999999,300,0.46,3,100,1.2,0,47]
[3,13.3,240,26,1,1.21,1.21,100,0.46,2,2,0.4,0,7]
[3,14.9,240,26,50,1.38,1.01,100,0.46,3,92,0.4,0,7]
[3,16.5,240,26,60,1.57,0.93,100,0.46,3,94,0.4,0,7]
[3,18,240,26,70,1.75,0.85,100,0.46,3,96,0.4,0,7]
[3,19.5,240,26,80,1.93,0.77,100,0.46,3,97,0.4,0,7]
[3,21,240,26,90,2.1,0.69,100,0.46,3,99,0.4,0,7]
[3,22.3,240,26,99,2.25,0.62,100,0.46,3,100,0.4,0,7]
[3,9.1,240,26,1,1.43,1.43,200,0.46,2,3,0.8,0,24]
[3,11.6,240,26,50,2,1.26,200,0.46,3,91,0.8,0,23]
[3,12.8,240,26,60,2.27,1.21,200,0.46,3,93,0.8,0,23]
[3,13.9,240,26,70,2.5499999999999998,1.1599999999999999,200,0.46,3,95,0.8,0,23]
[3,15.1,240,26,80,2.83,1.1100000000000001,200,0.46,3,97,0.8,0,23]
[3,16.3,240,26,90,3.1,1.06,200,0.46,3,99,0.8,0,23]
[3,17.399999999999999,240,26,99,3.35,1.01,200,0.46,3,100,0.8,0,23]
[3,7.3,240,26,1,1.5,1.5,300,0.46,2,3,1.2,0,48]
[3,9.4,240,26,50,2.23,1.37,300,0.46,3,91,1.2,0,48]
[3,10.3,240,26,60,2.54,1.34,300,0.46,3,93,1.2,0,48]
[3,11.2,240,26,70,2.86,1.3,300,0.46,3,95,1.2,0,48]
[3,12.1,240,26,80,3.18,1.26,300,0.46,3,97,1.2,0,48]
[3,13,240,26,90,3.49,1.22,300,0.46,3,98,1.2,0,47]
[3,13.8,240,26,99,3.77,1.19,300,0.46,3,100,1.2,0,47]
[3,13.8,240,27,1,1.26,1.26,100,0.46,2,2,0.4,0,7]
[3,15.7,240,27,50,1.48,1.04,100,0.46,3,92,0.4,0,7]
[3,17.3,240,27,60,1.67,0.95,100,0.46,3,94,0.4,0,7]
[3,19,240,27,70,1.86,0.87,100,0.46,3,96,0.4,0,7]
[3,20.5,240,27,80,2.04,0.79,100,0.46,3,97,0.4,0,7]
[3,22.1,240,27,90,2.2200000000000002,0.71,100,0.46,3,99,0.4,0,7]
[3,23.4,240,27,99,2.38,0.63,100,0.46,3,100,0.4,0,7]
[3,9.4,240,27,1,1.49,1.49,200,0.46,2,3,0.8,0,24]
[3,12.1,240,27,50,2.13,1.31,200,0.46,3,91,0.8,0,23]
[3,13.4,240,27,60,2.42,1.25,200,0.46,3,93,0.8,0,23]
[3,14.7,240,27,70,2.72,1.2,200,0.46,3,95,0.8,0,23]
[3,15.9,240,27,80,3.01,1.1399999999999999,200,0.46,3,97,0.8,0,23]
[3,17.100000000000001,240,27,90,3.3,1.0900000000000001,200,0.46,3,99,0.8,0,23]
[3,18.3,240,27,99,3.56,1.04,200,0.46,3,100,0.8,0,23]
[3,7.5,240,27,1,1.57,1.57,300,0.46,2,3,1.2,0,48]
[3,9.8000000000000007,240,27,50,2.38,1.42,300,0.46,3,91,1.2,0,48]
[3,10.8,240,27,60,2.71,1.38,300,0.46,3,93,1.2,0,48]
[3,11.7,240,27,70,3.05,1.34,300,0.46,3,95,1.2,0,48]
[3,12.7,240,27,80,3.38,1.3,300,0.46,3,97,1.2,0,47]
[3,13.6,240,27,90,3.72,1.26,300,0.46,3,98,1.2,0,47]
[3,14.5,240,27,99,4.0199999999999996,1.22,300,0.46,3,100,1.2,0,47]
[3,12.1,310,21,1,1.07,1.07,100,0.6,3,2,0.4,0,7]
[3,12.1,310,21,50,1.06,1.06,100,0.6,3,97,0.4,0,7]
[3,13.1,310,21,60,1.17,0.89,100,0.6,4,92,0.4,0,7]
[3,14.3,310,21,70,1.32,0.8,100,0.6,4,94,0.4,0,7]
[3,15.6,310,21,80,1.47,0.72,100,0.6,4,96,0.4,0,7]
[3,16.8,310,21,90,1.61,0.64,100,0.6,4,98,0.4,0,7]
[3,17.899999999999999,310,21,99,1.73,0.56000000000000005,100,0.6,4,100,0.4,0,7]
[3,8.6999999999999993,310,21,1,1.33,1.33,200,0.6,3,2,0.8,0,24]
[3,9.6999999999999993,310,21,50,1.55,1.21,200,0.6,4,89,0.8,0,24]
[3,10.7,310,21,60,1.79,1.1499999999999999,200,0.6,4,91,0.8,0,24]
[3,11.7,310,21,70,2.02,1.0900000000000001,200,0.6,4,94,0.8,0,23]
[3,12.6,310,21,80,2.25,1.03,200,0.6,4,96,0.8,0,23]
[3,13.6,310,21,90,2.48,0.97,200,0.6,4,98,0.8,0,23]
[3,14.5,310,21,99,2.69,0.92,200,0.6,4,100,0.8,0,23]
[3,7.1,310,21,1,1.42,1.42,300,0.6,3,2,1.2,0,48]
[3,8.1,310,21,50,1.79,1.32,300,0.6,4,88,1.2,0,48]
[3,8.9,310,21,60,2.06,1.27,300,0.6,4,91,1.2,0,48]
[3,9.6999999999999993,310,21,70,2.33,1.23,300,0.6,4,93,1.2,0,48]
[3,10.4,310,21,80,2.6,1.19,300,0.6,4,96,1.2,0,48]
[3,11.2,310,21,90,2.87,1.1399999999999999,300,0.6,4,98,1.2,0,48]
[3,11.9,310,21,99,3.11,1.1000000000000001,300,0.6,4,100,1.2,0,48]
[3,12.6,310,22,1,1.1299999999999999,1.1299999999999999,100,0.6,3,2,0.4,0,7]
[3,12.5,310,22,50,1.1100000000000001,1.01,100,0.6,4,89,0.4,0,7]
[3,13.9,310,22,60,1.27,0.92,100,0.6,4,92,0.4,0,7]
[3,15.2,310,22,70,1.42,0.83,100,0.6,4,94,0.4,0,7]
[3,16.5,310,22,80,1.57,0.74,100,0.6,4,96,0.4,0,7]
[3,17.8,310,22,90,1.72,0.66,100,0.6,4,98,0.4,0,7]
[3,18.899999999999999,310,22,99,1.85,0.57999999999999996,100,0.6,4,100,0.4,0,7]
[3,9,310,22,1,1.4,1.4,200,0.6,3,2,0.8,0,24]
[3,10.199999999999999,310,22,50,1.68,1.26,200,0.6,4,89,0.8,0,24]
[3,11.3,310,22,60,1.93,1.2,200,0.6,4,91,0.8,0,23]
[3,12.3,310,22,70,2.1800000000000002,1.1399999999999999,200,0.6,4,94,0.8,0,23]
[3,13.4,310,22,80,2.42,1.08,200,0.6,4,96,0.8,0,23]
[3,14.4,310,22,90,2.66,1.02,200,0.6,4,98,0.8,0,23]
[3,15.4,310,22,99,2.88,0.96,200,0.6,4,100,0.8,0,23]
[3,7.3,310,22,1,1.5,1.5,300,0.6,3,2,1.2,0,48]
[3,8.5,310,22,50,1.94,1.38,300,0.6,4,88,1.2,0,48]
[3,9.4,310,22,60,2.23,1.33,300,0.6,4,91,1.2,0,48]
[3,10.199999999999999,310,22,70,2.5099999999999998,1.29,300,0.6,4,93,1.2,0,48]
[3,11,310,22,80,2.8,1.24,300,0.6,4,96,1.2,0,48]
[3,11.8,310,22,90,3.09,1.19,300,0.6,4,98,1.2,0,48]
[3,12.6,310,22,99,3.35,1.1499999999999999,300,0.6,4,100,1.2,0,48]
[3,13.2,310,23,1,1.19,1.19,100,0.6,3,2,0.4,0,7]
[3,13.3,310,23,50,1.2,1.05,100,0.6,4,89,0.4,0,7]
[3,14.7,310,23,60,1.36,0.95,100,0.6,4,92,0.4,0,7]
[3,16.100000000000001,310,23,70,1.52,0.86,100,0.6,4,94,0.4,0,7]
[3,17.399999999999999,310,23,80,1.68,0.77,100,0.6,4,96,0.4,0,7]
[3,18.8,310,23,90,1.84,0.68,100,0.6,4,98,0.4,0,7]
[3,20,310,23,99,1.97,0.6,100,0.6,4,100,0.4,0,7]
[3,9.3000000000000007,310,23,1,1.48,1.48,200,0.6,3,2,0.8,0,24]
[3,10.8,310,23,50,1.82,1.31,200,0.6,4,89,0.8,0,23]
[3,11.9,310,23,60,2.08,1.25,200,0.6,4,91,0.8,0,23]
[3,13,310,23,70,2.34,1.18,200,0.6,4,94,0.8,0,23]
[3,14.2,310,23,80,2.6,1.1200000000000001,200,0.6,4,96,0.8,0,23]
[3,15.3,310,23,90,2.86,1.05,200,0.6,4,98,0.8,0,23]
[3,16.2,310,23,99,3.08,1,200,0.6,4,100,0.8,0,23]
[3,7.5,310,23,1,1.57,1.57,300,0.6,3,2,1.2,0,48]
[3,9,310,23,50,2.1,1.44,300,0.6,4,88,1.2,0,48]
[3,9.9,310,23,60,2.4,1.39,300,0.6,4,91,1.2,0,48]
[3,10.7,310,23,70,2.71,1.34,300,0.6,4,93,1.2,0,48]
[3,11.6,310,23,80,3.01,1.29,300,0.6,4,96,1.2,0,48]
[3,12.5,310,23,90,3.31,1.24,300,0.6,4,98,1.2,0,48]
[3,13.3,310,23,99,3.59,1.2,300,0.6,4,100,1.2,0,47]
[3,13.7,310,24,1,1.24,1.24,100,0.6,3,2,0.4,0,7]
[3,14,310,24,50,1.28,1.08,100,0.6,4,89,0.4,0,7]
[3,15.5,310,24,60,1.46,0.98,100,0.6,4,92,0.4,0,7]
[3,17,310,24,70,1.63,0.88,100,0.6,4,94,0.4,0,7]
[3,18.399999999999999,310,24,80,1.8,0.79,100,0.6,4,96,0.4,0,7]
[3,19.8,310,24,90,1.96,0.69,100,0.6,4,98,0.4,0,7]
[3,21,310,24,99,2.1,0.61,100,0.6,4,100,0.4,0,7]
[3,9.6,310,24,1,1.55,1.55,200,0.6,3,2,0.8,0,24]
[3,11.4,310,24,50,1.96,1.36,200,0.6,4,89,0.8,0,23]
[3,12.6,310,24,60,2.23,1.29,200,0.6,4,91,0.8,0,23]
[3,13.8,310,24,70,2.5099999999999998,1.23,200,0.6,4,94,0.8,0,23]
[3,14.9,310,24,80,2.78,1.1599999999999999,200,0.6,4,96,0.8,0,23]
[3,16.100000000000001,310,24,90,3.06,1.0900000000000001,200,0.6,4,98,0.8,0,23]
[3,17.100000000000001,310,24,99,3.3,1.03,200,0.6,4,100,0.8,0,23]
[3,7.7,310,24,1,1.65,1.65,300,0.6,3,2,1.2,0,48]
[3,9.4,310,24,50,2.2599999999999998,1.5,300,0.6,4,88,1.2,0,48]
[3,10.4,310,24,60,2.58,1.45,300,0.6,4,91,1.2,0,48]
[3,11.3,310,24,70,2.9,1.39,300,0.6,4,93,1.2,0,48]
[3,12.2,310,24,80,3.23,1.34,300,0.6,4,96,1.2,0,48]
[3,13.1,310,24,90,3.55,1.29,300,0.6,4,98,1.2,0,47]
[3,14,310,24,99,3.84,1.24,300,0.6,4,100,1.2,0,47]
[3,14.2,310,25,1,1.3,1.3,100,0.6,3,2,0.4,0,7]
[3,14.8,310,25,50,1.37,1.1200000000000001,100,0.6,4,90,0.4,0,7]
[3,16.399999999999999,310,25,60,1.56,1.01,100,0.6,4,92,0.4,0,7]
[3,17.899999999999999,310,25,70,1.73,0.91,100,0.6,4,94,0.4,0,7]
[3,19.399999999999999,310,25,80,1.91,0.81,100,0.6,4,96,0.4,0,7]
[3,20.8,310,25,90,2.08,0.71,100,0.6,4,98,0.4,0,7]
[3,22.1,310,25,99,2.2200000000000002,0.62,100,0.6,4,100,0.4,0,7]
[3,9.9,310,25,1,1.62,1.62,200,0.6,3,2,0.8,0,24]
[3,12,310,25,50,2.1,1.41,200,0.6,4,89,0.8,0,23]
[3,13.3,310,25,60,2.39,1.34,200,0.6,4,91,0.8,0,23]
[3,14.5,310,25,70,2.68,1.27,200,0.6,4,94,0.8,0,23]
[3,15.7,310,25,80,2.97,1.19,200,0.6,4,96,0.8,0,23]
[3,17,310,25,90,3.26,1.1200000000000001,200,0.6,4,98,0.8,0,23]
[3,18.100000000000001,310,25,99,3.51,1.06,200,0.6,4,100,0.8,0,23]
[3,7.9,310,25,1,1.73,1.73,300,0.6,3,2,1.2,0,48]
[3,9.9,310,25,50,2.42,1.56,300,0.6,4,88,1.2,0,48]
[3,10.9,310,25,60,2.76,1.5,300,0.6,4,91,1.2,0,48]
[3,11.9,310,25,70,3.11,1.44,300,0.6,4,93,1.2,0,48]
[3,12.9,310,25,80,3.45,1.39,300,0.6,4,96,1.2,0,47]
[3,13.8,310,25,90,3.79,1.33,300,0.6,4,98,1.2,0,47]
[3,14.7,310,25,99,4.0999999999999996,1.28,300,0.6,4,100,1.2,0,47]
[3,14.7,310,26,1,1.36,1.36,100,0.6,3,2,0.4,0,7]
[3,15.6,310,26,50,1.47,1.1499999999999999,100,0.6,4,90,0.4,0,7]
[3,17.2,310,26,60,1.66,1.04,100,0.6,4,92,0.4,0,7]
[3,18.8,310,26,70,1.84,0.93,100,0.6,4,94,0.4,0,7]
[3,20.399999999999999,310,26,80,2.02,0.82,100,0.6,4,97,0.4,0,7]
[3,21.9,310,26,90,2.2000000000000002,0.72,100,0.6,4,98,0.4,0,7]
[3,23.2,310,26,99,2.35,0.63,100,0.6,4,100,0.4,0,7]
[3,10.199999999999999,310,26,1,1.69,1.69,200,0.6,3,2,0.8,0,24]
[3,12.6,310,26,50,2.25,1.46,200,0.6,4,88,0.8,0,23]
[3,14,310,26,60,2.56,1.38,200,0.6,4,91,0.8,0,23]
[3,15.3,310,26,70,2.86,1.31,200,0.6,4,94,0.8,0,23]
[3,16.600000000000001,310,26,80,3.16,1.23,200,0.6,4,96,0.8,0,23]
[3,17.899999999999999,310,26,90,3.47,1.1499999999999999,200,0.6,4,98,0.8,0,23]
[3,19,310,26,99,3.74,1.0900000000000001,200,0.6,4,100,0.8,0,23]
[3,8.1,310,26,1,1.8,1.8,300,0.6,3,3,1.2,0,48]
[3,10.4,310,26,50,2.59,1.61,300,0.6,4,88,1.2,0,48]
[3,11.4,310,26,60,2.95,1.55,300,0.6,4,91,1.2,0,48]
[3,12.5,310,26,70,3.32,1.5,300,0.6,4,93,1.2,0,48]
[3,13.5,310,26,80,3.68,1.44,300,0.6,4,96,1.2,0,47]
[3,14.6,310,26,90,4.04,1.38,300,0.6,4,98,1.2,0,47]
[3,15.5,310,26,99,4.37,1.32,300,0.6,4,100,1.2,0,47]
[3,15.2,310,27,1,1.42,1.42,100,0.6,3,2,0.4,0,7]
[3,16.399999999999999,310,27,50,1.56,1.18,100,0.6,4,90,0.4,0,7]
[3,18.100000000000001,310,27,60,1.76,1.06,100,0.6,4,92,0.4,0,7]
[3,19.8,310,27,70,1.95,0.95,100,0.6,4,94,0.4,0,7]
[3,21.4,310,27,80,2.14,0.84,100,0.6,4,97,0.4,0,7]
[3,22.9,310,27,90,2.3199999999999998,0.73,100,0.6,4,98,0.4,0,7]
[3,24.3,310,27,99,2.48,0.64,100,0.6,4,100,0.4,0,7]
[3,10.6,310,27,1,1.76,1.76,200,0.6,3,2,0.8,0,24]
[3,13.3,310,27,50,2.4,1.51,200,0.6,4,88,0.8,0,23]
[3,14.7,310,27,60,2.72,1.43,200,0.6,4,91,0.8,0,23]
[3,16.100000000000001,310,27,70,3.05,1.34,200,0.6,4,94,0.8,0,23]
[3,17.399999999999999,310,27,80,3.36,1.26,200,0.6,4,96,0.8,0,23]
[3,18.8,310,27,90,3.68,1.19,200,0.6,4,98,0.8,0,23]
[3,20,310,27,99,3.96,1.1100000000000001,200,0.6,4,100,0.8,0,23]
[3,8.4,310,27,1,1.88,1.88,300,0.6,3,3,1.2,0,48]
[3,10.9,310,27,50,2.77,1.67,300,0.6,4,88,1.2,0,48]
[3,12,310,27,60,3.15,1.61,300,0.6,4,91,1.2,0,48]
[3,13.1,310,27,70,3.53,1.54,300,0.6,4,93,1.2,0,47]
[3,14.2,310,27,80,3.92,1.48,300,0.6,4,96,1.2,0,47]
[3,15.3,310,27,90,4.3,1.42,300,0.6,4,98,1.2,0,47]
[3,16.3,310,27,99,4.6399999999999997,1.36,300,0.6,4,100,1.2,0,47]
[3,12.9,380,21,1,1.1599999999999999,1.1599999999999999,100,0.74,4,1,0.4,0,7]
[3,12.9,380,21,50,1.1499999999999999,1.1499999999999999,100,0.74,4,90,0.4,0,7]
[3,13.5,380,21,60,1.22,0.98,100,0.74,6,90,0.4,0,7]
[3,14.8,380,21,70,1.37,0.87,100,0.74,6,93,0.4,0,7]
[3,16,380,21,80,1.52,0.77,100,0.74,6,96,0.4,0,7]
[3,17.3,380,21,90,1.66,0.66,100,0.74,6,98,0.4,0,7]
[3,18.399999999999999,380,21,99,1.79,0.56999999999999995,100,0.74,6,100,0.4,0,7]
[3,9.4,380,21,1,1.5,1.5,200,0.74,4,2,0.8,0,24]
[3,10.199999999999999,380,21,50,1.68,1.35,200,0.74,6,86,0.8,0,24]
[3,11.3,380,21,60,1.93,1.27,200,0.74,6,90,0.8,0,23]
[3,12.4,380,21,70,2.1800000000000002,1.2,200,0.74,6,93,0.8,0,23]
[3,13.4,380,21,80,2.4300000000000002,1.1200000000000001,200,0.74,6,95,0.8,0,23]
[3,14.5,380,21,90,2.68,1.04,200,0.74,6,98,0.8,0,23]
[3,15.4,380,21,99,2.9,0.98,200,0.74,6,100,0.8,0,23]
[3,7.6,380,21,1,1.62,1.62,300,0.74,4,2,1.2,0,48]
[3,8.6999999999999993,380,21,50,1.98,1.49,300,0.74,6,86,1.2,0,48]
[3,9.5,380,21,60,2.2799999999999998,1.43,300,0.74,6,89,1.2,0,48]
[3,10.4,380,21,70,2.58,1.37,300,0.74,6,92,1.2,0,48]
[3,11.2,380,21,80,2.88,1.31,300,0.74,6,95,1.2,0,48]
[3,12.1,380,21,90,3.18,1.25,300,0.74,6,98,1.2,0,48]
[3,12.9,380,21,99,3.45,1.19,300,0.74,6,100,1.2,0,47]
[3,13.5,380,22,1,1.22,1.22,100,0.74,4,1,0.4,0,7]
[3,13.5,380,22,50,1.22,1.22,100,0.74,4,93,0.4,0,7]
[3,14.3,380,22,60,1.31,1.01,100,0.74,6,90,0.4,0,7]
[3,15.6,380,22,70,1.47,0.9,100,0.74,6,93,0.4,0,7]
[3,17,380,22,80,1.63,0.79,100,0.74,6,96,0.4,0,7]
[3,18.3,380,22,90,1.78,0.68,100,0.74,6,98,0.4,0,7]
[3,19.399999999999999,380,22,99,1.91,0.59,100,0.74,6,100,0.4,0,7]
[3,9.8000000000000007,380,22,1,1.58,1.58,200,0.74,4,2,0.8,0,24]
[3,10.8,380,22,50,1.83,1.41,200,0.74,6,86,0.8,0,23]
[3,12,380,22,60,2.09,1.33,200,0.74,6,90,0.8,0,23]
[3,13.1,380,22,70,2.35,1.25,200,0.74,6,93,0.8,0,23]
[3,14.2,380,22,80,2.62,1.1599999999999999,200,0.74,6,95,0.8,0,23]
[3,15.3,380,22,90,2.87,1.08,200,0.74,6,98,0.8,0,23]
[3,16.3,380,22,99,3.11,1.01,200,0.74,6,100,0.8,0,23]
[3,7.9,380,22,1,1.71,1.71,300,0.74,4,2,1.2,0,48]
[3,9.1,380,22,50,2.15,1.56,300,0.74,6,86,1.2,0,48]
[3,10.1,380,22,60,2.4700000000000002,1.49,300,0.74,6,89,1.2,0,48]
[3,11,380,22,70,2.79,1.43,300,0.74,6,92,1.2,0,48]
[3,11.9,380,22,80,3.11,1.37,300,0.74,6,95,1.2,0,48]
[3,12.8,380,22,90,3.42,1.3,300,0.74,6,98,1.2,0,47]
[3,13.6,380,22,99,3.71,1.25,300,0.74,6,100,1.2,0,47]
[3,14,380,23,1,1.29,1.29,100,0.74,4,1,0.4,0,7]
[3,13.7,380,23,50,1.24,1.17,100,0.74,6,87,0.4,0,7]
[3,15.1,380,23,60,1.41,1.05,100,0.74,6,90,0.4,0,7]
[3,16.5,380,23,70,1.58,0.93,100,0.74,6,93,0.4,0,7]
[3,17.899999999999999,380,23,80,1.74,0.81,100,0.74,6,96,0.4,0,7]
[3,19.3,380,23,90,1.9,0.7,100,0.74,6,98,0.4,0,7]
[3,20.5,380,23,99,2.0299999999999998,0.61,100,0.74,6,100,0.4,0,7]
[3,10.1,380,23,1,1.66,1.66,200,0.74,4,2,0.8,0,24]
[3,11.4,380,23,50,1.97,1.46,200,0.74,6,86,0.8,0,23]
[3,12.7,380,23,60,2.25,1.38,200,0.74,6,90,0.8,0,23]
[3,13.9,380,23,70,2.5299999999999998,1.29,200,0.74,6,93,0.8,0,23]
[3,15,380,23,80,2.81,1.2,200,0.74,6,95,0.8,0,23]
[3,16.2,380,23,90,3.08,1.1200000000000001,200,0.74,6,98,0.8,0,23]
[3,17.3,380,23,99,3.32,1.04,200,0.74,6,100,0.8,0,23]
[3,8.1,380,23,1,1.8,1.8,300,0.74,4,2,1.2,0,48]
[3,9.6,380,23,50,2.33,1.62,300,0.74,6,86,1.2,0,48]
[3,10.6,380,23,60,2.66,1.55,300,0.74,6,89,1.2,0,48]
[3,11.6,380,23,70,3,1.49,300,0.74,6,92,1.2,0,48]
[3,12.5,380,23,80,3.34,1.42,300,0.74,6,95,1.2,0,48]
[3,13.5,380,23,90,3.67,1.35,300,0.74,6,98,1.2,0,47]
[3,14.4,380,23,99,3.97,1.29,300,0.74,6,100,1.2,0,47]
[3,14.6,380,24,1,1.35,1.35,100,0.74,4,1,0.4,0,7]
[3,14.4,380,24,50,1.33,1.2,100,0.74,6,87,0.4,0,7]
[3,16,380,24,60,1.51,1.08,100,0.74,6,90,0.4,0,7]
[3,17.5,380,24,70,1.68,0.95,100,0.74,6,93,0.4,0,7]
[3,18.899999999999999,380,24,80,1.85,0.83,100,0.74,6,96,0.4,0,7]
[3,20.3,380,24,90,2.02,0.72,100,0.74,6,98,0.4,0,7]
[3,21.5,380,24,99,2.16,0.62,100,0.74,6,100,0.4,0,7]
[3,10.5,380,24,1,1.74,1.74,200,0.74,4,2,0.8,0,24]
[3,12.1,380,24,50,2.12,1.52,200,0.74,6,86,0.8,0,23]
[3,13.4,380,24,60,2.42,1.43,200,0.74,6,90,0.8,0,23]
[3,14.6,380,24,70,2.71,1.34,200,0.74,6,93,0.8,0,23]
[3,15.9,380,24,80,3,1.25,200,0.74,6,95,0.8,0,23]
[3,17.100000000000001,380,24,90,3.29,1.1599999999999999,200,0.74,6,98,0.8,0,23]
[3,18.2,380,24,99,3.54,1.08,200,0.74,6,100,0.8,0,23]
[3,8.4,380,24,1,1.88,1.88,300,0.74,4,2,1.2,0,48]
[3,10.199999999999999,380,24,50,2.5,1.69,300,0.74,6,86,1.2,0,48]
[3,11.2,380,24,60,2.86,1.62,300,0.74,6,89,1.2,0,48]
[3,12.2,380,24,70,3.22,1.54,300,0.74,6,92,1.2,0,48]
[3,13.2,380,24,80,3.58,1.47,300,0.74,6,95,1.2,0,47]
[3,14.2,380,24,90,3.93,1.4,300,0.74,6,98,1.2,0,47]
[3,15.1,380,24,99,4.25,1.34,300,0.74,6,100,1.2,0,47]
[3,15.2,380,25,1,1.42,1.42,100,0.74,4,1,0.4,0,7]
[3,15.2,380,25,50,1.42,1.24,100,0.74,6,87,0.4,0,7]
[3,16.8,380,25,60,1.61,1.1100000000000001,100,0.74,6,91,0.4,0,7]
[3,18.399999999999999,380,25,70,1.79,0.98,100,0.74,6,93,0.4,0,7]
[3,19.899999999999999,380,25,80,1.97,0.85,100,0.74,6,96,0.4,0,7]
[3,21.3,380,25,90,2.14,0.73,100,0.74,6,98,0.4,0,7]
[3,22.6,380,25,99,2.2799999999999998,0.63,100,0.74,6,100,0.4,0,7]
[3,10.8,380,25,1,1.82,1.82,200,0.74,4,2,0.8,0,23]
[3,12.7,380,25,50,2.27,1.57,200,0.74,6,86,0.8,0,23]
[3,14.1,380,25,60,2.59,1.47,200,0.74,6,90,0.8,0,23]
[3,15.4,380,25,70,2.9,1.38,200,0.74,6,93,0.8,0,23]
[3,16.7,380,25,80,3.2,1.29,200,0.74,6,95,0.8,0,23]
[3,18,380,25,90,3.5,1.19,200,0.74,6,98,0.8,0,23]
[3,19.2,380,25,99,3.77,1.1100000000000001,200,0.74,6,100,0.8,0,23]
[3,8.6,380,25,1,1.97,1.97,300,0.74,4,2,1.2,0,48]
[3,10.7,380,25,50,2.69,1.75,300,0.74,6,86,1.2,0,48]
[3,11.8,380,25,60,3.07,1.68,300,0.74,6,89,1.2,0,48]
[3,12.9,380,25,70,3.44,1.6,300,0.74,6,92,1.2,0,47]
[3,13.9,380,25,80,3.82,1.52,300,0.74,6,95,1.2,0,47]
[3,15,380,25,90,4.2,1.45,300,0.74,6,98,1.2,0,47]
[3,16,380,25,99,4.53,1.38,300,0.74,6,100,1.2,0,47]
[3,15.7,380,26,1,1.48,1.48,100,0.74,4,2,0.4,0,7]
[3,16,380,26,50,1.52,1.27,100,0.74,6,87,0.4,0,7]
[3,17.7,380,26,60,1.71,1.1399999999999999,100,0.74,6,91,0.4,0,7]
[3,19.3,380,26,70,1.9,1,100,0.74,6,93,0.4,0,7]
[3,20.9,380,26,80,2.08,0.87,100,0.74,6,96,0.4,0,7]
[3,22.4,380,26,90,2.2599999999999998,0.75,100,0.74,6,98,0.4,0,7]
[3,23.7,380,26,99,2.41,0.64,100,0.74,6,100,0.4,0,7]
[3,11.2,380,26,1,1.91,1.91,200,0.74,4,2,0.8,0,23]
[3,13.4,380,26,50,2.4300000000000002,1.62,200,0.74,6,86,0.8,0,23]
[3,14.8,380,26,60,2.76,1.52,200,0.74,6,90,0.8,0,23]
[3,16.2,380,26,70,3.08,1.42,200,0.74,6,93,0.8,0,23]
[3,17.600000000000001,380,26,80,3.41,1.32,200,0.74,6,95,0.8,0,23]
[3,19,380,26,90,3.72,1.22,200,0.74,6,98,0.8,0,23]
[3,20.2,380,26,99,4,1.1299999999999999,200,0.74,6,100,0.8,0,23]
[3,8.9,380,26,1,2.06,2.06,300,0.74,4,2,1.2,0,48]
[3,11.2,380,26,50,2.88,1.81,300,0.74,6,86,1.2,0,48]
[3,12.4,380,26,60,3.28,1.73,300,0.74,6,89,1.2,0,48]
[3,13.5,380,26,70,3.68,1.65,300,0.74,6,92,1.2,0,47]
[3,14.7,380,26,80,4.07,1.57,300,0.74,6,95,1.2,0,47]
[3,15.8,380,26,90,4.47,1.49,300,0.74,6,98,1.2,0,47]
[3,16.8,380,26,99,4.83,1.42,300,0.74,6,100,1.2,0,47]
[3,16.3,380,27,1,1.55,1.55,100,0.74,4,2,0.4,0,7]
[3,16.899999999999999,380,27,50,1.62,1.31,100,0.74,6,87,0.4,0,7]
[3,18.600000000000001,380,27,60,1.82,1.1599999999999999,100,0.74,6,91,0.4,0,7]
[3,20.3,380,27,70,2.0099999999999998,1.02,100,0.74,6,93,0.4,0,7]
[3,21.9,380,27,80,2.2000000000000002,0.89,100,0.74,6,96,0.4,0,7]
[3,23.5,380,27,90,2.38,0.76,100,0.74,6,98,0.4,0,7]
[3,24.8,380,27,99,2.54,0.64,100,0.74,6,100,0.4,0,7]
[3,11.5,380,27,1,1.99,1.99,200,0.74,4,2,0.8,0,23]
[3,14.1,380,27,50,2.59,1.67,200,0.74,6,86,0.8,0,23]
[3,15.6,380,27,60,2.94,1.57,200,0.74,6,90,0.8,0,23]
[3,17.100000000000001,380,27,70,3.28,1.46,200,0.74,6,93,0.8,0,23]
[3,18.5,380,27,80,3.62,1.35,200,0.74,6,95,0.8,0,23]
[3,20,380,27,90,3.95,1.25,200,0.74,6,98,0.8,0,23]
[3,21.2,380,27,99,4.24,1.1599999999999999,200,0.74,6,100,0.8,0,23]
[3,9.1,380,27,1,2.15,2.15,300,0.74,4,2,1.2,0,48]
[3,11.8,380,27,50,3.07,1.87,300,0.74,6,86,1.2,0,48]
[3,13,380,27,60,3.49,1.79,300,0.74,6,89,1.2,0,47]
[3,14.2,380,27,70,3.92,1.7,300,0.74,6,92,1.2,0,47]
[3,15.4,380,27,80,4.33,1.62,300,0.74,6,95,1.2,0,47]
[3,16.600000000000001,380,27,90,4.75,1.54,300,0.74,6,98,1.2,0,47]
[3,17.7,380,27,99,5.13,1.46,300,0.74,6,100,1.2,0,47]
[4,8.4,100,21,1,0.51,0.51,100,0.19,0,2,0.4,0,7]
[4,9.3000000000000007,100,21,50,0.61,0.47,100,0.19,1,98,0.4,0,7]
[4,10.1,100,21,60,0.72,0.45,100,0.19,1,98,0.4,0,7]
[4,11,100,21,70,0.82,0.44,100,0.19,1,99,0.4,0,7]
[4,11.9,100,21,80,0.92,0.43,100,0.19,1,99,0.4,0,7]
[4,12.7,100,21,90,1.02,0.41,100,0.19,1,100,0.4,0,7]
[4,13.5,100,21,99,1.1100000000000001,0.4,100,0.19,1,100,0.4,0,7]
[4,6.3,100,21,1,0.54,0.54,200,0.19,0,3,0.8,0,24]
[4,7.1,100,21,50,0.72,0.52,200,0.19,1,98,0.8,0,24]
[4,7.6,100,21,60,0.83,0.51,200,0.19,1,98,0.8,0,24]
[4,8.1,100,21,70,0.95,0.51,200,0.19,1,99,0.8,0,24]
[4,8.6,100,21,80,1.07,0.5,200,0.19,1,99,0.8,0,24]
[4,9.1,100,21,90,1.19,0.49,200,0.19,1,100,0.8,0,24]
[4,9.5,100,21,99,1.29,0.49,200,0.19,1,100,0.8,0,24]
[4,5.6,100,21,1,0.55000000000000004,0.55000000000000004,300,0.19,0,3,1.2,0,48]
[4,6.1,100,21,50,0.74,0.53,300,0.19,1,98,1.2,0,48]
[4,6.5,100,21,60,0.86,0.53,300,0.19,1,98,1.2,0,48]
[4,6.8,100,21,70,0.98,0.52,300,0.19,1,99,1.2,0,48]
[4,7.2,100,21,80,1.1000000000000001,0.52,300,0.19,1,99,1.2,0,48]
[4,7.5,100,21,90,1.23,0.51,300,0.19,1,100,1.2,0,48]
[4,7.8,100,21,99,1.34,0.51,300,0.19,1,100,1.2,0,48]
[4,8.6,100,22,1,0.54,0.54,100,0.19,0,3,0.4,0,7]
[4,9.6999999999999993,100,22,50,0.67,0.49,100,0.19,1,98,0.4,0,7]
[4,10.7,100,22,60,0.78,0.48,100,0.19,1,98,0.4,0,7]
[4,11.6,100,22,70,0.89,0.46,100,0.19,1,99,0.4,0,7]
[4,12.5,100,22,80,0.99,0.45,100,0.19,1,99,0.4,0,7]
[4,13.4,100,22,90,1.1000000000000001,0.43,100,0.19,1,100,0.4,0,7]
[4,14.3,100,22,99,1.2,0.42,100,0.19,1,100,0.4,0,7]
[4,6.4,100,22,1,0.56999999999999995,0.56999999999999995,200,0.19,0,3,0.8,0,24]
[4,7.3,100,22,50,0.78,0.55000000000000004,200,0.19,1,98,0.8,0,24]
[4,7.9,100,22,60,0.91,0.54,200,0.19,1,98,0.8,0,24]
[4,8.4,100,22,70,1.03,0.53,200,0.19,1,99,0.8,0,24]
[4,9,100,22,80,1.1599999999999999,0.53,200,0.19,1,99,0.8,0,24]
[4,9.5,100,22,90,1.28,0.52,200,0.19,1,100,0.8,0,24]
[4,10,100,22,99,1.39,0.51,200,0.19,1,100,0.8,0,23]
[4,5.6,100,22,1,0.57999999999999996,0.57999999999999996,300,0.19,0,3,1.2,0,48]
[4,6.3,100,22,50,0.81,0.56000000000000005,300,0.19,1,98,1.2,0,48]
[4,6.7,100,22,60,0.94,0.56000000000000005,300,0.19,1,98,1.2,0,48]
[4,7,100,22,70,1.07,0.55000000000000004,300,0.19,1,99,1.2,0,48]
[4,7.4,100,22,80,1.19,0.55000000000000004,300,0.19,1,99,1.2,0,48]
[4,7.8,100,22,90,1.32,0.54,300,0.19,1,100,1.2,0,48]
[4,8.1,100,22,99,1.44,0.54,300,0.19,1,100,1.2,0,48]
[4,8.9,100,23,1,0.56999999999999995,0.56999999999999995,100,0.19,0,3,0.4,0,7]
[4,10.3,100,23,50,0.73,0.52,100,0.19,1,98,0.4,0,7]
[4,11.2,100,23,60,0.84,0.5,100,0.19,1,98,0.4,0,7]
[4,12.2,100,23,70,0.96,0.49,100,0.19,1,99,0.4,0,7]
[4,13.2,100,23,80,1.07,0.47,100,0.19,1,99,0.4,0,7]
[4,14.2,100,23,90,1.18,0.46,100,0.19,1,100,0.4,0,7]
[4,15,100,23,99,1.29,0.44,100,0.19,1,100,0.4,0,7]
[4,6.6,100,23,1,0.6,0.6,200,0.19,0,3,0.8,0,24]
[4,7.6,100,23,50,0.85,0.56999999999999995,200,0.19,1,98,0.8,0,24]
[4,8.1999999999999993,100,23,60,0.98,0.56999999999999995,200,0.19,1,98,0.8,0,24]
[4,8.8000000000000007,100,23,70,1.1100000000000001,0.56000000000000005,200,0.19,1,99,0.8,0,24]
[4,9.3000000000000007,100,23,80,1.25,0.55000000000000004,200,0.19,1,99,0.8,0,24]
[4,9.9,100,23,90,1.38,0.55000000000000004,200,0.19,1,100,0.8,0,23]
[4,10.4,100,23,99,1.5,0.54,200,0.19,1,100,0.8,0,23]
[4,5.7,100,23,1,0.61,0.61,300,0.19,0,3,1.2,0,48]
[4,6.5,100,23,50,0.88,0.59,300,0.19,1,98,1.2,0,48]
[4,6.9,100,23,60,1.01,0.57999999999999996,300,0.19,1,98,1.2,0,48]
[4,7.3,100,23,70,1.1499999999999999,0.57999999999999996,300,0.19,1,99,1.2,0,48]
[4,7.7,100,23,80,1.29,0.56999999999999995,300,0.19,1,99,1.2,0,48]
[4,8.1,100,23,90,1.42,0.56999999999999995,300,0.19,1,100,1.2,0,48]
[4,8.4,100,23,99,1.55,0.56000000000000005,300,0.19,1,100,1.2,0,48]
[4,9.1,100,24,1,0.59,0.59,100,0.19,0,3,0.4,0,7]
[4,10.8,100,24,50,0.79,0.54,100,0.19,1,98,0.4,0,7]
[4,11.8,100,24,60,0.91,0.52,100,0.19,1,98,0.4,0,7]
[4,12.8,100,24,70,1.03,0.51,100,0.19,1,99,0.4,0,7]
[4,13.9,100,24,80,1.1499999999999999,0.49,100,0.19,1,99,0.4,0,7]
[4,14.9,100,24,90,1.27,0.47,100,0.19,1,100,0.4,0,7]
[4,15.8,100,24,99,1.38,0.46,100,0.19,1,100,0.4,0,7]
[4,6.7,100,24,1,0.63,0.63,200,0.19,0,3,0.8,0,24]
[4,7.9,100,24,50,0.92,0.6,200,0.19,1,98,0.8,0,24]
[4,8.5,100,24,60,1.06,0.59,200,0.19,1,98,0.8,0,24]
[4,9.1,100,24,70,1.2,0.59,200,0.19,1,99,0.8,0,24]
[4,9.6999999999999993,100,24,80,1.34,0.57999999999999996,200,0.19,1,99,0.8,0,24]
[4,10.3,100,24,90,1.48,0.56999999999999995,200,0.19,1,100,0.8,0,23]
[4,10.9,100,24,99,1.61,0.56999999999999995,200,0.19,1,100,0.8,0,23]
[4,5.8,100,24,1,0.64,0.64,300,0.19,0,3,1.2,0,48]
[4,6.7,100,24,50,0.95,0.62,300,0.19,1,98,1.2,0,48]
[4,7.1,100,24,60,1.0900000000000001,0.61,300,0.19,1,98,1.2,0,48]
[4,7.5,100,24,70,1.24,0.61,300,0.19,1,99,1.2,0,48]
[4,8,100,24,80,1.38,0.6,300,0.19,1,99,1.2,0,48]
[4,8.4,100,24,90,1.53,0.6,300,0.19,1,100,1.2,0,48]
[4,8.6999999999999993,100,24,99,1.66,0.59,300,0.19,1,100,1.2,0,48]
[4,9.3000000000000007,100,25,1,0.62,0.62,100,0.19,0,3,0.4,0,7]
[4,11.3,100,25,50,0.85,0.56000000000000005,100,0.19,1,98,0.4,0,7]
[4,12.4,100,25,60,0.98,0.54,100,0.19,1,98,0.4,0,7]
[4,13.5,100,25,70,1.1100000000000001,0.53,100,0.19,1,99,0.4,0,7]
[4,14.6,100,25,80,1.23,0.51,100,0.19,1,99,0.4,0,7]
[4,15.7,100,25,90,1.36,0.49,100,0.19,1,100,0.4,0,7]
[4,16.7,100,25,99,1.48,0.48,100,0.19,1,100,0.4,0,7]
[4,6.8,100,25,1,0.66,0.66,200,0.19,0,3,0.8,0,24]
[4,8.1999999999999993,100,25,50,0.99,0.63,200,0.19,1,98,0.8,0,24]
[4,8.9,100,25,60,1.1399999999999999,0.62,200,0.19,1,98,0.8,0,24]
[4,9.5,100,25,70,1.29,0.61,200,0.19,1,99,0.8,0,24]
[4,10.199999999999999,100,25,80,1.43,0.6,200,0.19,1,99,0.8,0,23]
[4,10.8,100,25,90,1.58,0.6,200,0.19,1,100,0.8,0,23]
[4,11.4,100,25,99,1.72,0.59,200,0.19,1,100,0.8,0,23]
[4,5.9,100,25,1,0.67,0.67,300,0.19,0,3,1.2,0,48]
[4,6.9,100,25,50,1.02,0.64,300,0.19,1,98,1.2,0,48]
[4,7.4,100,25,60,1.17,0.64,300,0.19,1,98,1.2,0,48]
[4,7.8,100,25,70,1.33,0.63,300,0.19,1,99,1.2,0,48]
[4,8.1999999999999993,100,25,80,1.48,0.63,300,0.19,1,99,1.2,0,48]
[4,8.6999999999999993,100,25,90,1.64,0.62,300,0.19,1,100,1.2,0,48]
[4,9.1,100,25,99,1.78,0.62,300,0.19,1,100,1.2,0,48]
[4,9.6,100,26,1,0.65,0.65,100,0.19,0,3,0.4,0,7]
[4,11.8,100,26,50,0.91,0.57999999999999996,100,0.19,1,98,0.4,0,7]
[4,13,100,26,60,1.05,0.56999999999999995,100,0.19,1,98,0.4,0,7]
[4,14.2,100,26,70,1.18,0.55000000000000004,100,0.19,1,99,0.4,0,7]
[4,15.3,100,26,80,1.32,0.53,100,0.19,1,99,0.4,0,7]
[4,16.5,100,26,90,1.45,0.51,100,0.19,1,100,0.4,0,7]
[4,17.5,100,26,99,1.57,0.5,100,0.19,1,100,0.4,0,7]
[4,6.9,100,26,1,0.69,0.69,200,0.19,0,3,0.8,0,24]
[4,8.5,100,26,50,1.06,0.65,200,0.19,1,98,0.8,0,24]
[4,9.1999999999999993,100,26,60,1.22,0.65,200,0.19,1,98,0.8,0,24]
[4,9.9,100,26,70,1.38,0.64,200,0.19,1,99,0.8,0,23]
[4,10.6,100,26,80,1.54,0.63,200,0.19,1,99,0.8,0,23]
[4,11.3,100,26,90,1.69,0.62,200,0.19,1,100,0.8,0,23]
[4,11.9,100,26,99,1.84,0.61,200,0.19,1,100,0.8,0,23]
[4,6,100,26,1,0.7,0.7,300,0.19,0,4,1.2,0,48]
[4,7.1,100,26,50,1.1000000000000001,0.67,300,0.19,1,98,1.2,0,48]
[4,7.6,100,26,60,1.26,0.67,300,0.19,1,98,1.2,0,48]
[4,8.1,100,26,70,1.42,0.66,300,0.19,1,99,1.2,0,48]
[4,8.5,100,26,80,1.58,0.65,300,0.19,1,99,1.2,0,48]
[4,9,100,26,90,1.75,0.65,300,0.19,1,100,1.2,0,48]
[4,9.4,100,26,99,1.89,0.64,300,0.19,1,100,1.2,0,48]
[4,9.8000000000000007,100,27,1,0.68,0.68,100,0.19,0,3,0.4,0,7]
[4,12.4,100,27,50,0.98,0.61,100,0.19,1,98,0.4,0,7]
[4,13.6,100,27,60,1.1200000000000001,0.59,100,0.19,1,98,0.4,0,7]
[4,14.9,100,27,70,1.26,0.56999999999999995,100,0.19,1,99,0.4,0,7]
[4,16.100000000000001,100,27,80,1.41,0.55000000000000004,100,0.19,1,99,0.4,0,7]
[4,17.3,100,27,90,1.55,0.53,100,0.19,1,100,0.4,0,7]
[4,18.399999999999999,100,27,99,1.68,0.51,100,0.19,1,100,0.4,0,7]
[4,7.1,100,27,1,0.72,0.72,200,0.19,0,4,0.8,0,24]
[4,8.9,100,27,50,1.1399999999999999,0.68,200,0.19,1,98,0.8,0,24]
[4,9.6,100,27,60,1.3,0.67,200,0.19,1,98,0.8,0,24]
[4,10.3,100,27,70,1.47,0.66,200,0.19,1,99,0.8,0,23]
[4,11,100,27,80,1.64,0.65,200,0.19,1,99,0.8,0,23]
[4,11.7,100,27,90,1.81,0.65,200,0.19,1,100,0.8,0,23]
[4,12.4,100,27,99,1.96,0.64,200,0.19,1,100,0.8,0,23]
[4,6.1,100,27,1,0.73,0.73,300,0.19,0,4,1.2,0,48]
[4,7.3,100,27,50,1.17,0.7,300,0.19,1,98,1.2,0,48]
[4,7.8,100,27,60,1.35,0.69,300,0.19,1,98,1.2,0,48]
[4,8.3000000000000007,100,27,70,1.52,0.69,300,0.19,1,99,1.2,0,48]
[4,8.8000000000000007,100,27,80,1.69,0.68,300,0.19,1,99,1.2,0,48]
[4,9.3000000000000007,100,27,90,1.86,0.67,300,0.19,1,100,1.2,0,48]
[4,9.8000000000000007,100,27,99,2.02,0.67,300,0.19,1,100,1.2,0,48]
[4,10.3,170,21,1,0.74,0.74,100,0.33,1,2,0.4,0,7]
[4,10.8,170,21,50,0.79,0.66,100,0.33,1,95,0.4,0,7]
[4,11.9,170,21,60,0.92,0.63,100,0.33,1,96,0.4,0,7]
[4,13,170,21,70,1.05,0.59,100,0.33,1,97,0.4,0,7]
[4,14.1,170,21,80,1.17,0.55000000000000004,100,0.33,1,98,0.4,0,7]
[4,15.1,170,21,90,1.3,0.52,100,0.33,1,99,0.4,0,7]
[4,16.100000000000001,170,21,99,1.41,0.48,100,0.33,1,100,0.4,0,7]
[4,7.6,170,21,1,0.83,0.83,200,0.33,1,2,0.8,0,24]
[4,8.5,170,21,50,1.04,0.78,200,0.33,1,94,0.8,0,24]
[4,9.1999999999999993,170,21,60,1.22,0.76,200,0.33,1,96,0.8,0,24]
[4,10,170,21,70,1.39,0.74,200,0.33,1,97,0.8,0,23]
[4,10.7,170,21,80,1.56,0.72,200,0.33,1,98,0.8,0,23]
[4,11.4,170,21,90,1.73,0.7,200,0.33,1,99,0.8,0,23]
[4,12.1,170,21,99,1.89,0.68,200,0.33,1,100,0.8,0,23]
[4,6.5,170,21,1,0.86,0.86,300,0.33,1,2,1.2,0,48]
[4,7.2,170,21,50,1.1299999999999999,0.82,300,0.33,1,94,1.2,0,48]
[4,7.8,170,21,60,1.31,0.81,300,0.33,1,96,1.2,0,48]
[4,8.3000000000000007,170,21,70,1.5,0.8,300,0.33,1,97,1.2,0,48]
[4,8.8000000000000007,170,21,80,1.68,0.78,300,0.33,1,98,1.2,0,48]
[4,9.3000000000000007,170,21,90,1.87,0.77,300,0.33,1,99,1.2,0,48]
[4,9.8000000000000007,170,21,99,2.04,0.75,300,0.33,1,100,1.2,0,48]
[4,10.7,170,22,1,0.78,0.78,100,0.33,1,2,0.4,0,7]
[4,11.4,170,22,50,0.86,0.69,100,0.33,1,95,0.4,0,7]
[4,12.6,170,22,60,1,0.65,100,0.33,1,96,0.4,0,7]
[4,13.7,170,22,70,1.1299999999999999,0.61,100,0.33,1,97,0.4,0,7]
[4,14.9,170,22,80,1.27,0.57999999999999996,100,0.33,1,98,0.4,0,7]
[4,16,170,22,90,1.4,0.54,100,0.33,1,99,0.4,0,7]
[4,17,170,22,99,1.52,0.5,100,0.33,1,100,0.4,0,7]
[4,7.8,170,22,1,0.88,0.88,200,0.33,1,2,0.8,0,24]
[4,8.9,170,22,50,1.1399999999999999,0.82,200,0.33,1,94,0.8,0,24]
[4,9.6999999999999993,170,22,60,1.32,0.8,200,0.33,1,96,0.8,0,24]
[4,10.5,170,22,70,1.51,0.78,200,0.33,1,97,0.8,0,23]
[4,11.2,170,22,80,1.69,0.76,200,0.33,1,98,0.8,0,23]
[4,12,170,22,90,1.87,0.74,200,0.33,1,99,0.8,0,23]
[4,12.7,170,22,99,2.0299999999999998,0.72,200,0.33,1,100,0.8,0,23]
[4,6.6,170,22,1,0.91,0.91,300,0.33,1,3,1.2,0,48]
[4,7.5,170,22,50,1.23,0.87,300,0.33,1,94,1.2,0,48]
[4,8.1,170,22,60,1.43,0.85,300,0.33,1,96,1.2,0,48]
[4,8.6,170,22,70,1.63,0.84,300,0.33,1,97,1.2,0,48]
[4,9.1999999999999993,170,22,80,1.82,0.82,300,0.33,1,98,1.2,0,48]
[4,9.8000000000000007,170,22,90,2.02,0.81,300,0.33,1,99,1.2,0,48]
[4,10.3,170,22,99,2.2000000000000002,0.79,300,0.33,1,100,1.2,0,48]
[4,11.1,170,23,1,0.82,0.82,100,0.33,1,2,0.4,0,7]
[4,12,170,23,50,0.94,0.72,100,0.33,1,95,0.4,0,7]
[4,13.3,170,23,60,1.08,0.68,100,0.33,1,96,0.4,0,7]
[4,14.5,170,23,70,1.22,0.64,100,0.33,1,97,0.4,0,7]
[4,15.7,170,23,80,1.37,0.6,100,0.33,1,98,0.4,0,7]
[4,16.899999999999999,170,23,90,1.5,0.56000000000000005,100,0.33,1,99,0.4,0,7]
[4,18,170,23,99,1.63,0.52,100,0.33,1,100,0.4,0,7]
[4,8,170,23,1,0.93,0.93,200,0.33,1,3,0.8,0,24]
[4,9.3000000000000007,170,23,50,1.24,0.86,200,0.33,1,94,0.8,0,24]
[4,10.1,170,23,60,1.43,0.84,200,0.33,1,96,0.8,0,23]
[4,11,170,23,70,1.63,0.82,200,0.33,1,97,0.8,0,23]
[4,11.8,170,23,80,1.82,0.79,200,0.33,1,98,0.8,0,23]
[4,12.6,170,23,90,2.0099999999999998,0.77,200,0.33,1,99,0.8,0,23]
[4,13.4,170,23,99,2.19,0.75,200,0.33,1,100,0.8,0,23]
[4,6.7,170,23,1,0.96,0.96,300,0.33,1,3,1.2,0,48]
[4,7.8,170,23,50,1.34,0.91,300,0.33,1,94,1.2,0,48]
[4,8.4,170,23,60,1.55,0.89,300,0.33,1,96,1.2,0,48]
[4,9,170,23,70,1.75,0.88,300,0.33,1,97,1.2,0,48]
[4,9.6,170,23,80,1.97,0.86,300,0.33,1,98,1.2,0,48]
[4,10.199999999999999,170,23,90,2.17,0.85,300,0.33,1,99,1.2,0,48]
[4,10.8,170,23,99,2.36,0.83,300,0.33,1,100,1.2,0,48]
[4,11.4,170,24,1,0.87,0.87,100,0.33,1,2,0.4,0,7]
[4,12.7,170,24,50,1.01,0.75,100,0.33,1,95,0.4,0,7]
[4,14,170,24,60,1.17,0.71,100,0.33,1,96,0.4,0,7]
[4,15.3,170,24,70,1.32,0.66,100,0.33,1,97,0.4,0,7]
[4,16.600000000000001,170,24,80,1.47,0.62,100,0.33,1,98,0.4,0,7]
[4,17.8,170,24,90,1.61,0.57999999999999996,100,0.33,1,99,0.4,0,7]
[4,19,170,24,99,1.74,0.54,100,0.33,1,100,0.4,0,7]
[4,8.1999999999999993,170,24,1,0.97,0.97,200,0.33,1,3,0.8,0,24]
[4,9.8000000000000007,170,24,50,1.34,0.9,200,0.33,1,94,0.8,0,24]
[4,10.6,170,24,60,1.55,0.88,200,0.33,1,96,0.8,0,23]
[4,11.5,170,24,70,1.75,0.85,200,0.33,1,97,0.8,0,23]
[4,12.4,170,24,80,1.96,0.83,200,0.33,1,98,0.8,0,23]
[4,13.3,170,24,90,2.16,0.8,200,0.33,1,99,0.8,0,23]
[4,14.1,170,24,99,2.34,0.78,200,0.33,1,100,0.8,0,23]
[4,6.9,170,24,1,1.01,1.01,300,0.33,1,3,1.2,0,48]
[4,8.1,170,24,50,1.45,0.95,300,0.33,1,94,1.2,0,48]
[4,8.8000000000000007,170,24,60,1.67,0.93,300,0.33,1,96,1.2,0,48]
[4,9.4,170,24,70,1.89,0.92,300,0.33,1,97,1.2,0,48]
[4,10,170,24,80,2.11,0.9,300,0.33,1,98,1.2,0,48]
[4,10.7,170,24,90,2.34,0.88,300,0.33,1,99,1.2,0,48]
[4,11.2,170,24,99,2.5299999999999998,0.87,300,0.33,1,100,1.2,0,48]
[4,11.8,170,25,1,0.91,0.91,100,0.33,1,2,0.4,0,7]
[4,13.4,170,25,50,1.0900000000000001,0.78,100,0.33,1,95,0.4,0,7]
[4,14.7,170,25,60,1.25,0.73,100,0.33,1,96,0.4,0,7]
[4,16.100000000000001,170,25,70,1.41,0.69,100,0.33,1,97,0.4,0,7]
[4,17.5,170,25,80,1.57,0.64,100,0.33,1,98,0.4,0,7]
[4,18.8,170,25,90,1.72,0.6,100,0.33,1,99,0.4,0,7]
[4,20,170,25,99,1.86,0.56000000000000005,100,0.33,1,100,0.4,0,7]
[4,8.4,170,25,1,1.02,1.02,200,0.33,1,3,0.8,0,24]
[4,10.199999999999999,170,25,50,1.45,0.94,200,0.33,1,94,0.8,0,23]
[4,11.1,170,25,60,1.66,0.91,200,0.33,1,96,0.8,0,23]
[4,12.1,170,25,70,1.88,0.89,200,0.33,1,97,0.8,0,23]
[4,13,170,25,80,2.1,0.86,200,0.33,1,98,0.8,0,23]
[4,13.9,170,25,90,2.31,0.84,200,0.33,1,99,0.8,0,23]
[4,14.8,170,25,99,2.5099999999999998,0.81,200,0.33,1,100,0.8,0,23]
[4,7,170,25,1,1.05,1.05,300,0.33,1,3,1.2,0,48]
[4,8.5,170,25,50,1.56,0.99,300,0.33,1,94,1.2,0,48]
[4,9.1,170,25,60,1.79,0.97,300,0.33,1,95,1.2,0,48]
[4,9.8000000000000007,170,25,70,2.0299999999999998,0.96,300,0.33,1,97,1.2,0,48]
[4,10.5,170,25,80,2.2599999999999998,0.94,300,0.33,1,98,1.2,0,48]
[4,11.1,170,25,90,2.5,0.92,300,0.33,1,99,1.2,0,48]
[4,11.8,170,25,99,2.71,0.9,300,0.33,1,100,1.2,0,47]
[4,12.1,170,26,1,0.95,0.95,100,0.33,1,2,0.4,0,7]
[4,14.1,170,26,50,1.17,0.81,100,0.33,1,95,0.4,0,7]
[4,15.5,170,26,60,1.34,0.76,100,0.33,1,96,0.4,0,7]
[4,16.899999999999999,170,26,70,1.51,0.71,100,0.33,1,97,0.4,0,7]
[4,18.399999999999999,170,26,80,1.67,0.66,100,0.33,1,98,0.4,0,7]
[4,19.8,170,26,90,1.84,0.61,100,0.33,1,99,0.4,0,7]
[4,21,170,26,99,1.98,0.56999999999999995,100,0.33,1,100,0.4,0,7]
[4,8.6,170,26,1,1.07,1.07,200,0.33,1,3,0.8,0,24]
[4,10.7,170,26,50,1.55,0.98,200,0.33,1,94,0.8,0,23]
[4,11.6,170,26,60,1.78,0.95,200,0.33,1,96,0.8,0,23]
[4,12.6,170,26,70,2.0099999999999998,0.92,200,0.33,1,97,0.8,0,23]
[4,13.6,170,26,80,2.2400000000000002,0.89,200,0.33,1,98,0.8,0,23]
[4,14.6,170,26,90,2.4700000000000002,0.87,200,0.33,1,99,0.8,0,23]
[4,15.5,170,26,99,2.68,0.84,200,0.33,1,100,0.8,0,23]
[4,7.1,170,26,1,1.1000000000000001,1.1000000000000001,300,0.33,1,3,1.2,0,48]
[4,8.8000000000000007,170,26,50,1.67,1.03,300,0.33,1,94,1.2,0,48]
[4,9.5,170,26,60,1.92,1.01,300,0.33,1,95,1.2,0,48]
[4,10.199999999999999,170,26,70,2.17,0.99,300,0.33,1,97,1.2,0,48]
[4,10.9,170,26,80,2.42,0.98,300,0.33,1,98,1.2,0,48]
[4,11.6,170,26,90,2.67,0.96,300,0.33,1,99,1.2,0,47]
[4,12.3,170,26,99,2.9,0.94,300,0.33,1,100,1.2,0,47]
[4,12.5,170,27,1,0.99,0.99,100,0.33,1,2,0.4,0,7]
[4,14.8,170,27,50,1.25,0.83,100,0.33,1,95,0.4,0,7]
[4,16.3,170,27,60,1.43,0.78,100,0.33,1,96,0.4,0,7]
[4,17.8,170,27,70,1.61,0.73,100,0.33,1,97,0.4,0,7]
[4,19.3,170,27,80,1.78,0.68,100,0.33,1,98,0.4,0,7]
[4,20.8,170,27,90,1.95,0.63,100,0.33,1,99,0.4,0,7]
[4,22,170,27,99,2.1,0.59,100,0.33,1,100,0.4,0,7]
[4,8.8000000000000007,170,27,1,1.1100000000000001,1.1100000000000001,200,0.33,1,3,0.8,0,24]
[4,11.1,170,27,50,1.66,1.01,200,0.33,1,94,0.8,0,23]
[4,12.2,170,27,60,1.91,0.98,200,0.33,1,96,0.8,0,23]
[4,13.2,170,27,70,2.15,0.96,200,0.33,1,97,0.8,0,23]
[4,14.3,170,27,80,2.39,0.93,200,0.33,1,98,0.8,0,23]
[4,15.3,170,27,90,2.63,0.9,200,0.33,1,99,0.8,0,23]
[4,16.2,170,27,99,2.85,0.87,200,0.33,1,100,0.8,0,23]
[4,7.3,170,27,1,1.1499999999999999,1.1499999999999999,300,0.33,1,3,1.2,0,48]
[4,9.1,170,27,50,1.79,1.07,300,0.33,1,94,1.2,0,48]
[4,9.9,170,27,60,2.06,1.05,300,0.33,1,95,1.2,0,48]
[4,10.6,170,27,70,2.3199999999999998,1.03,300,0.33,1,97,1.2,0,48]
[4,11.4,170,27,80,2.59,1.01,300,0.33,1,98,1.2,0,48]
[4,12.1,170,27,90,2.85,0.99,300,0.33,1,99,1.2,0,47]
[4,12.8,170,27,99,3.09,0.97,300,0.33,1,100,1.2,0,47]
[4,11.7,240,21,1,0.9,0.9,100,0.46,2,2,0.4,0,7]
[4,11.6,240,21,50,0.88,0.81,100,0.46,3,92,0.4,0,7]
[4,12.8,240,21,60,1.02,0.75,100,0.46,3,94,0.4,0,7]
[4,14,240,21,70,1.1599999999999999,0.69,100,0.46,3,96,0.4,0,7]
[4,15.2,240,21,80,1.3,0.63,100,0.46,3,97,0.4,0,7]
[4,16.3,240,21,90,1.44,0.56999999999999995,100,0.46,3,99,0.4,0,7]
[4,17.399999999999999,240,21,99,1.56,0.52,100,0.46,3,100,0.4,0,7]
[4,8.6,240,21,1,1.07,1.07,200,0.46,2,2,0.8,0,24]
[4,9.4,240,21,50,1.27,0.99,200,0.46,3,91,0.8,0,24]
[4,10.3,240,21,60,1.48,0.95,200,0.46,3,93,0.8,0,23]
[4,11.2,240,21,70,1.68,0.91,200,0.46,3,95,0.8,0,23]
[4,12.1,240,21,80,1.89,0.87,200,0.46,3,97,0.8,0,23]
[4,13,240,21,90,2.1,0.83,200,0.46,3,99,0.8,0,23]
[4,13.8,240,21,99,2.2799999999999998,0.8,200,0.46,3,100,0.8,0,23]
[4,7.2,240,21,1,1.1200000000000001,1.1200000000000001,300,0.46,2,2,1.2,0,48]
[4,8.1,240,21,50,1.42,1.06,300,0.46,3,91,1.2,0,48]
[4,8.6999999999999993,240,21,60,1.65,1.03,300,0.46,3,93,1.2,0,48]
[4,9.4,240,21,70,1.89,1,300,0.46,3,95,1.2,0,48]
[4,10.1,240,21,80,2.12,0.98,300,0.46,3,97,1.2,0,48]
[4,10.7,240,21,90,2.36,0.95,300,0.46,3,98,1.2,0,48]
[4,11.3,240,21,99,2.56,0.92,300,0.46,3,100,1.2,0,48]
[4,12.1,240,22,1,0.95,0.95,100,0.46,2,2,0.4,0,7]
[4,12.3,240,22,50,0.96,0.85,100,0.46,3,92,0.4,0,7]
[4,13.5,240,22,60,1.1100000000000001,0.78,100,0.46,3,94,0.4,0,7]
[4,14.8,240,22,70,1.26,0.72,100,0.46,3,96,0.4,0,7]
[4,16.100000000000001,240,22,80,1.41,0.65,100,0.46,3,97,0.4,0,7]
[4,17.3,240,22,90,1.55,0.59,100,0.46,3,99,0.4,0,7]
[4,18.399999999999999,240,22,99,1.67,0.53,100,0.46,3,100,0.4,0,7]
[4,8.8000000000000007,240,22,1,1.1299999999999999,1.1299999999999999,200,0.46,2,2,0.8,0,24]
[4,9.9,240,22,50,1.39,1.03,200,0.46,3,91,0.8,0,23]
[4,10.9,240,22,60,1.61,0.99,200,0.46,3,93,0.8,0,23]
[4,11.8,240,22,70,1.83,0.95,200,0.46,3,95,0.8,0,23]
[4,12.8,240,22,80,2.04,0.91,200,0.46,3,97,0.8,0,23]
[4,13.7,240,22,90,2.2599999999999998,0.87,200,0.46,3,99,0.8,0,23]
[4,14.5,240,22,99,2.46,0.83,200,0.46,3,100,0.8,0,23]
[4,7.4,240,22,1,1.19,1.19,300,0.46,2,2,1.2,0,48]
[4,8.4,240,22,50,1.55,1.1100000000000001,300,0.46,3,91,1.2,0,48]
[4,9.1,240,22,60,1.8,1.08,300,0.46,3,93,1.2,0,48]
[4,9.8000000000000007,240,22,70,2.0499999999999998,1.05,300,0.46,3,95,1.2,0,48]
[4,10.6,240,22,80,2.2999999999999998,1.02,300,0.46,3,97,1.2,0,48]
[4,11.3,240,22,90,2.54,0.99,300,0.46,3,98,1.2,0,48]
[4,11.9,240,22,99,2.77,0.97,300,0.46,3,100,1.2,0,47]
[4,12.6,240,23,1,1,1,100,0.46,2,2,0.4,0,7]
[4,13,240,23,50,1.05,0.88,100,0.46,3,92,0.4,0,7]
[4,14.3,240,23,60,1.2,0.81,100,0.46,3,94,0.4,0,7]
[4,15.6,240,23,70,1.36,0.74,100,0.46,3,96,0.4,0,7]
[4,17,240,23,80,1.51,0.68,100,0.46,3,97,0.4,0,7]
[4,18.2,240,23,90,1.66,0.61,100,0.46,3,99,0.4,0,7]
[4,19.399999999999999,240,23,99,1.79,0.55000000000000004,100,0.46,3,100,0.4,0,7]
[4,9.1,240,23,1,1.19,1.19,200,0.46,2,2,0.8,0,24]
[4,10.5,240,23,50,1.51,1.08,200,0.46,3,91,0.8,0,23]
[4,11.5,240,23,60,1.74,1.04,200,0.46,3,93,0.8,0,23]
[4,12.5,240,23,70,1.97,0.99,200,0.46,3,95,0.8,0,23]
[4,13.4,240,23,80,2.2000000000000002,0.95,200,0.46,3,97,0.8,0,23]
[4,14.4,240,23,90,2.4300000000000002,0.91,200,0.46,3,99,0.8,0,23]
[4,15.3,240,23,99,2.64,0.87,200,0.46,3,100,0.8,0,23]
[4,7.6,240,23,1,1.25,1.25,300,0.46,2,2,1.2,0,48]
[4,8.8000000000000007,240,23,50,1.69,1.1599999999999999,300,0.46,3,91,1.2,0,48]
[4,9.6,240,23,60,1.95,1.1299999999999999,300,0.46,3,93,1.2,0,48]
[4,10.3,240,23,70,2.21,1.1000000000000001,300,0.46,3,95,1.2,0,48]
[4,11.1,240,23,80,2.48,1.07,300,0.46,3,97,1.2,0,48]
[4,11.8,240,23,90,2.74,1.04,300,0.46,3,98,1.2,0,47]
[4,12.5,240,23,99,2.97,1.01,300,0.46,3,100,1.2,0,47]
[4,13,240,24,1,1.05,1.05,100,0.46,2,2,0.4,0,7]
[4,13.7,240,24,50,1.1299999999999999,0.91,100,0.46,3,92,0.4,0,7]
[4,15.1,240,24,60,1.29,0.84,100,0.46,3,94,0.4,0,7]
[4,16.5,240,24,70,1.46,0.77,100,0.46,3,96,0.4,0,7]
[4,17.899999999999999,240,24,80,1.62,0.7,100,0.46,3,97,0.4,0,7]
[4,19.2,240,24,90,1.77,0.63,100,0.46,3,99,0.4,0,7]
[4,20.399999999999999,240,24,99,1.91,0.56999999999999995,100,0.46,3,100,0.4,0,7]
[4,9.4,240,24,1,1.25,1.25,200,0.46,2,2,0.8,0,24]
[4,11,240,24,50,1.63,1.1299999999999999,200,0.46,3,91,0.8,0,23]
[4,12,240,24,60,1.88,1.08,200,0.46,3,93,0.8,0,23]
[4,13.1,240,24,70,2.12,1.04,200,0.46,3,95,0.8,0,23]
[4,14.2,240,24,80,2.37,0.99,200,0.46,3,97,0.8,0,23]
[4,15.2,240,24,90,2.61,0.94,200,0.46,3,99,0.8,0,23]
[4,16.100000000000001,240,24,99,2.83,0.9,200,0.46,3,100,0.8,0,23]
[4,7.8,240,24,1,1.31,1.31,300,0.46,2,2,1.2,0,48]
[4,9.1999999999999993,240,24,50,1.82,1.22,300,0.46,3,91,1.2,0,48]
[4,10,240,24,60,2.1,1.18,300,0.46,3,93,1.2,0,48]
[4,10.8,240,24,70,2.38,1.1499999999999999,300,0.46,3,95,1.2,0,48]
[4,11.6,240,24,80,2.66,1.1200000000000001,300,0.46,3,97,1.2,0,47]
[4,12.4,240,24,90,2.94,1.08,300,0.46,3,98,1.2,0,47]
[4,13.1,240,24,99,3.19,1.05,300,0.46,3,100,1.2,0,47]
[4,13.5,240,25,1,1.1100000000000001,1.1100000000000001,100,0.46,2,2,0.4,0,7]
[4,14.4,240,25,50,1.21,0.94,100,0.46,3,92,0.4,0,7]
[4,15.9,240,25,60,1.39,0.87,100,0.46,3,94,0.4,0,7]
[4,17.399999999999999,240,25,70,1.56,0.79,100,0.46,3,96,0.4,0,7]
[4,18.8,240,25,80,1.73,0.72,100,0.46,3,97,0.4,0,7]
[4,20.2,240,25,90,1.89,0.64,100,0.46,3,99,0.4,0,7]
[4,21.5,240,25,99,2.0299999999999998,0.57999999999999996,100,0.46,3,100,0.4,0,7]
[4,9.6,240,25,1,1.31,1.31,200,0.46,2,2,0.8,0,24]
[4,11.5,240,25,50,1.75,1.17,200,0.46,3,91,0.8,0,23]
[4,12.6,240,25,60,2.02,1.1200000000000001,200,0.46,3,93,0.8,0,23]
[4,13.8,240,25,70,2.2799999999999998,1.07,200,0.46,3,95,0.8,0,23]
[4,14.9,240,25,80,2.54,1.03,200,0.46,3,97,0.8,0,23]
[4,16,240,25,90,2.79,0.98,200,0.46,3,99,0.8,0,23]
[4,17,240,25,99,3.02,0.94,200,0.46,3,100,0.8,0,23]
[4,7.9,240,25,1,1.38,1.38,300,0.46,2,3,1.2,0,48]
[4,9.6,240,25,50,1.97,1.27,300,0.46,3,91,1.2,0,48]
[4,10.5,240,25,60,2.2599999999999998,1.23,300,0.46,3,93,1.2,0,48]
[4,11.3,240,25,70,2.56,1.2,300,0.46,3,95,1.2,0,48]
[4,12.2,240,25,80,2.85,1.1599999999999999,300,0.46,3,97,1.2,0,47]
[4,13,240,25,90,3.15,1.1200000000000001,300,0.46,3,98,1.2,0,47]
[4,13.8,240,25,99,3.41,1.0900000000000001,300,0.46,3,100,1.2,0,47]
[4,13.9,240,26,1,1.1599999999999999,1.1599999999999999,100,0.46,2,2,0.4,0,7]
[4,15.2,240,26,50,1.3,0.97,100,0.46,3,92,0.4,0,7]
[4,16.7,240,26,60,1.48,0.89,100,0.46,3,94,0.4,0,7]
[4,18.3,240,26,70,1.66,0.81,100,0.46,3,96,0.4,0,7]
[4,19.8,240,26,80,1.84,0.74,100,0.46,3,97,0.4,0,7]
[4,21.2,240,26,90,2.0099999999999998,0.66,100,0.46,3,99,0.4,0,7]
[4,22.5,240,26,99,2.16,0.59,100,0.46,3,100,0.4,0,7]
[4,9.9,240,26,1,1.37,1.37,200,0.46,2,2,0.8,0,23]
[4,12.1,240,26,50,1.88,1.22,200,0.46,3,91,0.8,0,23]
[4,13.3,240,26,60,2.16,1.1599999999999999,200,0.46,3,93,0.8,0,23]
[4,14.5,240,26,70,2.44,1.1100000000000001,200,0.46,3,95,0.8,0,23]
[4,15.6,240,26,80,2.71,1.06,200,0.46,3,97,0.8,0,23]
[4,16.8,240,26,90,2.98,1.01,200,0.46,3,99,0.8,0,23]
[4,17.899999999999999,240,26,99,3.23,0.97,200,0.46,3,100,0.8,0,23]
[4,8.1,240,26,1,1.44,1.44,300,0.46,2,3,1.2,0,48]
[4,10,240,26,50,2.11,1.32,300,0.46,3,91,1.2,0,48]
[4,10.9,240,26,60,2.42,1.28,300,0.46,3,93,1.2,0,48]
[4,11.8,240,26,70,2.74,1.24,300,0.46,3,95,1.2,0,47]
[4,12.7,240,26,80,3.05,1.2,300,0.46,3,97,1.2,0,47]
[4,13.6,240,26,90,3.36,1.17,300,0.46,3,98,1.2,0,47]
[4,14.4,240,26,99,3.65,1.1299999999999999,300,0.46,3,100,1.2,0,47]
[4,14.4,240,27,1,1.21,1.21,100,0.46,2,2,0.4,0,7]
[4,15.9,240,27,50,1.39,1,100,0.46,3,92,0.4,0,7]
[4,17.600000000000001,240,27,60,1.58,0.92,100,0.46,3,94,0.4,0,7]
[4,19.2,240,27,70,1.77,0.84,100,0.46,3,96,0.4,0,7]
[4,20.8,240,27,80,1.95,0.76,100,0.46,3,97,0.4,0,7]
[4,22.3,240,27,90,2.13,0.67,100,0.46,3,99,0.4,0,7]
[4,23.6,240,27,99,2.2799999999999998,0.6,100,0.46,3,100,0.4,0,7]
[4,10.1,240,27,1,1.43,1.43,200,0.46,2,3,0.8,0,23]
[4,12.7,240,27,50,2.02,1.26,200,0.46,3,91,0.8,0,23]
[4,13.9,240,27,60,2.31,1.2,200,0.46,3,93,0.8,0,23]
[4,15.2,240,27,70,2.6,1.1499999999999999,200,0.46,3,95,0.8,0,23]
[4,16.399999999999999,240,27,80,2.89,1.1000000000000001,200,0.46,3,97,0.8,0,23]
[4,17.600000000000001,240,27,90,3.18,1.04,200,0.46,3,99,0.8,0,23]
[4,18.8,240,27,99,3.43,0.99,200,0.46,3,100,0.8,0,23]
[4,8.3000000000000007,240,27,1,1.5,1.5,300,0.46,2,3,1.2,0,48]
[4,10.5,240,27,50,2.2599999999999998,1.37,300,0.46,3,91,1.2,0,48]
[4,11.4,240,27,60,2.59,1.33,300,0.46,3,93,1.2,0,48]
[4,12.4,240,27,70,2.92,1.29,300,0.46,3,95,1.2,0,47]
[4,13.3,240,27,80,3.26,1.25,300,0.46,3,97,1.2,0,47]
[4,14.3,240,27,90,3.59,1.21,300,0.46,3,98,1.2,0,47]
[4,15.1,240,27,99,3.89,1.17,300,0.46,3,100,1.2,0,47]
[4,12.7,310,21,1,1.01,1.01,100,0.6,3,1,0.4,0,7]
[4,12.6,310,21,50,1.01,1.01,100,0.6,3,94,0.4,0,7]
[4,13.3,310,21,60,1.0900000000000001,0.85,100,0.6,4,92,0.4,0,7]
[4,14.6,310,21,70,1.23,0.77,100,0.6,4,94,0.4,0,7]
[4,15.8,310,21,80,1.38,0.69,100,0.6,4,96,0.4,0,7]
[4,17,310,21,90,1.52,0.6,100,0.6,4,98,0.4,0,7]
[4,18.100000000000001,310,21,99,1.64,0.53,100,0.6,4,100,0.4,0,7]
[4,9.4,310,21,1,1.26,1.26,200,0.6,3,2,0.8,0,24]
[4,10.1,310,21,50,1.43,1.1499999999999999,200,0.6,4,89,0.8,0,23]
[4,11.1,310,21,60,1.66,1.0900000000000001,200,0.6,4,91,0.8,0,23]
[4,12.1,310,21,70,1.89,1.04,200,0.6,4,94,0.8,0,23]
[4,13.1,310,21,80,2.12,0.98,200,0.6,4,96,0.8,0,23]
[4,14.1,310,21,90,2.35,0.92,200,0.6,4,98,0.8,0,23]
[4,15,310,21,99,2.5499999999999998,0.87,200,0.6,4,100,0.8,0,23]
[4,7.8,310,21,1,1.34,1.34,300,0.6,3,2,1.2,0,48]
[4,8.6999999999999993,310,21,50,1.65,1.25,300,0.6,4,88,1.2,0,48]
[4,9.5,310,21,60,1.92,1.21,300,0.6,4,91,1.2,0,48]
[4,10.3,310,21,70,2.19,1.17,300,0.6,4,94,1.2,0,48]
[4,11,310,21,80,2.46,1.1200000000000001,300,0.6,4,96,1.2,0,48]
[4,11.8,310,21,90,2.73,1.08,300,0.6,4,98,1.2,0,47]
[4,12.5,310,21,99,2.97,1.04,300,0.6,4,100,1.2,0,47]
[4,13.2,310,22,1,1.07,1.07,100,0.6,3,2,0.4,0,7]
[4,13.1,310,22,50,1.07,1.07,100,0.6,3,97,0.4,0,7]
[4,14.1,310,22,60,1.18,0.89,100,0.6,4,92,0.4,0,7]
[4,15.4,310,22,70,1.33,0.8,100,0.6,4,94,0.4,0,7]
[4,16.7,310,22,80,1.48,0.71,100,0.6,4,96,0.4,0,7]
[4,18,310,22,90,1.63,0.62,100,0.6,4,98,0.4,0,7]
[4,19.100000000000001,310,22,99,1.76,0.55000000000000004,100,0.6,4,100,0.4,0,7]
[4,9.6999999999999993,310,22,1,1.33,1.33,200,0.6,3,2,0.8,0,24]
[4,10.7,310,22,50,1.56,1.2,200,0.6,4,89,0.8,0,23]
[4,11.7,310,22,60,1.8,1.1399999999999999,200,0.6,4,91,0.8,0,23]
[4,12.8,310,22,70,2.0499999999999998,1.08,200,0.6,4,94,0.8,0,23]
[4,13.8,310,22,80,2.29,1.02,200,0.6,4,96,0.8,0,23]
[4,14.9,310,22,90,2.5299999999999998,0.96,200,0.6,4,98,0.8,0,23]
[4,15.8,310,22,99,2.75,0.91,200,0.6,4,100,0.8,0,23]
[4,8.1,310,22,1,1.42,1.42,300,0.6,3,2,1.2,0,48]
[4,9.1,310,22,50,1.8,1.31,300,0.6,4,88,1.2,0,48]
[4,10,310,22,60,2.09,1.27,300,0.6,4,91,1.2,0,48]
[4,10.8,310,22,70,2.37,1.22,300,0.6,4,94,1.2,0,48]
[4,11.6,310,22,80,2.66,1.18,300,0.6,4,96,1.2,0,47]
[4,12.4,310,22,90,2.94,1.1299999999999999,300,0.6,4,98,1.2,0,47]
[4,13.2,310,22,99,3.2,1.0900000000000001,300,0.6,4,100,1.2,0,47]
[4,13.7,310,23,1,1.1299999999999999,1.1299999999999999,100,0.6,3,2,0.4,0,7]
[4,13.5,310,23,50,1.1100000000000001,1.01,100,0.6,4,90,0.4,0,7]
[4,14.9,310,23,60,1.27,0.92,100,0.6,4,92,0.4,0,7]
[4,16.3,310,23,70,1.43,0.82,100,0.6,4,94,0.4,0,7]
[4,17.7,310,23,80,1.59,0.73,100,0.6,4,96,0.4,0,7]
[4,19,310,23,90,1.75,0.64,100,0.6,4,98,0.4,0,7]
[4,20.100000000000001,310,23,99,1.88,0.56999999999999995,100,0.6,4,100,0.4,0,7]
[4,10,310,23,1,1.4,1.4,200,0.6,3,2,0.8,0,23]
[4,11.3,310,23,50,1.69,1.26,200,0.6,4,89,0.8,0,23]
[4,12.4,310,23,60,1.95,1.19,200,0.6,4,91,0.8,0,23]
[4,13.5,310,23,70,2.21,1.1299999999999999,200,0.6,4,94,0.8,0,23]
[4,14.6,310,23,80,2.4700000000000002,1.06,200,0.6,4,96,0.8,0,23]
[4,15.7,310,23,90,2.72,1,200,0.6,4,98,0.8,0,23]
[4,16.7,310,23,99,2.95,0.94,200,0.6,4,100,0.8,0,23]
[4,8.3000000000000007,310,23,1,1.5,1.5,300,0.6,3,2,1.2,0,48]
[4,9.6,310,23,50,1.96,1.37,300,0.6,4,88,1.2,0,48]
[4,10.5,310,23,60,2.2599999999999998,1.32,300,0.6,4,91,1.2,0,48]
[4,11.3,310,23,70,2.56,1.28,300,0.6,4,94,1.2,0,48]
[4,12.2,310,23,80,2.87,1.23,300,0.6,4,96,1.2,0,47]
[4,13.1,310,23,90,3.17,1.18,300,0.6,4,98,1.2,0,47]
[4,13.8,310,23,99,3.44,1.1299999999999999,300,0.6,4,100,1.2,0,47]
[4,14.2,310,24,1,1.19,1.19,100,0.6,3,2,0.4,0,7]
[4,14.3,310,24,50,1.2,1.05,100,0.6,4,90,0.4,0,7]
[4,15.7,310,24,60,1.37,0.95,100,0.6,4,92,0.4,0,7]
[4,17.2,310,24,70,1.54,0.85,100,0.6,4,94,0.4,0,7]
[4,18.600000000000001,310,24,80,1.7,0.76,100,0.6,4,96,0.4,0,7]
[4,20,310,24,90,1.86,0.66,100,0.6,4,98,0.4,0,7]
[4,21.2,310,24,99,2,0.57999999999999996,100,0.6,4,100,0.4,0,7]
[4,10.3,310,24,1,1.48,1.48,200,0.6,3,2,0.8,0,23]
[4,11.9,310,24,50,1.83,1.31,200,0.6,4,89,0.8,0,23]
[4,13,310,24,60,2.11,1.24,200,0.6,4,91,0.8,0,23]
[4,14.2,310,24,70,2.38,1.17,200,0.6,4,94,0.8,0,23]
[4,15.4,310,24,80,2.65,1.1000000000000001,200,0.6,4,96,0.8,0,23]
[4,16.5,310,24,90,2.92,1.04,200,0.6,4,98,0.8,0,23]
[4,17.600000000000001,310,24,99,3.16,0.98,200,0.6,4,100,0.8,0,23]
[4,8.5,310,24,1,1.57,1.57,300,0.6,3,2,1.2,0,48]
[4,10,310,24,50,2.12,1.43,300,0.6,4,88,1.2,0,48]
[4,11,310,24,60,2.44,1.38,300,0.6,4,91,1.2,0,48]
[4,11.9,310,24,70,2.76,1.33,300,0.6,4,94,1.2,0,47]
[4,12.8,310,24,80,3.08,1.28,300,0.6,4,96,1.2,0,47]
[4,13.7,310,24,90,3.4,1.23,300,0.6,4,98,1.2,0,47]
[4,14.6,310,24,99,3.69,1.18,300,0.6,4,100,1.2,0,47]
[4,14.7,310,25,1,1.25,1.25,100,0.6,3,2,0.4,0,7]
[4,15,310,25,50,1.29,1.08,100,0.6,4,90,0.4,0,7]
[4,16.600000000000001,310,25,60,1.47,0.98,100,0.6,4,92,0.4,0,7]
[4,18.100000000000001,310,25,70,1.64,0.87,100,0.6,4,94,0.4,0,7]
[4,19.600000000000001,310,25,80,1.81,0.77,100,0.6,4,97,0.4,0,7]
[4,21,310,25,90,1.98,0.68,100,0.6,4,98,0.4,0,7]
[4,22.3,310,25,99,2.13,0.59,100,0.6,4,100,0.4,0,7]
[4,10.6,310,25,1,1.55,1.55,200,0.6,3,2,0.8,0,23]
[4,12.5,310,25,50,1.97,1.36,200,0.6,4,89,0.8,0,23]
[4,13.7,310,25,60,2.2599999999999998,1.29,200,0.6,4,91,0.8,0,23]
[4,14.9,310,25,70,2.5499999999999998,1.21,200,0.6,4,94,0.8,0,23]
[4,16.2,310,25,80,2.84,1.1399999999999999,200,0.6,4,96,0.8,0,23]
[4,17.399999999999999,310,25,90,3.12,1.07,200,0.6,4,98,0.8,0,23]
[4,18.5,310,25,99,3.37,1.01,200,0.6,4,100,0.8,0,23]
[4,8.6999999999999993,310,25,1,1.65,1.65,300,0.6,3,2,1.2,0,48]
[4,10.5,310,25,50,2.2799999999999998,1.49,300,0.6,4,88,1.2,0,48]
[4,11.5,310,25,60,2.62,1.44,300,0.6,4,91,1.2,0,48]
[4,12.5,310,25,70,2.96,1.38,300,0.6,4,94,1.2,0,47]
[4,13.4,310,25,80,3.3,1.33,300,0.6,4,96,1.2,0,47]
[4,14.4,310,25,90,3.64,1.27,300,0.6,4,98,1.2,0,47]
[4,15.3,310,25,99,3.95,1.22,300,0.6,4,100,1.2,0,47]
[4,15.2,310,26,1,1.31,1.31,100,0.6,3,2,0.4,0,7]
[4,15.8,310,26,50,1.38,1.1200000000000001,100,0.6,4,90,0.4,0,7]
[4,17.399999999999999,310,26,60,1.57,1.01,100,0.6,4,92,0.4,0,7]
[4,19,310,26,70,1.75,0.9,100,0.6,4,95,0.4,0,7]
[4,20.6,310,26,80,1.93,0.79,100,0.6,4,97,0.4,0,7]
[4,22,310,26,90,2.1,0.69,100,0.6,4,98,0.4,0,7]
[4,23.3,310,26,99,2.25,0.6,100,0.6,4,100,0.4,0,7]
[4,10.9,310,26,1,1.62,1.62,200,0.6,3,2,0.8,0,23]
[4,13.1,310,26,50,2.12,1.41,200,0.6,4,89,0.8,0,23]
[4,14.4,310,26,60,2.42,1.33,200,0.6,4,91,0.8,0,23]
[4,15.7,310,26,70,2.73,1.25,200,0.6,4,94,0.8,0,23]
[4,17,310,26,80,3.03,1.18,200,0.6,4,96,0.8,0,23]
[4,18.3,310,26,90,3.33,1.1000000000000001,200,0.6,4,98,0.8,0,23]
[4,19.399999999999999,310,26,99,3.59,1.04,200,0.6,4,100,0.8,0,23]
[4,8.9,310,26,1,1.73,1.73,300,0.6,3,2,1.2,0,48]
[4,11,310,26,50,2.4500000000000002,1.55,300,0.6,4,88,1.2,0,48]
[4,12,310,26,60,2.81,1.49,300,0.6,4,91,1.2,0,47]
[4,13.1,310,26,70,3.17,1.43,300,0.6,4,94,1.2,0,47]
[4,14.1,310,26,80,3.53,1.38,300,0.6,4,96,1.2,0,47]
[4,15.1,310,26,90,3.89,1.32,300,0.6,4,98,1.2,0,47]
[4,16.100000000000001,310,26,99,4.22,1.27,300,0.6,4,100,1.2,0,47]
[4,15.7,310,27,1,1.37,1.37,100,0.6,3,2,0.4,0,7]
[4,16.600000000000001,310,27,50,1.47,1.1499999999999999,100,0.6,4,90,0.4,0,7]
[4,18.3,310,27,60,1.67,1.03,100,0.6,4,92,0.4,0,7]
[4,20,310,27,70,1.86,0.92,100,0.6,4,95,0.4,0,7]
[4,21.6,310,27,80,2.04,0.81,100,0.6,4,97,0.4,0,7]
[4,23.1,310,27,90,2.2200000000000002,0.7,100,0.6,4,98,0.4,0,7]
[4,24.4,310,27,99,2.38,0.61,100,0.6,4,100,0.4,0,7]
[4,11.2,310,27,1,1.69,1.69,200,0.6,3,2,0.8,0,23]
[4,13.7,310,27,50,2.27,1.46,200,0.6,4,89,0.8,0,23]
[4,15.1,310,27,60,2.59,1.37,200,0.6,4,91,0.8,0,23]
[4,16.5,310,27,70,2.91,1.29,200,0.6,4,94,0.8,0,23]
[4,17.8,310,27,80,3.23,1.21,200,0.6,4,96,0.8,0,23]
[4,19.2,310,27,90,3.54,1.1299999999999999,200,0.6,4,98,0.8,0,23]
[4,20.399999999999999,310,27,99,3.82,1.06,200,0.6,4,100,0.8,0,23]
[4,9.1,310,27,1,1.8,1.8,300,0.6,3,3,1.2,0,48]
[4,11.5,310,27,50,2.62,1.61,300,0.6,4,88,1.2,0,48]
[4,12.6,310,27,60,3.01,1.54,300,0.6,4,91,1.2,0,47]
[4,13.7,310,27,70,3.39,1.48,300,0.6,4,94,1.2,0,47]
[4,14.8,310,27,80,3.77,1.42,300,0.6,4,96,1.2,0,47]
[4,15.9,310,27,90,4.1500000000000004,1.36,300,0.6,4,98,1.2,0,47]
[4,16.8,310,27,99,4.49,1.31,300,0.6,4,100,1.2,0,47]
[4,13.4,380,21,1,1.1000000000000001,1.1000000000000001,100,0.74,4,1,0.4,0,7]
[4,13.4,380,21,50,1.0900000000000001,1.0900000000000001,100,0.74,4,87,0.4,0,7]
[4,13.7,380,21,60,1.1299999999999999,0.94,100,0.74,6,90,0.4,0,7]
[4,15,380,21,70,1.28,0.84,100,0.74,6,93,0.4,0,7]
[4,16.2,380,21,80,1.42,0.73,100,0.74,6,96,0.4,0,7]
[4,17.5,380,21,90,1.57,0.63,100,0.74,6,98,0.4,0,7]
[4,18.5,380,21,99,1.69,0.54,100,0.74,6,100,0.4,0,7]
[4,10.1,380,21,1,1.42,1.42,200,0.74,4,2,0.8,0,23]
[4,10.6,380,21,50,1.55,1.29,200,0.74,6,87,0.8,0,23]
[4,11.7,380,21,60,1.8,1.22,200,0.74,6,90,0.8,0,23]
[4,12.8,380,21,70,2.04,1.1399999999999999,200,0.74,6,93,0.8,0,23]
[4,13.8,380,21,80,2.29,1.06,200,0.74,6,95,0.8,0,23]
[4,14.9,380,21,90,2.5299999999999998,0.99,200,0.74,6,98,0.8,0,23]
[4,15.8,380,21,99,2.75,0.92,200,0.74,6,100,0.8,0,23]
[4,8.4,380,21,1,1.53,1.53,300,0.74,4,2,1.2,0,48]
[4,9.1999999999999993,380,21,50,1.83,1.42,300,0.74,6,86,1.2,0,48]
[4,10.1,380,21,60,2.13,1.36,300,0.74,6,89,1.2,0,48]
[4,10.9,380,21,70,2.42,1.3,300,0.74,6,92,1.2,0,48]
[4,11.8,380,21,80,2.72,1.24,300,0.74,6,95,1.2,0,47]
[4,12.6,380,21,90,3.02,1.18,300,0.74,6,98,1.2,0,47]
[4,13.4,380,21,99,3.29,1.1299999999999999,300,0.74,6,100,1.2,0,47]
[4,14,380,22,1,1.1599999999999999,1.1599999999999999,100,0.74,4,1,0.4,0,7]
[4,13.9,380,22,50,1.1599999999999999,1.1599999999999999,100,0.74,4,90,0.4,0,7]
[4,14.5,380,22,60,1.22,0.98,100,0.74,6,90,0.4,0,7]
[4,15.8,380,22,70,1.38,0.87,100,0.74,6,93,0.4,0,7]
[4,17.2,380,22,80,1.53,0.76,100,0.74,6,96,0.4,0,7]
[4,18.399999999999999,380,22,90,1.68,0.65,100,0.74,6,98,0.4,0,7]
[4,19.600000000000001,380,22,99,1.81,0.56000000000000005,100,0.74,6,100,0.4,0,7]
[4,10.4,380,22,1,1.5,1.5,200,0.74,4,2,0.8,0,23]
[4,11.2,380,22,50,1.69,1.35,200,0.74,6,87,0.8,0,23]
[4,12.4,380,22,60,1.95,1.27,200,0.74,6,90,0.8,0,23]
[4,13.5,380,22,70,2.21,1.19,200,0.74,6,93,0.8,0,23]
[4,14.6,380,22,80,2.4700000000000002,1.1100000000000001,200,0.74,6,95,0.8,0,23]
[4,15.7,380,22,90,2.73,1.03,200,0.74,6,98,0.8,0,23]
[4,16.7,380,22,99,2.96,0.96,200,0.74,6,100,0.8,0,23]
[4,8.6,380,22,1,1.62,1.62,300,0.74,4,2,1.2,0,48]
[4,9.6999999999999993,380,22,50,2,1.49,300,0.74,6,86,1.2,0,48]
[4,10.6,380,22,60,2.31,1.42,300,0.74,6,89,1.2,0,48]
[4,11.5,380,22,70,2.63,1.36,300,0.74,6,92,1.2,0,48]
[4,12.4,380,22,80,2.94,1.3,300,0.74,6,95,1.2,0,47]
[4,13.3,380,22,90,3.26,1.24,300,0.74,6,98,1.2,0,47]
[4,14.1,380,22,99,3.54,1.18,300,0.74,6,100,1.2,0,47]
[4,14.5,380,23,1,1.23,1.23,100,0.74,4,1,0.4,0,7]
[4,14.5,380,23,50,1.22,1.22,100,0.74,4,93,0.4,0,7]
[4,15.3,380,23,60,1.32,1.01,100,0.74,6,91,0.4,0,7]
[4,16.7,380,23,70,1.48,0.89,100,0.74,6,93,0.4,0,7]
[4,18.100000000000001,380,23,80,1.64,0.78,100,0.74,6,96,0.4,0,7]
[4,19.399999999999999,380,23,90,1.8,0.67,100,0.74,6,98,0.4,0,7]
[4,20.6,380,23,99,1.93,0.56999999999999995,100,0.74,6,100,0.4,0,7]
[4,10.8,380,23,1,1.58,1.58,200,0.74,4,2,0.8,0,23]
[4,11.9,380,23,50,1.83,1.41,200,0.74,6,87,0.8,0,23]
[4,13.1,380,23,60,2.11,1.32,200,0.74,6,90,0.8,0,23]
[4,14.2,380,23,70,2.39,1.24,200,0.74,6,93,0.8,0,23]
[4,15.4,380,23,80,2.66,1.1499999999999999,200,0.74,6,95,0.8,0,23]
[4,16.600000000000001,380,23,90,2.93,1.07,200,0.74,6,98,0.8,0,23]
[4,17.600000000000001,380,23,99,3.17,0.99,200,0.74,6,100,0.8,0,23]
[4,8.9,380,23,1,1.71,1.71,300,0.74,4,2,1.2,0,48]
[4,10.199999999999999,380,23,50,2.17,1.55,300,0.74,6,86,1.2,0,48]
[4,11.2,380,23,60,2.5,1.49,300,0.74,6,89,1.2,0,48]
[4,12.1,380,23,70,2.84,1.42,300,0.74,6,92,1.2,0,47]
[4,13.1,380,23,80,3.17,1.35,300,0.74,6,95,1.2,0,47]
[4,14,380,23,90,3.51,1.29,300,0.74,6,98,1.2,0,47]
[4,14.9,380,23,99,3.8,1.23,300,0.74,6,100,1.2,0,47]
[4,15.1,380,24,1,1.29,1.29,100,0.74,4,1,0.4,0,7]
[4,14.6,380,24,50,1.24,1.17,100,0.74,6,87,0.4,0,7]
[4,16.2,380,24,60,1.42,1.04,100,0.74,6,91,0.4,0,7]
[4,17.600000000000001,380,24,70,1.59,0.92,100,0.74,6,93,0.4,0,7]
[4,19.100000000000001,380,24,80,1.75,0.8,100,0.74,6,96,0.4,0,7]
[4,20.5,380,24,90,1.92,0.69,100,0.74,6,98,0.4,0,7]
[4,21.7,380,24,99,2.06,0.59,100,0.74,6,100,0.4,0,7]
[4,11.1,380,24,1,1.66,1.66,200,0.74,4,2,0.8,0,23]
[4,12.5,380,24,50,1.98,1.46,200,0.74,6,87,0.8,0,23]
[4,13.8,380,24,60,2.27,1.37,200,0.74,6,90,0.8,0,23]
[4,15,380,24,70,2.57,1.28,200,0.74,6,93,0.8,0,23]
[4,16.2,380,24,80,2.85,1.19,200,0.74,6,95,0.8,0,23]
[4,17.5,380,24,90,3.14,1.1000000000000001,200,0.74,6,98,0.8,0,23]
[4,18.600000000000001,380,24,99,3.39,1.02,200,0.74,6,100,0.8,0,23]
[4,9.1,380,24,1,1.8,1.8,300,0.74,4,2,1.2,0,48]
[4,10.7,380,24,50,2.35,1.62,300,0.74,6,86,1.2,0,48]
[4,11.7,380,24,60,2.7,1.55,300,0.74,6,89,1.2,0,47]
[4,12.7,380,24,70,3.06,1.48,300,0.74,6,92,1.2,0,47]
[4,13.7,380,24,80,3.41,1.41,300,0.74,6,95,1.2,0,47]
[4,14.8,380,24,90,3.76,1.33,300,0.74,6,98,1.2,0,47]
[4,15.7,380,24,99,4.08,1.27,300,0.74,6,100,1.2,0,47]
[4,15.7,380,25,1,1.36,1.36,100,0.74,4,1,0.4,0,7]
[4,15.4,380,25,50,1.33,1.2,100,0.74,6,88,0.4,0,7]
[4,17,380,25,60,1.52,1.07,100,0.74,6,91,0.4,0,7]
[4,18.600000000000001,380,25,70,1.7,0.95,100,0.74,6,93,0.4,0,7]
[4,20.100000000000001,380,25,80,1.87,0.82,100,0.74,6,96,0.4,0,7]
[4,21.5,380,25,90,2.0299999999999998,0.7,100,0.74,6,98,0.4,0,7]
[4,22.7,380,25,99,2.1800000000000002,0.6,100,0.74,6,100,0.4,0,7]
[4,11.5,380,25,1,1.74,1.74,200,0.74,4,2,0.8,0,23]
[4,13.1,380,25,50,2.13,1.51,200,0.74,6,87,0.8,0,23]
[4,14.5,380,25,60,2.44,1.42,200,0.74,6,90,0.8,0,23]
[4,15.8,380,25,70,2.75,1.32,200,0.74,6,93,0.8,0,23]
[4,17.100000000000001,380,25,80,3.05,1.23,200,0.74,6,95,0.8,0,23]
[4,18.399999999999999,380,25,90,3.35,1.1299999999999999,200,0.74,6,98,0.8,0,23]
[4,19.5,380,25,99,3.61,1.05,200,0.74,6,100,0.8,0,23]
[4,9.4,380,25,1,1.89,1.89,300,0.74,4,2,1.2,0,48]
[4,11.2,380,25,50,2.5299999999999998,1.68,300,0.74,6,86,1.2,0,48]
[4,12.3,380,25,60,2.9,1.61,300,0.74,6,89,1.2,0,47]
[4,13.4,380,25,70,3.28,1.53,300,0.74,6,92,1.2,0,47]
[4,14.4,380,25,80,3.66,1.46,300,0.74,6,95,1.2,0,47]
[4,15.5,380,25,90,4.03,1.38,300,0.74,6,98,1.2,0,47]
[4,16.5,380,25,99,4.3600000000000003,1.31,300,0.74,6,100,1.2,0,47]
[4,16.2,380,26,1,1.42,1.42,100,0.74,4,1,0.4,0,7]
[4,16.2,380,26,50,1.43,1.24,100,0.74,6,88,0.4,0,7]
[4,17.899999999999999,380,26,60,1.62,1.1000000000000001,100,0.74,6,91,0.4,0,7]
[4,19.5,380,26,70,1.81,0.97,100,0.74,6,93,0.4,0,7]
[4,21,380,26,80,1.98,0.84,100,0.74,6,96,0.4,0,7]
[4,22.5,380,26,90,2.16,0.71,100,0.74,6,98,0.4,0,7]
[4,23.8,380,26,99,2.31,0.61,100,0.74,6,100,0.4,0,7]
[4,11.8,380,26,1,1.83,1.83,200,0.74,4,2,0.8,0,23]
[4,13.8,380,26,50,2.29,1.57,200,0.74,6,87,0.8,0,23]
[4,15.2,380,26,60,2.61,1.46,200,0.74,6,90,0.8,0,23]
[4,16.600000000000001,380,26,70,2.94,1.36,200,0.74,6,93,0.8,0,23]
[4,18,380,26,80,3.26,1.27,200,0.74,6,95,0.8,0,23]
[4,19.3,380,26,90,3.57,1.17,200,0.74,6,98,0.8,0,23]
[4,20.5,380,26,99,3.85,1.08,200,0.74,6,100,0.8,0,23]
[4,9.6,380,26,1,1.97,1.97,300,0.74,4,2,1.2,0,48]
[4,11.8,380,26,50,2.72,1.75,300,0.74,6,86,1.2,0,47]
[4,12.9,380,26,60,3.11,1.66,300,0.74,6,89,1.2,0,47]
[4,14,380,26,70,3.51,1.59,300,0.74,6,92,1.2,0,47]
[4,15.2,380,26,80,3.91,1.51,300,0.74,6,95,1.2,0,47]
[4,16.3,380,26,90,4.3,1.43,300,0.74,6,98,1.2,0,47]
[4,17.3,380,26,99,4.6500000000000004,1.36,300,0.74,6,100,1.2,0,47]
[4,16.8,380,27,1,1.49,1.49,100,0.74,4,2,0.4,0,7]
[4,17,380,27,50,1.52,1.27,100,0.74,6,88,0.4,0,7]
[4,18.8,380,27,60,1.72,1.1299999999999999,100,0.74,6,91,0.4,0,7]
[4,20.399999999999999,380,27,70,1.91,0.99,100,0.74,6,93,0.4,0,7]
[4,22,380,27,80,2.1,0.86,100,0.74,6,96,0.4,0,7]
[4,23.6,380,27,90,2.2799999999999998,0.73,100,0.74,6,98,0.4,0,7]
[4,24.9,380,27,99,2.4300000000000002,0.61,100,0.74,6,100,0.4,0,7]
[4,12.2,380,27,1,1.91,1.91,200,0.74,4,2,0.8,0,23]
[4,14.5,380,27,50,2.4500000000000002,1.62,200,0.74,6,87,0.8,0,23]
[4,16,380,27,60,2.79,1.51,200,0.74,6,90,0.8,0,23]
[4,17.399999999999999,380,27,70,3.13,1.41,200,0.74,6,93,0.8,0,23]
[4,18.899999999999999,380,27,80,3.46,1.3,200,0.74,6,95,0.8,0,23]
[4,20.3,380,27,90,3.79,1.2,200,0.74,6,98,0.8,0,23]
[4,21.5,380,27,99,4.08,1.1000000000000001,200,0.74,6,100,0.8,0,23]
[4,9.9,380,27,1,2.06,2.06,300,0.74,4,2,1.2,0,48]
[4,12.3,380,27,50,2.91,1.81,300,0.74,6,86,1.2,0,47]
[4,13.5,380,27,60,3.33,1.72,300,0.74,6,89,1.2,0,47]
[4,14.7,380,27,70,3.75,1.64,300,0.74,6,92,1.2,0,47]
[4,15.9,380,27,80,4.17,1.55,300,0.74,6,95,1.2,0,47]
[4,17.100000000000001,380,27,90,4.58,1.47,300,0.74,6,98,1.2,0,47]
[4,18.2,380,27,99,4.96,1.4,300,0.74,6,100,1.2,0,47]
[5,9.1,100,21,1,0.48,0.48,100,0.19,0,2,0.4,0,7]
[5,9.8000000000000007,100,21,50,0.56000000000000005,0.44,100,0.19,1,98,0.4,0,7]
[5,10.7,100,21,60,0.66,0.43,100,0.19,1,98,0.4,0,7]
[5,11.5,100,21,70,0.76,0.42,100,0.19,1,99,0.4,0,7]
[5,12.4,100,21,80,0.86,0.4,100,0.19,1,99,0.4,0,7]
[5,13.3,100,21,90,0.96,0.39,100,0.19,1,100,0.4,0,7]
[5,14,100,21,99,1.05,0.38,100,0.19,1,100,0.4,0,7]
[5,7.2,100,21,1,0.51,0.51,200,0.19,0,2,0.8,0,24]
[5,7.8,100,21,50,0.66,0.49,200,0.19,1,98,0.8,0,24]
[5,8.3000000000000007,100,21,60,0.77,0.48,200,0.19,1,98,0.8,0,24]
[5,8.8000000000000007,100,21,70,0.89,0.48,200,0.19,1,99,0.8,0,23]
[5,9.3000000000000007,100,21,80,1.01,0.47,200,0.19,1,99,0.8,0,23]
[5,9.8000000000000007,100,21,90,1.1299999999999999,0.47,200,0.19,1,100,0.8,0,23]
[5,10.3,100,21,99,1.23,0.46,200,0.19,1,100,0.8,0,23]
[5,6.5,100,21,1,0.51,0.51,300,0.19,0,3,1.2,0,48]
[5,6.9,100,21,50,0.68,0.5,300,0.19,1,98,1.2,0,48]
[5,7.3,100,21,60,0.8,0.5,300,0.19,1,98,1.2,0,48]
[5,7.6,100,21,70,0.92,0.49,300,0.19,1,99,1.2,0,48]
[5,8,100,21,80,1.05,0.49,300,0.19,1,99,1.2,0,48]
[5,8.3000000000000007,100,21,90,1.17,0.48,300,0.19,1,100,1.2,0,48]
[5,8.6,100,21,99,1.28,0.48,300,0.19,1,100,1.2,0,48]
[5,9.4,100,22,1,0.51,0.51,100,0.19,0,2,0.4,0,7]
[5,10.3,100,22,50,0.62,0.47,100,0.19,1,98,0.4,0,7]
[5,11.2,100,22,60,0.72,0.45,100,0.19,1,98,0.4,0,7]
[5,12.1,100,22,70,0.83,0.44,100,0.19,1,99,0.4,0,7]
[5,13,100,22,80,0.94,0.42,100,0.19,1,99,0.4,0,7]
[5,14,100,22,90,1.05,0.41,100,0.19,1,100,0.4,0,7]
[5,14.8,100,22,99,1.1399999999999999,0.4,100,0.19,1,100,0.4,0,7]
[5,7.3,100,22,1,0.54,0.54,200,0.19,0,3,0.8,0,24]
[5,8.1,100,22,50,0.72,0.52,200,0.19,1,98,0.8,0,24]
[5,8.6,100,22,60,0.85,0.51,200,0.19,1,98,0.8,0,24]
[5,9.1999999999999993,100,22,70,0.97,0.5,200,0.19,1,99,0.8,0,23]
[5,9.6999999999999993,100,22,80,1.1000000000000001,0.5,200,0.19,1,99,0.8,0,23]
[5,10.199999999999999,100,22,90,1.22,0.49,200,0.19,1,100,0.8,0,23]
[5,10.7,100,22,99,1.33,0.49,200,0.19,1,100,0.8,0,23]
[5,6.6,100,22,1,0.54,0.54,300,0.19,0,3,1.2,0,48]
[5,7.1,100,22,50,0.75,0.53,300,0.19,1,98,1.2,0,48]
[5,7.5,100,22,60,0.88,0.53,300,0.19,1,98,1.2,0,48]
[5,7.9,100,22,70,1.01,0.52,300,0.19,1,99,1.2,0,48]
[5,8.1999999999999993,100,22,80,1.1299999999999999,0.52,300,0.19,1,99,1.2,0,48]
[5,8.6,100,22,90,1.26,0.51,300,0.19,1,100,1.2,0,48]
[5,8.9,100,22,99,1.38,0.51,300,0.19,1,100,1.2,0,48]
[5,9.6,100,23,1,0.54,0.54,100,0.19,0,2,0.4,0,7]
[5,10.8,100,23,50,0.68,0.49,100,0.19,1,98,0.4,0,7]
[5,11.8,100,23,60,0.79,0.48,100,0.19,1,98,0.4,0,7]
[5,12.7,100,23,70,0.9,0.46,100,0.19,1,99,0.4,0,7]
[5,13.7,100,23,80,1.02,0.45,100,0.19,1,99,0.4,0,7]
[5,14.7,100,23,90,1.1299999999999999,0.43,100,0.19,1,100,0.4,0,7]
[5,15.6,100,23,99,1.23,0.42,100,0.19,1,100,0.4,0,7]
[5,7.4,100,23,1,0.56999999999999995,0.56999999999999995,200,0.19,0,3,0.8,0,24]
[5,8.4,100,23,50,0.79,0.54,200,0.19,1,98,0.8,0,24]
[5,9,100,23,60,0.92,0.54,200,0.19,1,98,0.8,0,23]
[5,9.5,100,23,70,1.05,0.53,200,0.19,1,99,0.8,0,23]
[5,10.1,100,23,80,1.19,0.52,200,0.19,1,99,0.8,0,23]
[5,10.7,100,23,90,1.32,0.52,200,0.19,1,100,0.8,0,23]
[5,11.2,100,23,99,1.44,0.51,200,0.19,1,100,0.8,0,23]
[5,6.6,100,23,1,0.56999999999999995,0.56999999999999995,300,0.19,0,3,1.2,0,48]
[5,7.3,100,23,50,0.82,0.56000000000000005,300,0.19,1,98,1.2,0,48]
[5,7.7,100,23,60,0.95,0.55000000000000004,300,0.19,1,98,1.2,0,48]
[5,8.1,100,23,70,1.0900000000000001,0.55000000000000004,300,0.19,1,99,1.2,0,48]
[5,8.5,100,23,80,1.23,0.54,300,0.19,1,99,1.2,0,48]
[5,8.9,100,23,90,1.36,0.54,300,0.19,1,100,1.2,0,48]
[5,9.3000000000000007,100,23,99,1.49,0.54,300,0.19,1,100,1.2,0,48]
[5,9.9,100,24,1,0.56999999999999995,0.56999999999999995,100,0.19,0,3,0.4,0,7]
[5,11.3,100,24,50,0.74,0.51,100,0.19,1,98,0.4,0,7]
[5,12.3,100,24,60,0.86,0.5,100,0.19,1,98,0.4,0,7]
[5,13.4,100,24,70,0.98,0.48,100,0.19,1,99,0.4,0,7]
[5,14.4,100,24,80,1.1000000000000001,0.47,100,0.19,1,99,0.4,0,7]
[5,15.4,100,24,90,1.22,0.45,100,0.19,1,100,0.4,0,7]
[5,16.399999999999999,100,24,99,1.32,0.44,100,0.19,1,100,0.4,0,7]
[5,7.6,100,24,1,0.6,0.6,200,0.19,0,3,0.8,0,24]
[5,8.6999999999999993,100,24,50,0.86,0.56999999999999995,200,0.19,1,98,0.8,0,24]
[5,9.3000000000000007,100,24,60,1,0.56000000000000005,200,0.19,1,98,0.8,0,23]
[5,9.9,100,24,70,1.1399999999999999,0.56000000000000005,200,0.19,1,99,0.8,0,23]
[5,10.5,100,24,80,1.28,0.55000000000000004,200,0.19,1,99,0.8,0,23]
[5,11.1,100,24,90,1.42,0.54,200,0.19,1,100,0.8,0,23]
[5,11.6,100,24,99,1.55,0.54,200,0.19,1,100,0.8,0,23]
[5,6.7,100,24,1,0.6,0.6,300,0.19,0,3,1.2,0,48]
[5,7.5,100,24,50,0.89,0.59,300,0.19,1,98,1.2,0,48]
[5,8,100,24,60,1.03,0.57999999999999996,300,0.19,1,98,1.2,0,48]
[5,8.4,100,24,70,1.18,0.57999999999999996,300,0.19,1,99,1.2,0,48]
[5,8.8000000000000007,100,24,80,1.32,0.56999999999999995,300,0.19,1,99,1.2,0,48]
[5,9.1999999999999993,100,24,90,1.47,0.56999999999999995,300,0.19,1,100,1.2,0,48]
[5,9.6,100,24,99,1.6,0.56000000000000005,300,0.19,1,100,1.2,0,48]
[5,10.1,100,25,1,0.59,0.59,100,0.19,0,3,0.4,0,7]
[5,11.8,100,25,50,0.8,0.54,100,0.19,1,98,0.4,0,7]
[5,12.9,100,25,60,0.92,0.52,100,0.19,1,98,0.4,0,7]
[5,14,100,25,70,1.05,0.5,100,0.19,1,99,0.4,0,7]
[5,15.1,100,25,80,1.18,0.49,100,0.19,1,99,0.4,0,7]
[5,16.2,100,25,90,1.31,0.47,100,0.19,1,100,0.4,0,7]
[5,17.2,100,25,99,1.42,0.45,100,0.19,1,100,0.4,0,7]
[5,7.7,100,25,1,0.63,0.63,200,0.19,0,3,0.8,0,24]
[5,9,100,25,50,0.93,0.6,200,0.19,1,98,0.8,0,23]
[5,9.6,100,25,60,1.08,0.59,200,0.19,1,98,0.8,0,23]
[5,10.3,100,25,70,1.23,0.57999999999999996,200,0.19,1,99,0.8,0,23]
[5,10.9,100,25,80,1.38,0.57999999999999996,200,0.19,1,99,0.8,0,23]
[5,11.5,100,25,90,1.53,0.56999999999999995,200,0.19,1,100,0.8,0,23]
[5,12.1,100,25,99,1.66,0.56000000000000005,200,0.19,1,100,0.8,0,23]
[5,6.8,100,25,1,0.63,0.63,300,0.19,0,3,1.2,0,48]
[5,7.7,100,25,50,0.96,0.61,300,0.19,1,98,1.2,0,48]
[5,8.1999999999999993,100,25,60,1.1100000000000001,0.61,300,0.19,1,98,1.2,0,48]
[5,8.6,100,25,70,1.27,0.6,300,0.19,1,99,1.2,0,48]
[5,9.1,100,25,80,1.42,0.6,300,0.19,1,99,1.2,0,48]
[5,9.5,100,25,90,1.58,0.59,300,0.19,1,100,1.2,0,48]
[5,9.9,100,25,99,1.71,0.59,300,0.19,1,100,1.2,0,48]
[5,10.3,100,26,1,0.62,0.62,100,0.19,0,3,0.4,0,7]
[5,12.4,100,26,50,0.86,0.56000000000000005,100,0.19,1,98,0.4,0,7]
[5,13.5,100,26,60,0.99,0.54,100,0.19,1,98,0.4,0,7]
[5,14.7,100,26,70,1.1299999999999999,0.52,100,0.19,1,99,0.4,0,7]
[5,15.8,100,26,80,1.26,0.51,100,0.19,1,99,0.4,0,7]
[5,17,100,26,90,1.4,0.49,100,0.19,1,100,0.4,0,7]
[5,18,100,26,99,1.52,0.47,100,0.19,1,100,0.4,0,7]
[5,7.8,100,26,1,0.66,0.66,200,0.19,0,3,0.8,0,24]
[5,9.3000000000000007,100,26,50,1,0.63,200,0.19,1,98,0.8,0,23]
[5,10,100,26,60,1.1599999999999999,0.62,200,0.19,1,98,0.8,0,23]
[5,10.6,100,26,70,1.32,0.61,200,0.19,1,99,0.8,0,23]
[5,11.3,100,26,80,1.48,0.6,200,0.19,1,99,0.8,0,23]
[5,12,100,26,90,1.63,0.59,200,0.19,1,100,0.8,0,23]
[5,12.6,100,26,99,1.78,0.59,200,0.19,1,100,0.8,0,23]
[5,6.9,100,26,1,0.66,0.66,300,0.19,0,3,1.2,0,48]
[5,8,100,26,50,1.04,0.64,300,0.19,1,98,1.2,0,48]
[5,8.4,100,26,60,1.2,0.64,300,0.19,1,98,1.2,0,48]
[5,8.9,100,26,70,1.36,0.63,300,0.19,1,99,1.2,0,48]
[5,9.4,100,26,80,1.52,0.62,300,0.19,1,99,1.2,0,48]
[5,9.8000000000000007,100,26,90,1.69,0.62,300,0.19,1,100,1.2,0,48]
[5,10.199999999999999,100,26,99,1.84,0.61,300,0.19,1,100,1.2,0,48]
[5,10.6,100,27,1,0.65,0.65,100,0.19,0,3,0.4,0,7]
[5,12.9,100,27,50,0.92,0.57999999999999996,100,0.19,1,98,0.4,0,7]
[5,14.2,100,27,60,1.07,0.56000000000000005,100,0.19,1,98,0.4,0,7]
[5,15.4,100,27,70,1.21,0.54,100,0.19,1,99,0.4,0,7]
[5,16.600000000000001,100,27,80,1.35,0.52,100,0.19,1,99,0.4,0,7]
[5,17.8,100,27,90,1.49,0.51,100,0.19,1,100,0.4,0,7]
[5,18.899999999999999,100,27,99,1.62,0.49,100,0.19,1,100,0.4,0,7]
[5,7.9,100,27,1,0.69,0.69,200,0.19,0,3,0.8,0,24]
[5,9.6,100,27,50,1.08,0.65,200,0.19,1,98,0.8,0,23]
[5,10.3,100,27,60,1.24,0.64,200,0.19,1,98,0.8,0,23]
[5,11.1,100,27,70,1.41,0.63,200,0.19,1,99,0.8,0,23]
[5,11.8,100,27,80,1.58,0.63,200,0.19,1,99,0.8,0,23]
[5,12.5,100,27,90,1.75,0.62,200,0.19,1,100,0.8,0,23]
[5,13.1,100,27,99,1.9,0.61,200,0.19,1,100,0.8,0,23]
[5,7,100,27,1,0.69,0.69,300,0.19,0,3,1.2,0,48]
[5,8.1999999999999993,100,27,50,1.1100000000000001,0.67,300,0.19,1,98,1.2,0,48]
[5,8.6999999999999993,100,27,60,1.28,0.66,300,0.19,1,98,1.2,0,48]
[5,9.1999999999999993,100,27,70,1.46,0.66,300,0.19,1,99,1.2,0,48]
[5,9.6999999999999993,100,27,80,1.63,0.65,300,0.19,1,99,1.2,0,48]
[5,10.199999999999999,100,27,90,1.8,0.64,300,0.19,1,100,1.2,0,48]
[5,10.6,100,27,99,1.96,0.64,300,0.19,1,100,1.2,0,47]
[5,11,170,21,1,0.7,0.7,100,0.33,1,2,0.4,0,7]
[5,11.2,170,21,50,0.72,0.63,100,0.33,1,95,0.4,0,7]
[5,12.3,170,21,60,0.85,0.6,100,0.33,1,96,0.4,0,7]
[5,13.4,170,21,70,0.97,0.56000000000000005,100,0.33,1,97,0.4,0,7]
[5,14.4,170,21,80,1.1000000000000001,0.52,100,0.33,1,98,0.4,0,7]
[5,15.5,170,21,90,1.22,0.49,100,0.33,1,99,0.4,0,7]
[5,16.5,170,21,99,1.34,0.45,100,0.33,1,100,0.4,0,7]
[5,8.4,170,21,1,0.79,0.79,200,0.33,1,2,0.8,0,24]
[5,9.1,170,21,50,0.96,0.74,200,0.33,1,95,0.8,0,23]
[5,9.8000000000000007,170,21,60,1.1299999999999999,0.72,200,0.33,1,96,0.8,0,23]
[5,10.6,170,21,70,1.3,0.7,200,0.33,1,97,0.8,0,23]
[5,11.3,170,21,80,1.47,0.68,200,0.33,1,98,0.8,0,23]
[5,12,170,21,90,1.64,0.66,200,0.33,1,99,0.8,0,23]
[5,12.7,170,21,99,1.79,0.64,200,0.33,1,100,0.8,0,23]
[5,7.3,170,21,1,0.81,0.81,300,0.33,1,2,1.2,0,48]
[5,8,170,21,50,1.03,0.78,300,0.33,1,94,1.2,0,48]
[5,8.5,170,21,60,1.22,0.76,300,0.33,1,96,1.2,0,48]
[5,9,170,21,70,1.41,0.75,300,0.33,1,97,1.2,0,48]
[5,9.5,170,21,80,1.59,0.74,300,0.33,1,98,1.2,0,48]
[5,10.1,170,21,90,1.78,0.72,300,0.33,1,99,1.2,0,48]
[5,10.6,170,21,99,1.94,0.71,300,0.33,1,100,1.2,0,48]
[5,11.3,170,22,1,0.74,0.74,100,0.33,1,2,0.4,0,7]
[5,11.8,170,22,50,0.79,0.66,100,0.33,1,95,0.4,0,7]
[5,13,170,22,60,0.93,0.62,100,0.33,1,96,0.4,0,7]
[5,14.1,170,22,70,1.06,0.57999999999999996,100,0.33,1,97,0.4,0,7]
[5,15.2,170,22,80,1.19,0.55000000000000004,100,0.33,1,98,0.4,0,7]
[5,16.399999999999999,170,22,90,1.33,0.51,100,0.33,1,99,0.4,0,7]
[5,17.399999999999999,170,22,99,1.44,0.47,100,0.33,1,100,0.4,0,7]
[5,8.6,170,22,1,0.83,0.83,200,0.33,1,2,0.8,0,24]
[5,9.5,170,22,50,1.05,0.78,200,0.33,1,95,0.8,0,23]
[5,10.3,170,22,60,1.23,0.76,200,0.33,1,96,0.8,0,23]
[5,11.1,170,22,70,1.42,0.74,200,0.33,1,97,0.8,0,23]
[5,11.8,170,22,80,1.6,0.72,200,0.33,1,98,0.8,0,23]
[5,12.6,170,22,90,1.78,0.7,200,0.33,1,99,0.8,0,23]
[5,13.3,170,22,99,1.94,0.68,200,0.33,1,100,0.8,0,23]
[5,7.5,170,22,1,0.86,0.86,300,0.33,1,2,1.2,0,48]
[5,8.3000000000000007,170,22,50,1.1399999999999999,0.82,300,0.33,1,94,1.2,0,48]
[5,8.8000000000000007,170,22,60,1.33,0.81,300,0.33,1,96,1.2,0,48]
[5,9.4,170,22,70,1.53,0.79,300,0.33,1,97,1.2,0,48]
[5,9.9,170,22,80,1.73,0.78,300,0.33,1,98,1.2,0,48]
[5,10.5,170,22,90,1.92,0.76,300,0.33,1,99,1.2,0,48]
[5,11,170,22,99,2.1,0.75,300,0.33,1,100,1.2,0,47]
[5,11.7,170,23,1,0.78,0.78,100,0.33,1,2,0.4,0,7]
[5,12.4,170,23,50,0.87,0.69,100,0.33,1,95,0.4,0,7]
[5,13.7,170,23,60,1.01,0.65,100,0.33,1,96,0.4,0,7]
[5,14.9,170,23,70,1.1499999999999999,0.61,100,0.33,1,97,0.4,0,7]
[5,16.100000000000001,170,23,80,1.29,0.56999999999999995,100,0.33,1,98,0.4,0,7]
[5,17.3,170,23,90,1.43,0.53,100,0.33,1,99,0.4,0,7]
[5,18.3,170,23,99,1.55,0.49,100,0.33,1,100,0.4,0,7]
[5,8.8000000000000007,170,23,1,0.88,0.88,200,0.33,1,2,0.8,0,23]
[5,9.9,170,23,50,1.1499999999999999,0.82,200,0.33,1,95,0.8,0,23]
[5,10.8,170,23,60,1.34,0.8,200,0.33,1,96,0.8,0,23]
[5,11.6,170,23,70,1.54,0.77,200,0.33,1,97,0.8,0,23]
[5,12.4,170,23,80,1.73,0.75,200,0.33,1,98,0.8,0,23]
[5,13.2,170,23,90,1.92,0.73,200,0.33,1,99,0.8,0,23]
[5,14,170,23,99,2.09,0.71,200,0.33,1,100,0.8,0,23]
[5,7.6,170,23,1,0.91,0.91,300,0.33,1,2,1.2,0,48]
[5,8.6,170,23,50,1.24,0.86,300,0.33,1,94,1.2,0,48]
[5,9.1999999999999993,170,23,60,1.45,0.85,300,0.33,1,96,1.2,0,48]
[5,9.6999999999999993,170,23,70,1.66,0.83,300,0.33,1,97,1.2,0,48]
[5,10.3,170,23,80,1.87,0.82,300,0.33,1,98,1.2,0,48]
[5,10.9,170,23,90,2.08,0.8,300,0.33,1,99,1.2,0,47]
[5,11.5,170,23,99,2.27,0.79,300,0.33,1,100,1.2,0,47]
[5,12.1,170,24,1,0.82,0.82,100,0.33,1,2,0.4,0,7]
[5,13.1,170,24,50,0.94,0.72,100,0.33,1,95,0.4,0,7]
[5,14.4,170,24,60,1.0900000000000001,0.68,100,0.33,1,96,0.4,0,7]
[5,15.7,170,24,70,1.24,0.63,100,0.33,1,97,0.4,0,7]
[5,16.899999999999999,170,24,80,1.39,0.59,100,0.33,1,98,0.4,0,7]
[5,18.2,170,24,90,1.54,0.55000000000000004,100,0.33,1,99,0.4,0,7]
[5,19.3,170,24,99,1.66,0.51,100,0.33,1,100,0.4,0,7]
[5,9,170,24,1,0.93,0.93,200,0.33,1,2,0.8,0,23]
[5,10.4,170,24,50,1.25,0.86,200,0.33,1,94,0.8,0,23]
[5,11.2,170,24,60,1.46,0.83,200,0.33,1,96,0.8,0,23]
[5,12.1,170,24,70,1.66,0.81,200,0.33,1,97,0.8,0,23]
[5,13,170,24,80,1.86,0.79,200,0.33,1,98,0.8,0,23]
[5,13.9,170,24,90,2.0699999999999998,0.76,200,0.33,1,99,0.8,0,23]
[5,14.7,170,24,99,2.25,0.74,200,0.33,1,100,0.8,0,23]
[5,7.7,170,24,1,0.96,0.96,300,0.33,1,3,1.2,0,48]
[5,8.9,170,24,50,1.35,0.91,300,0.33,1,94,1.2,0,48]
[5,9.5,170,24,60,1.57,0.89,300,0.33,1,96,1.2,0,48]
[5,10.1,170,24,70,1.8,0.87,300,0.33,1,97,1.2,0,48]
[5,10.8,170,24,80,2.02,0.86,300,0.33,1,98,1.2,0,47]
[5,11.4,170,24,90,2.2400000000000002,0.84,300,0.33,1,99,1.2,0,47]
[5,12,170,24,99,2.44,0.82,300,0.33,1,100,1.2,0,47]
[5,12.4,170,25,1,0.87,0.87,100,0.33,1,2,0.4,0,7]
[5,13.7,170,25,50,1.02,0.75,100,0.33,1,95,0.4,0,7]
[5,15.1,170,25,60,1.18,0.7,100,0.33,1,96,0.4,0,7]
[5,16.5,170,25,70,1.34,0.66,100,0.33,1,97,0.4,0,7]
[5,17.8,170,25,80,1.49,0.61,100,0.33,1,98,0.4,0,7]
[5,19.100000000000001,170,25,90,1.64,0.56999999999999995,100,0.33,1,99,0.4,0,7]
[5,20.3,170,25,99,1.78,0.53,100,0.33,1,100,0.4,0,7]
[5,9.1999999999999993,170,25,1,0.97,0.97,200,0.33,1,3,0.8,0,23]
[5,10.8,170,25,50,1.36,0.9,200,0.33,1,94,0.8,0,23]
[5,11.7,170,25,60,1.57,0.87,200,0.33,1,96,0.8,0,23]
[5,12.7,170,25,70,1.79,0.85,200,0.33,1,97,0.8,0,23]
[5,13.6,170,25,80,2,0.82,200,0.33,1,98,0.8,0,23]
[5,14.5,170,25,90,2.2200000000000002,0.8,200,0.33,1,99,0.8,0,23]
[5,15.4,170,25,99,2.41,0.77,200,0.33,1,100,0.8,0,23]
[5,7.9,170,25,1,1,1,300,0.33,1,3,1.2,0,48]
[5,9.1999999999999993,170,25,50,1.47,0.95,300,0.33,1,94,1.2,0,48]
[5,9.9,170,25,60,1.7,0.93,300,0.33,1,96,1.2,0,48]
[5,10.5,170,25,70,1.93,0.91,300,0.33,1,97,1.2,0,48]
[5,11.2,170,25,80,2.17,0.89,300,0.33,1,98,1.2,0,47]
[5,11.9,170,25,90,2.4,0.88,300,0.33,1,99,1.2,0,47]
[5,12.5,170,25,99,2.61,0.86,300,0.33,1,100,1.2,0,47]
[5,12.8,170,26,1,0.91,0.91,100,0.33,1,2,0.4,0,7]
[5,14.4,170,26,50,1.1000000000000001,0.78,100,0.33,1,95,0.4,0,7]
[5,15.9,170,26,60,1.27,0.73,100,0.33,1,96,0.4,0,7]
[5,17.3,170,26,70,1.43,0.68,100,0.33,1,97,0.4,0,7]
[5,18.7,170,26,80,1.59,0.63,100,0.33,1,98,0.4,0,7]
[5,20.100000000000001,170,26,90,1.76,0.59,100,0.33,1,99,0.4,0,7]
[5,21.3,170,26,99,1.9,0.54,100,0.33,1,100,0.4,0,7]
[5,9.4,170,26,1,1.02,1.02,200,0.33,1,3,0.8,0,23]
[5,11.3,170,26,50,1.46,0.93,200,0.33,1,94,0.8,0,23]
[5,12.3,170,26,60,1.69,0.91,200,0.33,1,96,0.8,0,23]
[5,13.2,170,26,70,1.92,0.88,200,0.33,1,97,0.8,0,23]
[5,14.2,170,26,80,2.15,0.85,200,0.33,1,98,0.8,0,23]
[5,15.2,170,26,90,2.38,0.83,200,0.33,1,99,0.8,0,23]
[5,16.100000000000001,170,26,99,2.58,0.8,200,0.33,1,100,0.8,0,23]
[5,8,170,26,1,1.05,1.05,300,0.33,1,3,1.2,0,48]
[5,9.5,170,26,50,1.58,0.99,300,0.33,1,94,1.2,0,48]
[5,10.199999999999999,170,26,60,1.83,0.97,300,0.33,1,96,1.2,0,48]
[5,10.9,170,26,70,2.08,0.95,300,0.33,1,97,1.2,0,47]
[5,11.7,170,26,80,2.33,0.93,300,0.33,1,98,1.2,0,47]
[5,12.4,170,26,90,2.58,0.91,300,0.33,1,99,1.2,0,47]
[5,13,170,26,99,2.8,0.9,300,0.33,1,100,1.2,0,47]
[5,13.2,170,27,1,0.95,0.95,100,0.33,1,2,0.4,0,7]
[5,15.1,170,27,50,1.18,0.8,100,0.33,1,95,0.4,0,7]
[5,16.600000000000001,170,27,60,1.36,0.75,100,0.33,1,96,0.4,0,7]
[5,18.100000000000001,170,27,70,1.53,0.7,100,0.33,1,97,0.4,0,7]
[5,19.600000000000001,170,27,80,1.7,0.65,100,0.33,1,98,0.4,0,7]
[5,21.1,170,27,90,1.87,0.6,100,0.33,1,99,0.4,0,7]
[5,22.3,170,27,99,2.02,0.56000000000000005,100,0.33,1,100,0.4,0,7]
[5,9.6,170,27,1,1.07,1.07,200,0.33,1,3,0.8,0,23]
[5,11.7,170,27,50,1.57,0.97,200,0.33,1,94,0.8,0,23]
[5,12.8,170,27,60,1.82,0.94,200,0.33,1,96,0.8,0,23]
[5,13.8,170,27,70,2.06,0.91,200,0.33,1,97,0.8,0,23]
[5,14.9,170,27,80,2.2999999999999998,0.89,200,0.33,1,98,0.8,0,23]
[5,15.9,170,27,90,2.54,0.86,200,0.33,1,99,0.8,0,23]
[5,16.8,170,27,99,2.76,0.83,200,0.33,1,100,0.8,0,23]
[5,8.1,170,27,1,1.1000000000000001,1.1000000000000001,300,0.33,1,3,1.2,0,48]
[5,9.9,170,27,50,1.7,1.03,300,0.33,1,94,1.2,0,48]
[5,10.6,170,27,60,1.96,1.01,300,0.33,1,96,1.2,0,47]
[5,11.4,170,27,70,2.23,0.99,300,0.33,1,97,1.2,0,47]
[5,12.1,170,27,80,2.4900000000000002,0.97,300,0.33,1,98,1.2,0,47]
[5,12.9,170,27,90,2.76,0.95,300,0.33,1,99,1.2,0,47]
[5,13.6,170,27,99,2.99,0.93,300,0.33,1,100,1.2,0,47]
[5,12.3,240,21,1,0.85,0.85,100,0.46,2,2,0.4,0,7]
[5,12.2,240,21,50,0.84,0.84,100,0.46,2,99,0.4,0,7]
[5,13.1,240,21,60,0.94,0.72,100,0.46,3,94,0.4,0,7]
[5,14.3,240,21,70,1.08,0.66,100,0.46,3,96,0.4,0,7]
[5,15.5,240,21,80,1.22,0.6,100,0.46,3,97,0.4,0,7]
[5,16.600000000000001,240,21,90,1.35,0.54,100,0.46,3,99,0.4,0,7]
[5,17.600000000000001,240,21,99,1.47,0.48,100,0.46,3,100,0.4,0,7]
[5,9.3000000000000007,240,21,1,1.01,1.01,200,0.46,2,2,0.8,0,23]
[5,10,240,21,50,1.1599999999999999,0.94,200,0.46,3,92,0.8,0,23]
[5,10.9,240,21,60,1.36,0.9,200,0.46,3,94,0.8,0,23]
[5,11.7,240,21,70,1.57,0.86,200,0.46,3,95,0.8,0,23]
[5,12.6,240,21,80,1.78,0.82,200,0.46,3,97,0.8,0,23]
[5,13.5,240,21,90,1.98,0.78,200,0.46,3,99,0.8,0,23]
[5,14.3,240,21,99,2.16,0.75,200,0.46,3,100,0.8,0,23]
[5,8,240,21,1,1.06,1.06,300,0.46,2,2,1.2,0,48]
[5,8.6999999999999993,240,21,50,1.3,1,300,0.46,3,91,1.2,0,48]
[5,9.4,240,21,60,1.53,0.97,300,0.46,3,93,1.2,0,48]
[5,10,240,21,70,1.77,0.95,300,0.46,3,95,1.2,0,48]
[5,10.7,240,21,80,2,0.92,300,0.46,3,97,1.2,0,47]
[5,11.4,240,21,90,2.23,0.89,300,0.46,3,99,1.2,0,47]
[5,12,240,21,99,2.44,0.87,300,0.46,3,100,1.2,0,47]
[5,12.7,240,22,1,0.9,0.9,100,0.46,2,2,0.4,0,7]
[5,12.6,240,22,50,0.88,0.81,100,0.46,3,92,0.4,0,7]
[5,13.8,240,22,60,1.03,0.75,100,0.46,3,94,0.4,0,7]
[5,15.1,240,22,70,1.18,0.68,100,0.46,3,96,0.4,0,7]
[5,16.3,240,22,80,1.32,0.62,100,0.46,3,97,0.4,0,7]
[5,17.5,240,22,90,1.46,0.56000000000000005,100,0.46,3,99,0.4,0,7]
[5,18.600000000000001,240,22,99,1.59,0.5,100,0.46,3,100,0.4,0,7]
[5,9.6,240,22,1,1.07,1.07,200,0.46,2,2,0.8,0,23]
[5,10.5,240,22,50,1.27,0.98,200,0.46,3,92,0.8,0,23]
[5,11.4,240,22,60,1.49,0.94,200,0.46,3,94,0.8,0,23]
[5,12.3,240,22,70,1.71,0.9,200,0.46,3,95,0.8,0,23]
[5,13.3,240,22,80,1.93,0.86,200,0.46,3,97,0.8,0,23]
[5,14.2,240,22,90,2.15,0.82,200,0.46,3,99,0.8,0,23]
[5,15,240,22,99,2.34,0.79,200,0.46,3,100,0.8,0,23]
[5,8.1999999999999993,240,22,1,1.1200000000000001,1.1200000000000001,300,0.46,2,2,1.2,0,48]
[5,9.1,240,22,50,1.43,1.06,300,0.46,3,91,1.2,0,48]
[5,9.8000000000000007,240,22,60,1.68,1.02,300,0.46,3,93,1.2,0,48]
[5,10.5,240,22,70,1.92,1,300,0.46,3,95,1.2,0,48]
[5,11.2,240,22,80,2.17,0.97,300,0.46,3,97,1.2,0,47]
[5,11.9,240,22,90,2.42,0.94,300,0.46,3,99,1.2,0,47]
[5,12.6,240,22,99,2.64,0.91,300,0.46,3,100,1.2,0,47]
[5,13.2,240,23,1,0.95,0.95,100,0.46,2,2,0.4,0,7]
[5,13.3,240,23,50,0.96,0.85,100,0.46,3,92,0.4,0,7]
[5,14.6,240,23,60,1.1200000000000001,0.78,100,0.46,3,94,0.4,0,7]
[5,15.9,240,23,70,1.27,0.71,100,0.46,3,96,0.4,0,7]
[5,17.2,240,23,80,1.42,0.64,100,0.46,3,97,0.4,0,7]
[5,18.5,240,23,90,1.57,0.57999999999999996,100,0.46,3,99,0.4,0,7]
[5,19.600000000000001,240,23,99,1.7,0.52,100,0.46,3,100,0.4,0,7]
[5,9.8000000000000007,240,23,1,1.1299999999999999,1.1299999999999999,200,0.46,2,2,0.8,0,23]
[5,11,240,23,50,1.39,1.03,200,0.46,3,92,0.8,0,23]
[5,12,240,23,60,1.63,0.99,200,0.46,3,94,0.8,0,23]
[5,13,240,23,70,1.86,0.95,200,0.46,3,95,0.8,0,23]
[5,14,240,23,80,2.09,0.9,200,0.46,3,97,0.8,0,23]
[5,14.9,240,23,90,2.3199999999999998,0.86,200,0.46,3,99,0.8,0,23]
[5,15.8,240,23,99,2.52,0.82,200,0.46,3,100,0.8,0,23]
[5,8.4,240,23,1,1.19,1.19,300,0.46,2,2,1.2,0,48]
[5,9.5,240,23,50,1.57,1.1100000000000001,300,0.46,3,91,1.2,0,48]
[5,10.199999999999999,240,23,60,1.83,1.08,300,0.46,3,93,1.2,0,48]
[5,11,240,23,70,2.09,1.05,300,0.46,3,95,1.2,0,47]
[5,11.7,240,23,80,2.35,1.02,300,0.46,3,97,1.2,0,47]
[5,12.5,240,23,90,2.61,0.98,300,0.46,3,99,1.2,0,47]
[5,13.1,240,23,99,2.85,0.96,300,0.46,3,100,1.2,0,47]
[5,13.6,240,24,1,1,1,100,0.46,2,2,0.4,0,7]
[5,14,240,24,50,1.05,0.88,100,0.46,3,92,0.4,0,7]
[5,15.4,240,24,60,1.21,0.81,100,0.46,3,94,0.4,0,7]
[5,16.8,240,24,70,1.37,0.74,100,0.46,3,96,0.4,0,7]
[5,18.100000000000001,240,24,80,1.53,0.67,100,0.46,3,97,0.4,0,7]
[5,19.5,240,24,90,1.68,0.6,100,0.46,3,99,0.4,0,7]
[5,20.6,240,24,99,1.82,0.54,100,0.46,3,100,0.4,0,7]
[5,10.1,240,24,1,1.19,1.19,200,0.46,2,2,0.8,0,23]
[5,11.5,240,24,50,1.52,1.08,200,0.46,3,91,0.8,0,23]
[5,12.6,240,24,60,1.76,1.03,200,0.46,3,94,0.8,0,23]
[5,13.6,240,24,70,2.0099999999999998,0.99,200,0.46,3,95,0.8,0,23]
[5,14.7,240,24,80,2.25,0.94,200,0.46,3,97,0.8,0,23]
[5,15.7,240,24,90,2.4900000000000002,0.9,200,0.46,3,99,0.8,0,23]
[5,16.600000000000001,240,24,99,2.71,0.86,200,0.46,3,100,0.8,0,23]
[5,8.6,240,24,1,1.25,1.25,300,0.46,2,2,1.2,0,48]
[5,9.9,240,24,50,1.7,1.1599999999999999,300,0.46,3,91,1.2,0,48]
[5,10.7,240,24,60,1.98,1.1299999999999999,300,0.46,3,93,1.2,0,47]
[5,11.5,240,24,70,2.2599999999999998,1.0900000000000001,300,0.46,3,95,1.2,0,47]
[5,12.3,240,24,80,2.54,1.06,300,0.46,3,97,1.2,0,47]
[5,13,240,24,90,2.81,1.03,300,0.46,3,99,1.2,0,47]
[5,13.8,240,24,99,3.06,1,300,0.46,3,100,1.2,0,47]
[5,14.1,240,25,1,1.06,1.06,100,0.46,2,2,0.4,0,7]
[5,14.7,240,25,50,1.1299999999999999,0.91,100,0.46,3,92,0.4,0,7]
[5,16.2,240,25,60,1.3,0.84,100,0.46,3,94,0.4,0,7]
[5,17.600000000000001,240,25,70,1.47,0.76,100,0.46,3,96,0.4,0,7]
[5,19.100000000000001,240,25,80,1.64,0.69,100,0.46,3,97,0.4,0,7]
[5,20.5,240,25,90,1.8,0.61,100,0.46,3,99,0.4,0,7]
[5,21.7,240,25,99,1.94,0.55000000000000004,100,0.46,3,100,0.4,0,7]
[5,10.4,240,25,1,1.25,1.25,200,0.46,2,2,0.8,0,23]
[5,12,240,25,50,1.64,1.1200000000000001,200,0.46,3,91,0.8,0,23]
[5,13.2,240,25,60,1.9,1.07,200,0.46,3,94,0.8,0,23]
[5,14.3,240,25,70,2.16,1.03,200,0.46,3,95,0.8,0,23]
[5,15.4,240,25,80,2.42,0.98,200,0.46,3,97,0.8,0,23]
[5,16.5,240,25,90,2.67,0.93,200,0.46,3,99,0.8,0,23]
[5,17.5,240,25,99,2.9,0.89,200,0.46,3,100,0.8,0,23]
[5,8.6999999999999993,240,25,1,1.31,1.31,300,0.46,2,2,1.2,0,48]
[5,10.3,240,25,50,1.84,1.21,300,0.46,3,91,1.2,0,48]
[5,11.1,240,25,60,2.14,1.18,300,0.46,3,93,1.2,0,47]
[5,12,240,25,70,2.4300000000000002,1.1399999999999999,300,0.46,3,95,1.2,0,47]
[5,12.8,240,25,80,2.73,1.1100000000000001,300,0.46,3,97,1.2,0,47]
[5,13.6,240,25,90,3.02,1.07,300,0.46,3,99,1.2,0,47]
[5,14.4,240,25,99,3.29,1.04,300,0.46,3,100,1.2,0,47]
[5,14.5,240,26,1,1.1100000000000001,1.1100000000000001,100,0.46,2,2,0.4,0,7]
[5,15.4,240,26,50,1.22,0.94,100,0.46,3,92,0.4,0,7]
[5,17,240,26,60,1.4,0.86,100,0.46,3,94,0.4,0,7]
[5,18.5,240,26,70,1.58,0.78,100,0.46,3,96,0.4,0,7]
[5,20,240,26,80,1.75,0.71,100,0.46,3,97,0.4,0,7]
[5,21.5,240,26,90,1.92,0.63,100,0.46,3,99,0.4,0,7]
[5,22.7,240,26,99,2.06,0.56000000000000005,100,0.46,3,100,0.4,0,7]
[5,10.6,240,26,1,1.31,1.31,200,0.46,2,2,0.8,0,23]
[5,12.6,240,26,50,1.77,1.17,200,0.46,3,91,0.8,0,23]
[5,13.8,240,26,60,2.0499999999999998,1.1200000000000001,200,0.46,3,93,0.8,0,23]
[5,15,240,26,70,2.3199999999999998,1.06,200,0.46,3,95,0.8,0,23]
[5,16.100000000000001,240,26,80,2.59,1.01,200,0.46,3,97,0.8,0,23]
[5,17.3,240,26,90,2.86,0.96,200,0.46,3,99,0.8,0,23]
[5,18.3,240,26,99,3.11,0.92,200,0.46,3,100,0.8,0,23]
[5,8.9,240,26,1,1.37,1.37,300,0.46,2,3,1.2,0,48]
[5,10.7,240,26,50,1.99,1.26,300,0.46,3,91,1.2,0,47]
[5,11.6,240,26,60,2.2999999999999998,1.22,300,0.46,3,93,1.2,0,47]
[5,12.5,240,26,70,2.62,1.19,300,0.46,3,95,1.2,0,47]
[5,13.4,240,26,80,2.93,1.1499999999999999,300,0.46,3,97,1.2,0,47]
[5,14.3,240,26,90,3.24,1.1100000000000001,300,0.46,3,99,1.2,0,47]
[5,15.1,240,26,99,3.52,1.08,300,0.46,3,100,1.2,0,47]
[5,15,240,27,1,1.1599999999999999,1.1599999999999999,100,0.46,2,2,0.4,0,7]
[5,16.2,240,27,50,1.31,0.97,100,0.46,3,92,0.4,0,7]
[5,17.8,240,27,60,1.5,0.89,100,0.46,3,94,0.4,0,7]
[5,19.399999999999999,240,27,70,1.68,0.8,100,0.46,3,96,0.4,0,7]
[5,21,240,27,80,1.86,0.73,100,0.46,3,97,0.4,0,7]
[5,22.5,240,27,90,2.0299999999999998,0.65,100,0.46,3,99,0.4,0,7]
[5,23.8,240,27,99,2.19,0.57999999999999996,100,0.46,3,100,0.4,0,7]
[5,10.9,240,27,1,1.37,1.37,200,0.46,2,2,0.8,0,23]
[5,13.2,240,27,50,1.9,1.21,200,0.46,3,91,0.8,0,23]
[5,14.4,240,27,60,2.19,1.1599999999999999,200,0.46,3,94,0.8,0,23]
[5,15.7,240,27,70,2.48,1.1000000000000001,200,0.46,3,95,0.8,0,23]
[5,16.899999999999999,240,27,80,2.77,1.05,200,0.46,3,97,0.8,0,23]
[5,18.100000000000001,240,27,90,3.06,1,200,0.46,3,99,0.8,0,23]
[5,19.2,240,27,99,3.31,0.95,200,0.46,3,100,0.8,0,23]
[5,9.1,240,27,1,1.44,1.44,300,0.46,2,3,1.2,0,48]
[5,11.1,240,27,50,2.14,1.31,300,0.46,3,91,1.2,0,47]
[5,12.1,240,27,60,2.4700000000000002,1.27,300,0.46,3,93,1.2,0,47]
[5,13,240,27,70,2.8,1.23,300,0.46,3,95,1.2,0,47]
[5,14,240,27,80,3.13,1.19,300,0.46,3,97,1.2,0,47]
[5,14.9,240,27,90,3.46,1.1599999999999999,300,0.46,3,99,1.2,0,47]
[5,15.8,240,27,99,3.76,1.1200000000000001,300,0.46,3,100,1.2,0,47]
[5,13.2,310,21,1,0.95,0.95,100,0.6,3,1,0.4,0,7]
[5,13.2,310,21,50,0.95,0.95,100,0.6,3,90,0.4,0,7]
[5,13.6,310,21,60,1,0.82,100,0.6,4,92,0.4,0,7]
[5,14.8,310,21,70,1.1399999999999999,0.73,100,0.6,4,94,0.4,0,7]
[5,16,310,21,80,1.29,0.65,100,0.6,4,96,0.4,0,7]
[5,17.2,310,21,90,1.43,0.56999999999999995,100,0.6,4,98,0.4,0,7]
[5,18.3,310,21,99,1.55,0.5,100,0.6,4,100,0.4,0,7]
[5,10.1,310,21,1,1.19,1.19,200,0.6,3,2,0.8,0,23]
[5,10.6,310,21,50,1.3,1.0900000000000001,200,0.6,4,89,0.8,0,23]
[5,11.6,310,21,60,1.53,1.04,200,0.6,4,92,0.8,0,23]
[5,12.6,310,21,70,1.76,0.98,200,0.6,4,94,0.8,0,23]
[5,13.5,310,21,80,1.99,0.92,200,0.6,4,96,0.8,0,23]
[5,14.5,310,21,90,2.2200000000000002,0.87,200,0.6,4,98,0.8,0,23]
[5,15.4,310,21,99,2.42,0.82,200,0.6,4,100,0.8,0,23]
[5,8.6,310,21,1,1.27,1.27,300,0.6,3,2,1.2,0,48]
[5,9.3000000000000007,310,21,50,1.51,1.19,300,0.6,4,89,1.2,0,48]
[5,10.1,310,21,60,1.78,1.1499999999999999,300,0.6,4,91,1.2,0,48]
[5,10.8,310,21,70,2.04,1.1000000000000001,300,0.6,4,94,1.2,0,47]
[5,11.6,310,21,80,2.31,1.06,300,0.6,4,96,1.2,0,47]
[5,12.4,310,21,90,2.58,1.02,300,0.6,4,98,1.2,0,47]
[5,13.1,310,21,99,2.82,0.98,300,0.6,4,100,1.2,0,47]
[5,13.7,310,22,1,1.01,1.01,100,0.6,3,1,0.4,0,7]
[5,13.7,310,22,50,1.01,1.01,100,0.6,3,94,0.4,0,7]
[5,14.4,310,22,60,1.0900000000000001,0.85,100,0.6,4,92,0.4,0,7]
[5,15.7,310,22,70,1.24,0.76,100,0.6,4,94,0.4,0,7]
[5,16.899999999999999,310,22,80,1.39,0.68,100,0.6,4,96,0.4,0,7]
[5,18.2,310,22,90,1.54,0.59,100,0.6,4,98,0.4,0,7]
[5,19.3,310,22,99,1.66,0.52,100,0.6,4,100,0.4,0,7]
[5,10.4,310,22,1,1.26,1.26,200,0.6,3,2,0.8,0,23]
[5,11.1,310,22,50,1.43,1.1499999999999999,200,0.6,4,89,0.8,0,23]
[5,12.2,310,22,60,1.68,1.0900000000000001,200,0.6,4,92,0.8,0,23]
[5,13.2,310,22,70,1.92,1.03,200,0.6,4,94,0.8,0,23]
[5,14.3,310,22,80,2.16,0.97,200,0.6,4,96,0.8,0,23]
[5,15.3,310,22,90,2.4,0.91,200,0.6,4,98,0.8,0,23]
[5,16.2,310,22,99,2.61,0.86,200,0.6,4,100,0.8,0,23]
[5,8.8000000000000007,310,22,1,1.34,1.34,300,0.6,3,2,1.2,0,48]
[5,9.6999999999999993,310,22,50,1.66,1.25,300,0.6,4,89,1.2,0,48]
[5,10.6,310,22,60,1.94,1.2,300,0.6,4,91,1.2,0,48]
[5,11.4,310,22,70,2.23,1.1599999999999999,300,0.6,4,94,1.2,0,47]
[5,12.2,310,22,80,2.5099999999999998,1.1100000000000001,300,0.6,4,96,1.2,0,47]
[5,13,310,22,90,2.8,1.07,300,0.6,4,98,1.2,0,47]
[5,13.7,310,22,99,3.05,1.03,300,0.6,4,100,1.2,0,47]
[5,14.2,310,23,1,1.07,1.07,100,0.6,3,1,0.4,0,7]
[5,14.2,310,23,50,1.07,1.07,100,0.6,3,97,0.4,0,7]
[5,15.2,310,23,60,1.18,0.88,100,0.6,4,92,0.4,0,7]
[5,16.5,310,23,70,1.34,0.79,100,0.6,4,94,0.4,0,7]
[5,17.899999999999999,310,23,80,1.5,0.7,100,0.6,4,96,0.4,0,7]
[5,19.2,310,23,90,1.65,0.61,100,0.6,4,98,0.4,0,7]
[5,20.3,310,23,99,1.79,0.53,100,0.6,4,100,0.4,0,7]
[5,10.7,310,23,1,1.33,1.33,200,0.6,3,2,0.8,0,23]
[5,11.7,310,23,50,1.57,1.2,200,0.6,4,89,0.8,0,23]
[5,12.8,310,23,60,1.82,1.1399999999999999,200,0.6,4,92,0.8,0,23]
[5,13.9,310,23,70,2.08,1.07,200,0.6,4,94,0.8,0,23]
[5,15,310,23,80,2.34,1.01,200,0.6,4,96,0.8,0,23]
[5,16.100000000000001,310,23,90,2.59,0.95,200,0.6,4,98,0.8,0,23]
[5,17.100000000000001,310,23,99,2.81,0.89,200,0.6,4,100,0.8,0,23]
[5,9.1,310,23,1,1.42,1.42,300,0.6,3,2,1.2,0,48]
[5,10.199999999999999,310,23,50,1.81,1.31,300,0.6,4,89,1.2,0,48]
[5,11,310,23,60,2.12,1.26,300,0.6,4,91,1.2,0,47]
[5,11.9,310,23,70,2.42,1.21,300,0.6,4,94,1.2,0,47]
[5,12.8,310,23,80,2.72,1.17,300,0.6,4,96,1.2,0,47]
[5,13.6,310,23,90,3.02,1.1200000000000001,300,0.6,4,98,1.2,0,47]
[5,14.4,310,23,99,3.29,1.08,300,0.6,4,100,1.2,0,47]
[5,14.7,310,24,1,1.1299999999999999,1.1299999999999999,100,0.6,3,1,0.4,0,7]
[5,14.5,310,24,50,1.1100000000000001,1.01,100,0.6,4,90,0.4,0,7]
[5,16,310,24,60,1.28,0.91,100,0.6,4,92,0.4,0,7]
[5,17.399999999999999,310,24,70,1.45,0.82,100,0.6,4,94,0.4,0,7]
[5,18.8,310,24,80,1.61,0.72,100,0.6,4,97,0.4,0,7]
[5,20.2,310,24,90,1.77,0.63,100,0.6,4,98,0.4,0,7]
[5,21.4,310,24,99,1.9,0.55000000000000004,100,0.6,4,100,0.4,0,7]
[5,11,310,24,1,1.4,1.4,200,0.6,3,2,0.8,0,23]
[5,12.3,310,24,50,1.7,1.25,200,0.6,4,89,0.8,0,23]
[5,13.5,310,24,60,1.98,1.19,200,0.6,4,92,0.8,0,23]
[5,14.6,310,24,70,2.25,1.1200000000000001,200,0.6,4,94,0.8,0,23]
[5,15.8,310,24,80,2.5099999999999998,1.05,200,0.6,4,96,0.8,0,23]
[5,16.899999999999999,310,24,90,2.78,0.98,200,0.6,4,98,0.8,0,23]
[5,18,310,24,99,3.02,0.92,200,0.6,4,100,0.8,0,23]
[5,9.3000000000000007,310,24,1,1.5,1.5,300,0.6,3,2,1.2,0,48]
[5,10.6,310,24,50,1.97,1.37,300,0.6,4,88,1.2,0,47]
[5,11.6,310,24,60,2.29,1.32,300,0.6,4,91,1.2,0,47]
[5,12.5,310,24,70,2.61,1.27,300,0.6,4,94,1.2,0,47]
[5,13.4,310,24,80,2.93,1.22,300,0.6,4,96,1.2,0,47]
[5,18.3,310,25,70,1.55,0.84,100,0.6,4,95,0.4,0,7]
[5,12.9,310,25,50,1.84,1.3,200,0.6,4,89,0.8,0,23]
[5,9.5,310,25,1,1.57,1.57,300,0.6,3,2,1.2,0,48]
[5,15,310,25,90,3.49,1.21,300,0.6,4,98,1.2,0,47]
[5,19.2,310,26,70,1.66,0.87,100,0.6,4,95,0.4,0,7]
[5,14.8,310,26,60,2.29,1.28,200,0.6,4,92,0.8,0,23]
[5,9.6999999999999993,310,26,1,1.65,1.65,300,0.6,3,2,1.2,0,48]
[5,16.600000000000001,310,26,99,4.0599999999999996,1.21,300,0.6,4,100,1.2,0,47]
[5,21.7,310,27,80,1.95,0.78,100,0.6,4,97,0.4,0,7]
[5,15.5,310,27,60,2.46,1.32,200,0.6,4,92,0.8,0,23]
[5,16.899999999999999,310,27,70,2.77,1.24,200,0.6,4,94,0.8,0,23]
[5,12.1,310,27,50,2.48,1.54,300,0.6,4,88,1.2,0,47]
[5,17.399999999999999,310,27,99,4.34,1.25,300,0.6,4,100,1.2,0,46]
[5,17.600000000000001,380,21,90,1.47,0.6,100,0.74,6,98,0.4,0,7]
[5,13.2,380,21,70,1.9,1.08,200,0.74,6,93,0.8,0,23]
[5,10.6,380,21,60,1.97,1.29,300,0.74,6,90,1.2,0,47]
[5,14.5,380,22,1,1.1000000000000001,1.1000000000000001,100,0.74,4,1,0.4,0,7]
[5,18.600000000000001,380,22,90,1.58,0.62,100,0.74,6,98,0.4,0,7]
[5,15,380,22,80,2.33,1.05,200,0.74,6,95,0.8,0,23]
[5,11.1,380,22,60,2.15,1.35,300,0.74,6,90,1.2,0,47]
[5,15,380,23,50,1.1599999999999999,1.1599999999999999,100,0.74,4,90,0.4,0,7]
[5,20.8,380,23,99,1.84,0.54,100,0.74,6,100,0.4,0,7]
[5,15.8,380,23,80,2.5099999999999998,1.0900000000000001,200,0.74,6,95,0.8,0,23]
[5,16.899999999999999,380,23,90,2.78,1.01,200,0.74,6,98,0.8,0,23]
[5,12.6,380,23,70,2.67,1.35,300,0.74,6,92,1.2,0,47]
[5,15.5,380,24,50,1.23,1.23,100,0.74,4,93,0.4,0,7]
[5,11.8,380,24,1,1.58,1.58,200,0.74,4,2,0.8,0,23]
[5,17.8,380,24,90,2.99,1.05,200,0.74,6,98,0.8,0,23]
[5,14.3,380,24,80,3.24,1.34,300,0.74,6,95,1.2,0,47]
[5,17.2,380,25,60,1.42,1.04,100,0.74,6,91,0.4,0,7]
[5,12.1,380,25,1,1.66,1.66,200,0.74,4,2,0.8,0,23]
[5,19.899999999999999,380,25,99,3.46,1,200,0.74,6,100,0.8,0,23]
[5,15,380,25,80,3.48,1.39,300,0.74,6,95,1.2,0,47]
[5,18.100000000000001,380,26,60,1.52,1.07,100,0.74,6,91,0.4,0,7]
[5,14.2,380,26,50,2.14,1.51,200,0.74,6,87,0.8,0,23]
[5,20.8,380,26,99,3.69,1.03,200,0.74,6,100,0.8,0,23]
[5,10.4,380,26,1,1.89,1.89,300,0.74,4,2,1.2,0,48]
[5,16.8,380,26,90,4.12,1.37,300,0.74,6,98,1.2,0,47]
[5,20.6,380,27,70,1.81,0.96,100,0.74,6,93,0.4,0,7]
[5,16.3,380,27,60,2.64,1.45,200,0.74,6,90,0.8,0,23]
[5,10.6,380,27,1,1.97,1.97,300,0.74,4,2,1.2,0,47]
[5,18.7,380,27,99,4.7699999999999996,1.34,300,0.74,6,100,1.2,0,46]
[6,12.9,100,21,80,0.81,0.38,100,0.19,1,99,0.4,0,7]
[6,9.1,100,21,60,0.71,0.45,200,0.19,1,98,0.8,0,23]
[6,7.8,100,21,50,0.62,0.47,300,0.19,1,98,1.2,0,48]
[6,9.5,100,21,99,1.21,0.45,300,0.19,1,100,1.2,0,48]
[6,13.6,100,22,80,0.88,0.4,100,0.19,1,99,0.4,0,7]
[6,9.9,100,22,70,0.91,0.48,200,0.19,1,99,0.8,0,23]
[6,8,100,22,50,0.69,0.5,300,0.19,1,98,1.2,0,48]
[6,8.3000000000000007,100,22,60,0.81,0.5,300,0.19,1,98,1.2,0,48]
[6,10.4,100,23,1,0.51,0.51,100,0.19,0,2,0.4,0,7]
[6,15.2,100,23,90,1.07,0.41,100,0.19,1,100,0.4,0,7]
[6,10.8,100,23,80,1.1299999999999999,0.5,200,0.19,1,99,0.8,0,23]
[6,8.5,100,23,60,0.89,0.52,300,0.19,1,98,1.2,0,48]
[6,11.8,100,24,50,0.68,0.49,100,0.19,1,98,0.4,0,7]
[6,16.899999999999999,100,24,99,1.27,0.41,100,0.19,1,100,0.4,0,7]
[6,11.2,100,24,80,1.22,0.52,200,0.19,1,99,0.8,0,23]
[6,9.1999999999999993,100,24,70,1.1200000000000001,0.55000000000000004,300,0.19,1,99,1.2,0,48]
[6,12.4,100,25,50,0.74,0.51,100,0.19,1,98,0.4,0,7]
[6,17.7,100,25,99,1.36,0.43,100,0.19,1,100,0.4,0,7]
[6,12.3,100,25,90,1.46,0.54,200,0.19,1,100,0.8,0,23]
[6,9.4,100,25,70,1.21,0.56999999999999995,300,0.19,1,99,1.2,0,48]
[6,9.9,100,25,80,1.36,0.56999999999999995,300,0.19,1,99,1.2,0,47]
[6,14.1,100,26,60,0.94,0.52,100,0.19,1,98,0.4,0,7]
[6,8.6999999999999993,100,26,1,0.63,0.63,200,0.19,0,3,0.8,0,23]
[6,13.4,100,26,99,1.71,0.56000000000000005,200,0.19,1,100,0.8,0,23]
[6,10.199999999999999,100,26,80,1.46,0.59,300,0.19,1,99,1.2,0,47]
[6,14.7,100,27,60,1.01,0.54,100,0.19,1,98,0.4,0,7]
[6,10.4,100,27,50,1.02,0.62,200,0.19,1,98,0.8,0,23]
[6,13.9,100,27,99,1.83,0.57999999999999996,200,0.19,1,100,0.8,0,23]
[6,11,100,27,90,1.74,0.61,300,0.19,1,100,1.2,0,47]
[6,13.7,170,21,70,0.9,0.53,100,0.33,1,97,0.4,0,7]
[6,9.6999999999999993,170,21,50,0.87,0.7,200,0.33,1,95,0.8,0,23]
[6,8.1999999999999993,170,21,1,0.76,0.76,300,0.33,1,2,1.2,0,48]
[6,10.8,170,21,90,1.68,0.68,300,0.33,1,99,1.2,0,47]
[6,11.3,170,21,99,1.84,0.66,300,0.33,1,100,1.2,0,47]
[6,15.6,170,22,80,1.1200000000000001,0.52,100,0.33,1,98,0.4,0,7]
[6,10.9,170,22,60,1.1399999999999999,0.72,200,0.33,1,96,0.8,0,23]
[6,9,170,22,50,1.04,0.78,300,0.33,1,95,1.2,0,48]
[6,11.7,170,22,99,2,0.7,300,0.33,1,100,1.2,0,47]
[6,16.399999999999999,170,23,80,1.21,0.54,100,0.33,1,98,0.4,0,7]
[6,12.2,170,23,70,1.44,0.73,200,0.33,1,97,0.8,0,23]
[6,9.3000000000000007,170,23,50,1.1499999999999999,0.82,300,0.33,1,95,1.2,0,48]
[6,12.7,170,24,1,0.78,0.78,100,0.33,1,2,0.4,0,7]
[6,18.5,170,24,90,1.46,0.52,100,0.33,1,99,0.4,0,7]
[6,12.7,170,24,70,1.57,0.77,200,0.33,1,97,0.8,0,23]
[6,10.199999999999999,170,24,60,1.48,0.84,300,0.33,1,96,1.2,0,47]
[6,13.1,170,25,1,0.83,0.83,100,0.33,1,2,0.4,0,7]
[6,19.399999999999999,170,25,90,1.56,0.54,100,0.33,1,99,0.4,0,7]
[6,20.6,170,25,99,1.7,0.5,100,0.33,1,100,0.4,0,7]
[6,14.2,170,25,80,1.91,0.78,200,0.33,1,98,0.8,0,23]
[6,11.2,170,25,70,1.84,0.87,300,0.33,1,97,1.2,0,47]
[6,14.8,170,26,50,1.02,0.75,100,0.33,1,95,0.4,0,7]
[6,21.6,170,26,99,1.82,0.52,100,0.33,1,100,0.4,0,7]
[6,15.8,170,26,90,2.2799999999999998,0.79,200,0.33,1,99,0.8,0,23]
[6,11.7,170,26,70,1.98,0.91,300,0.33,1,97,1.2,0,47]
[6,17,170,27,60,1.28,0.72,100,0.33,1,96,0.4,0,7]
[6,10.4,170,27,1,1.02,1.02,200,0.33,1,3,0.8,0,23]
[6,16.5,170,27,90,2.44,0.82,200,0.33,1,99,0.8,0,23]
[6,12.8,170,27,80,2.39,0.93,300,0.33,1,98,1.2,0,47]
[6,13.4,240,21,60,0.86,0.68,100,0.46,3,94,0.4,0,7]
[6,10.1,240,21,1,0.95,0.95,200,0.46,2,2,0.8,0,23]
[6,10.5,240,21,50,1.05,0.88,200,0.46,3,92,0.8,0,23]
[6,14.8,240,21,99,2.0499999999999998,0.7,200,0.46,3,100,0.8,0,23]
[6,12,240,21,90,2.1,0.84,300,0.46,3,99,1.2,0,47]
[6,15.4,240,22,70,1.0900000000000001,0.65,100,0.46,3,96,0.4,0,7]
[6,11,240,22,50,1.1599999999999999,0.93,200,0.46,3,92,0.8,0,23]
[6,9,240,22,1,1.06,1.06,300,0.46,2,2,1.2,0,48]
[6,12.6,240,22,90,2.29,0.88,300,0.46,3,99,1.2,0,47]
[6,17.5,240,23,80,1.34,0.61,100,0.46,3,97,0.4,0,7]
[6,12.5,240,23,60,1.51,0.94,200,0.46,3,94,0.8,0,23]
[6,9.1999999999999993,240,23,1,1.1200000000000001,1.1200000000000001,300,0.46,2,2,1.2,0,48]
[6,13.8,240,23,99,2.72,0.9,300,0.46,3,100,1.2,0,47]
[6,18.399999999999999,240,24,80,1.44,0.64,100,0.46,3,97,0.4,0,7]
[6,13.1,240,24,60,1.65,0.98,200,0.46,3,94,0.8,0,23]
[6,14.1,240,24,70,1.89,0.94,200,0.46,3,95,0.8,0,23]
[6,10.5,240,24,50,1.58,1.1000000000000001,300,0.46,3,91,1.2,0,47]
[6,14.6,240,25,1,1.01,1.01,100,0.46,2,2,0.4,0,7]
[6,20.7,240,25,90,1.71,0.59,100,0.46,3,99,0.4,0,7]
[6,14.8,240,25,70,2.04,0.98,200,0.46,3,95,0.8,0,23]
[6,11.8,240,25,60,2.0099999999999998,1.1200000000000001,300,0.46,3,93,1.2,0,47]
[6,15.1,240,26,1,1.06,1.06,100,0.46,2,2,0.4,0,7]
[6,21.7,240,26,90,1.83,0.6,100,0.46,3,99,0.4,0,7]
[6,16.600000000000001,240,26,80,2.4700000000000002,0.97,200,0.46,3,97,0.8,0,23]
[6,12.2,240,26,60,2.1800000000000002,1.17,300,0.46,3,93,1.2,0,47]
[6,16.5,240,27,50,1.22,0.94,100,0.46,3,92,0.4,0,7]
[6,24,240,27,99,2.1,0.55000000000000004,100,0.46,3,100,0.4,0,7]
[6,17.399999999999999,240,27,80,2.65,1,200,0.46,3,97,0.8,0,23]
[6,18.600000000000001,240,27,90,2.93,0.95,200,0.46,3,99,0.8,0,23]
[6,13.6,240,27,70,2.67,1.18,300,0.46,3,95,1.2,0,47]
[6,13.8,310,21,60,0.91,0.78,100,0.6,4,92,0.4,0,7]
[6,10.8,310,21,1,1.1100000000000001,1.1100000000000001,200,0.6,3,2,0.8,0,23]
[6,14.9,310,21,90,2.08,0.81,200,0.6,4,98,0.8,0,23]
[6,12.2,310,21,80,2.16,1,300,0.6,4,96,1.2,0,47]
[6,14.6,310,22,60,1,0.82,100,0.6,4,92,0.4,0,7]
[6,11.1,310,22,1,1.19,1.19,200,0.6,3,2,0.8,0,23]
[6,16.600000000000001,310,22,99,2.48,0.8,200,0.6,4,100,0.8,0,23]
[6,12.8,310,22,80,2.36,1.05,300,0.6,4,96,1.2,0,47]
[6,16.7,310,23,70,1.25,0.76,100,0.6,4,95,0.4,0,7]
[6,12.2,310,23,50,1.44,1.1499999999999999,200,0.6,4,89,0.8,0,23]
[6,17.5,310,23,99,2.67,0.84,200,0.6,4,100,0.8,0,23]
[6,9.8000000000000007,310,23,1,1.34,1.34,300,0.6,3,2,1.2,0,47]
[6,14.2,310,23,90,2.87,1.06,300,0.6,4,98,1.2,0,47]
[6,19,310,24,80,1.51,0.69,100,0.6,4,97,0.4,0,7]
[6,13.9,310,24,60,1.84,1.1299999999999999,200,0.6,4,92,0.8,0,23]
[6,10.1,310,24,1,1.42,1.42,300,0.6,3,2,1.2,0,47]
[6,15.7,310,24,99,3.38,1.06,300,0.6,4,100,1.2,0,47]
[6,20,310,25,80,1.62,0.71,100,0.6,4,97,0.4,0,7]
[6,14.6,310,25,60,2,1.18,200,0.6,4,92,0.8,0,23]
[6,11.7,310,25,50,1.99,1.37,300,0.6,4,89,1.2,0,47]
[6,16.399999999999999,310,25,99,3.64,1.1000000000000001,300,0.6,4,100,1.2,0,46]
[6,22.4,310,26,90,1.9,0.63,100,0.6,4,98,0.4,0,7]
[6,16.5,310,26,70,2.4500000000000002,1.1499999999999999,200,0.6,4,94,0.8,0,23]
[6,12.2,310,26,50,2.16,1.42,300,0.6,4,89,1.2,0,47]
[6,13.2,310,26,60,2.5099999999999998,1.37,300,0.6,4,91,1.2,0,47]
[6,16.8,310,27,1,1.26,1.26,100,0.6,3,2,0.4,0,7]
[6,23.4,310,27,90,2.0299999999999998,0.65,100,0.6,4,98,0.4,0,7]
[6,18.7,310,27,80,2.94,1.1100000000000001,200,0.6,4,96,0.8,0,23]
[6,13.7,310,27,60,2.71,1.42,300,0.6,4,91,1.2,0,47]
[6,14.3,380,21,50,0.97,0.97,100,0.74,4,82,0.4,0,7]
[6,18.899999999999999,380,21,99,1.5,0.48,100,0.74,6,100,0.4,0,7]
[6,14.6,380,21,80,2,0.95,200,0.74,6,95,0.8,0,23]
[6,12,380,21,70,2.1,1.1599999999999999,300,0.74,6,93,1.2,0,47]
[6,14.9,380,22,50,1.04,1.04,100,0.74,4,84,0.4,0,7]
[6,11.7,380,22,1,1.34,1.34,200,0.74,4,2,0.8,0,23]
[6,16.399999999999999,380,22,90,2.4300000000000002,0.92,200,0.74,6,98,0.8,0,23]
[6,12.6,380,22,70,2.2999999999999998,1.22,300,0.74,6,93,1.2,0,47]
[6,13.5,380,22,80,2.61,1.1599999999999999,300,0.74,6,95,1.2,0,47]
[6,15.7,380,23,60,1.1299999999999999,0.94,100,0.74,6,91,0.4,0,7]
[6,12.1,380,23,1,1.42,1.42,200,0.74,4,2,0.8,0,23]
[6,18.3,380,23,99,2.87,0.88,200,0.74,6,100,0.8,0,23]
[6,14.1,380,23,80,2.84,1.22,300,0.74,6,95,1.2,0,47]
[6,18,380,24,70,1.4,0.86,100,0.74,6,93,0.4,0,7]
[6,13.3,380,24,50,1.7,1.34,200,0.74,6,87,0.8,0,23]
[6,19.2,380,24,99,3.08,0.91,200,0.74,6,100,0.8,0,23]
[6,15.8,380,24,90,3.42,1.21,300,0.74,6,98,1.2,0,47]
[6,18.899999999999999,380,25,70,1.5,0.88,100,0.74,6,93,0.4,0,7]
[6,13.9,380,25,50,1.84,1.4,200,0.74,6,87,0.8,0,23]
[6,10.9,380,25,1,1.71,1.71,300,0.74,4,2,1.2,0,47]
[6,16.5,380,25,90,3.68,1.25,300,0.74,6,98,1.2,0,46]
[6,17.5,380,25,99,4.01,1.19,300,0.74,6,100,1.2,0,46]
[6,21.3,380,26,80,1.78,0.78,100,0.74,6,96,0.4,0,7]
[6,16,380,26,60,2.3199999999999998,1.35,200,0.74,6,90,0.8,0,23]
[6,12.8,380,26,50,2.39,1.61,300,0.74,6,86,1.2,0,47]
[6,18.3,380,26,99,4.29,1.23,300,0.74,6,100,1.2,0,46]
[6,23.8,380,27,90,2.0699999999999998,0.67,100,0.74,6,98,0.4,0,7]
[6,18.100000000000001,380,27,70,2.83,1.3,200,0.74,6,93,0.8,0,23]
[6,13.4,380,27,50,2.58,1.67,300,0.74,6,86,1.2,0,47]
[7,10.6,100,21,1,0.42,0.42,100,0.19,0,2,0.4,0,7]
[7,14.3,100,21,90,0.85,0.34,100,0.19,1,100,0.4,0,7]
[7,10.3,100,21,70,0.77,0.42,200,0.19,1,99,0.8,0,23]
[7,8.9,100,21,60,0.68,0.44,300,0.19,1,98,1.2,0,47]
[7,10.9,100,22,1,0.45,0.45,100,0.19,0,2,0.4,0,7]
[7,11.4,100,22,50,0.51,0.42,100,0.19,1,98,0.4,0,7]
[7,15.8,100,22,99,1.03,0.35,100,0.19,1,100,0.4,0,7]
[7,11.2,100,22,80,0.97,0.44,200,0.19,1,99,0.8,0,23]
[7,9.5,100,22,70,0.88,0.46,300,0.19,1,99,1.2,0,47]
[7,11.9,100,23,50,0.56999999999999995,0.44,100,0.19,1,98,0.4,0,7]
[7,9.1999999999999993,100,23,1,0.5,0.5,200,0.19,0,2,0.8,0,23]
[7,12.1,100,23,90,1.2,0.46,200,0.19,1,100,0.8,0,23]
[7,9.8000000000000007,100,23,70,0.96,0.49,300,0.19,1,99,1.2,0,47]
[7,13.4,100,24,60,0.74,0.45,100,0.19,1,99,0.4,0,7]
[7,9.3000000000000007,100,24,1,0.53,0.53,200,0.19,0,2,0.8,0,23]
[7,12.6,100,24,90,1.3,0.49,200,0.19,1,100,0.8,0,23]
[7,10.4,100,24,80,1.2,0.51,300,0.19,1,99,1.2,0,47]
[7,14,100,25,60,0.81,0.47,100,0.19,1,99,0.4,0,7]
[7,15.1,100,25,70,0.94,0.45,100,0.19,1,99,0.4,0,7]
[7,10.5,100,25,50,0.81,0.54,200,0.19,1,98,0.8,0,23]
[7,13.6,100,25,99,1.53,0.5,200,0.19,1,100,0.8,0,23]
[7,11.1,100,25,90,1.45,0.53,300,0.19,1,100,1.2,0,47]
[7,15.7,100,26,70,1.02,0.47,100,0.19,1,99,0.4,0,7]
[7,10.8,100,26,50,0.88,0.56999999999999995,200,0.19,1,98,0.8,0,23]
[7,8.6999999999999993,100,26,1,0.6,0.6,300,0.19,0,3,1.2,0,47]
[7,11.5,100,26,90,1.56,0.56000000000000005,300,0.19,1,100,1.2,0,47]
[7,17.600000000000001,100,27,80,1.23,0.48,100,0.19,1,99,0.4,0,7]
[7,11.8,100,27,60,1.1200000000000001,0.59,200,0.19,1,98,0.8,0,23]
[7,8.8000000000000007,100,27,1,0.63,0.63,300,0.19,0,3,1.2,0,47]
[7,12.2,100,27,99,1.83,0.57999999999999996,300,0.19,1,100,1.2,0,47]
[7,15.2,170,21,80,0.95,0.46,100,0.33,1,98,0.4,0,7]
[7,16.2,170,21,90,1.07,0.43,100,0.33,1,99,0.4,0,7]
[7,11.8,170,21,70,1.1100000000000001,0.62,200,0.33,1,97,0.8,0,23]
[7,9.4,170,21,50,0.84,0.69,300,0.33,1,95,1.2,0,47]
[7,12.6,170,22,1,0.66,0.66,100,0.33,1,2,0.4,0,7]
[7,17.100000000000001,170,22,90,1.17,0.45,100,0.33,1,99,0.4,0,7]
[7,12.3,170,22,70,1.23,0.66,200,0.33,1,97,0.8,0,23]
[7,10.3,170,22,60,1.1399999999999999,0.72,300,0.33,1,96,1.2,0,47]
[7,13,170,23,1,0.7,0.7,100,0.33,1,2,0.4,0,7]
[7,19,170,23,99,1.39,0.43,100,0.33,1,100,0.4,0,7]
[7,13.6,170,23,80,1.54,0.67,200,0.33,1,98,0.8,0,23]
[7,10.6,170,23,60,1.26,0.76,300,0.33,1,96,1.2,0,47]
[7,13.8,170,24,50,0.79,0.66,100,0.33,1,95,0.4,0,7]
[7,19.899999999999999,170,24,99,1.5,0.45,100,0.33,1,100,0.4,0,7]
[7,14.2,170,24,80,1.67,0.71,200,0.33,1,98,0.8,0,23]
[7,15,170,24,90,1.87,0.68,200,0.33,1,99,0.8,0,23]
[7,11.6,170,24,70,1.6,0.78,300,0.33,1,97,1.2,0,47]
[7,15.8,170,25,60,1.03,0.64,100,0.33,1,96,0.4,0,7]
[7,10.8,170,25,1,0.88,0.88,200,0.33,1,2,0.8,0,23]
[7,15.7,170,25,90,2.0299999999999998,0.72,200,0.33,1,99,0.8,0,23]
[7,12.6,170,25,80,1.97,0.81,300,0.33,1,98,1.2,0,47]
[7,16.600000000000001,170,26,60,1.1100000000000001,0.67,100,0.33,1,96,0.4,0,7]
[7,12.5,170,26,50,1.28,0.85,200,0.33,1,95,0.8,0,23]
[7,17.2,170,26,99,2.39,0.72,200,0.33,1,100,0.8,0,23]
[7,13.1,170,26,80,2.13,0.84,300,0.33,1,98,1.2,0,47]
[7,18.8,170,27,70,1.37,0.64,100,0.33,1,97,0.4,0,7]
[7,12.9,170,27,50,1.39,0.89,200,0.33,1,95,0.8,0,23]
[7,18,170,27,99,2.56,0.75,200,0.33,1,100,0.8,0,23]
[7,9.9,170,27,1,1,1,300,0.33,1,3,1.2,0,47]
[7,14.3,170,27,90,2.5499999999999998,0.86,300,0.33,1,99,1.2,0,47]
[7,16,240,21,80,1.05,0.53,100,0.46,3,97,0.4,0,7]
[7,11.9,240,21,60,1.1399999999999999,0.8,200,0.46,3,94,0.8,0,23]
[7,9.6,240,21,1,0.93,0.93,300,0.46,2,2,1.2,0,47]
[7,13.2,240,21,99,2.1800000000000002,0.76,300,0.46,3,100,1.2,0,47]
[7,16.8,240,22,80,1.1499999999999999,0.56000000000000005,100,0.46,3,97,0.4,0,7]
[7,13.3,240,22,70,1.48,0.81,200,0.46,3,96,0.8,0,23]
[7,10.4,240,22,50,1.18,0.94,300,0.46,3,92,1.2,0,47]
[7,13.8,240,22,99,2.38,0.8,300,0.46,3,100,1.2,0,47]
[7,19,240,23,90,1.39,0.52,100,0.46,3,99,0.4,0,7]
[7,14,240,23,70,1.62,0.85,200,0.46,3,96,0.8,0,23]
[7,10.8,240,23,50,1.31,1,300,0.46,3,92,1.2,0,47]
[7,11.5,240,23,60,1.57,0.97,300,0.46,3,94,1.2,0,47]
[7,14.8,240,24,1,0.9,0.9,100,0.46,2,2,0.4,0,7]
[7,21.1,240,24,99,1.64,0.48,100,0.46,3,100,0.4,0,7]
[7,15.6,240,24,80,2.0099999999999998,0.85,200,0.46,3,97,0.8,0,23]
[7,11.9,240,24,60,1.73,1.02,300,0.46,3,94,1.2,0,47]
[7,15.3,240,25,50,0.96,0.85,100,0.46,3,92,0.4,0,7]
[7,22.1,240,25,99,1.76,0.49,100,0.46,3,100,0.4,0,7]
[7,16.3,240,25,80,2.1800000000000002,0.88,200,0.46,3,97,0.8,0,23]
[7,13.2,240,25,70,2.1800000000000002,1.03,300,0.46,3,95,1.2,0,47]
[7,16,240,26,50,1.05,0.88,100,0.46,3,92,0.4,0,7]
[7,12.1,240,26,1,1.19,1.19,200,0.46,2,2,0.8,0,23]
[7,18.2,240,26,90,2.61,0.87,200,0.46,3,99,0.8,0,23]
[7,13.7,240,26,70,2.36,1.08,300,0.46,3,95,1.2,0,47]
[7,14.6,240,26,80,2.67,1.05,300,0.46,3,97,1.2,0,47]
[7,18.3,240,27,60,1.32,0.83,100,0.46,3,94,0.4,0,7]
[7,14.2,240,27,50,1.67,1.1100000000000001,200,0.46,3,92,0.8,0,23]
[7,20.100000000000001,240,27,99,3.05,0.86,200,0.46,3,100,0.8,0,23]
[7,15.2,240,27,80,2.87,1.0900000000000001,300,0.46,3,97,1.2,0,47]
[7,15.3,310,21,70,0.96,0.66,100,0.6,4,95,0.4,0,7]
[7,11.5,310,21,50,1.04,0.98,200,0.6,4,89,0.8,0,23]
[7,16.2,310,21,99,2.14,0.71,200,0.6,4,100,0.8,0,23]
[7,13.5,310,21,90,2.2799999999999998,0.89,300,0.6,4,98,1.2,0,47]
[7,16.100000000000001,310,22,70,1.06,0.69,100,0.6,4,95,0.4,0,7]
[7,13.1,310,22,60,1.41,0.98,200,0.6,4,92,0.8,0,23]
[7,10.4,310,22,1,1.19,1.19,300,0.6,3,2,1.2,0,47]
[7,14.1,310,22,90,2.4900000000000002,0.94,300,0.6,4,98,1.2,0,47]
[7,14.9,310,22,99,2.74,0.91,300,0.6,4,100,1.2,0,47]
[7,18.3,310,23,80,1.31,0.64,100,0.6,4,97,0.4,0,7]
[7,14.8,310,23,70,1.81,0.97,200,0.6,4,94,0.8,0,23]
[7,11.3,310,23,50,1.52,1.18,300,0.6,4,89,1.2,0,47]
[7,15.5,310,23,99,2.98,0.95,300,0.6,4,100,1.2,0,46]
[7,20.5,310,24,90,1.57,0.56999999999999995,100,0.6,4,98,0.4,0,7]
[7,15.5,310,24,70,1.97,1.01,200,0.6,4,94,0.8,0,23]
[7,11.8,310,24,50,1.68,1.24,300,0.6,4,89,1.2,0,47]
[7,16.3,310,25,1,1.08,1.08,100,0.6,3,1,0.4,0,7]
[7,21.5,310,25,90,1.69,0.59,100,0.6,4,98,0.4,0,7]
[7,17.399999999999999,310,25,80,2.42,0.99,200,0.6,4,96,0.8,0,23]
[7,13.2,310,25,60,2.1800000000000002,1.25,300,0.6,4,92,1.2,0,47]
[7,16.8,310,26,1,1.1399999999999999,1.1399999999999999,100,0.6,3,1,0.4,0,7]
[7,16.5,310,26,50,1.1000000000000001,1.01,100,0.6,4,90,0.4,0,7]
[7,23.8,310,26,99,1.95,0.51,100,0.6,4,100,0.4,0,7]
[7,18.2,310,26,80,2.61,1.03,200,0.6,4,96,0.8,0,23]
[7,14.8,310,26,70,2.72,1.25,300,0.6,4,94,1.2,0,47]
[7,17.3,310,27,50,1.19,1.05,100,0.6,4,90,0.4,0,7]
[7,13.3,310,27,1,1.48,1.48,200,0.6,3,2,0.8,0,23]
[7,20.399999999999999,310,27,90,3.1,0.99,200,0.6,4,98,0.8,0,23]
[7,15.4,310,27,70,2.93,1.3,300,0.6,4,94,1.2,0,46]
[7,14.8,380,21,60,0.91,0.91,100,0.74,4,95,0.4,0,7]
[7,12,380,21,1,1.17,1.17,200,0.74,4,1,0.8,0,23]
[7,16.899999999999999,380,21,99,2.2999999999999998,0.75,200,0.74,6,100,0.8,0,23]
[7,13.4,380,21,80,2.2200000000000002,1.03,300,0.74,6,95,1.2,0,47]
[7,15.1,380,22,60,0.94,0.87,100,0.74,6,91,0.4,0,7]
[7,16.399999999999999,380,22,70,1.1000000000000001,0.76,100,0.74,6,93,0.4,0,7]
[7,12.4,380,22,50,1.27,1.17,200,0.74,6,87,0.8,0,23]
[7,17.7,380,22,99,2.5,0.79,200,0.74,6,100,0.8,0,23]
[7,14.9,380,22,90,2.75,1.04,300,0.74,6,98,1.2,0,47]
[7,17.3,380,23,70,1.2,0.79,100,0.74,6,93,0.4,0,7]
[7,14.2,380,23,60,1.68,1.1499999999999999,200,0.74,6,90,0.8,0,23]
[7,11.1,380,23,1,1.45,1.45,300,0.74,4,2,1.2,0,47]
[7,15.6,380,23,90,2.99,1.0900000000000001,300,0.74,6,98,1.2,0,46]
[7,19.600000000000001,380,24,80,1.46,0.71,100,0.74,6,96,0.4,0,7]
[7,14.9,380,24,60,1.84,1.2,200,0.74,6,90,0.8,0,23]
[7,11.4,380,24,1,1.53,1.53,300,0.74,4,2,1.2,0,47]
[7,17.2,380,24,99,3.55,1.08,300,0.74,6,100,1.2,0,46]
[7,20.5,380,25,80,1.57,0.73,100,0.74,6,96,0.4,0,7]
[7,21.9,380,25,90,1.73,0.61,100,0.74,6,98,0.4,0,7]
[7,16.899999999999999,380,25,70,2.2999999999999998,1.1599999999999999,200,0.74,6,93,0.8,0,23]
[7,12.8,380,25,50,2.0299999999999998,1.48,300,0.74,6,87,1.2,0,47]
[7,17.7,380,26,1,1.24,1.24,100,0.74,4,1,0.4,0,7]
[7,22.9,380,26,90,1.85,0.63,100,0.74,6,98,0.4,0,7]
[7,19,380,26,80,2.79,1.1100000000000001,200,0.74,6,96,0.8,0,23]
[7,14.5,380,26,60,2.61,1.46,300,0.74,6,90,1.2,0,47]
[7,18.3,380,27,1,1.31,1.31,100,0.74,4,1,0.4,0,7]
[7,25.2,380,27,99,2.12,0.53,100,0.74,6,100,0.4,0,7]
[7,19.899999999999999,380,27,80,3,1.1399999999999999,200,0.74,6,96,0.8,0,23]
[7,15.1,380,27,60,2.82,1.52,300,0.74,6,90,1.2,0,47]
[8,11.4,100,21,50,0.4,0.37,100,0.19,1,98,0.4,0,7]
[8,15.6,100,21,99,0.88,0.3,100,0.19,1,100,0.4,0,7]
[8,9.8000000000000007,100,21,1,0.41,0.41,200,0.19,0,2,0.8,0,23]
[8,12,100,21,90,0.94,0.38,200,0.19,1,100,0.8,0,23]
[8,10.1,100,21,70,0.73,0.4,300,0.19,1,99,1.2,0,47]
[8,12.8,100,22,60,0.56000000000000005,0.38,100,0.19,1,99,0.4,0,7]
[8,9.9,100,22,1,0.44,0.44,200,0.19,0,2,0.8,0,23]
[8,12.9,100,22,99,1.1399999999999999,0.4,200,0.19,1,100,0.8,0,23]
[8,10.7,100,22,80,0.94,0.43,300,0.19,1,99,1.2,0,47]
[8,13.3,100,23,60,0.62,0.4,100,0.19,1,99,0.4,0,7]
[8,10.6,100,23,50,0.6,0.46,200,0.19,1,98,0.8,0,23]
[8,13.4,100,23,99,1.25,0.42,200,0.19,1,100,0.8,0,23]
[8,11,100,23,80,1.03,0.45,300,0.19,1,99,1.2,0,47]
[8,14.9,100,24,70,0.81,0.41,100,0.19,1,99,0.4,0,7]
[8,10.9,100,24,50,0.67,0.48,200,0.19,1,98,0.8,0,23]
[8,11.5,100,24,60,0.81,0.48,200,0.19,1,98,0.8,0,23]
[8,9.5,100,24,1,0.51,0.51,300,0.19,0,2,1.2,0,47]
[8,11.7,100,24,90,1.28,0.48,300,0.19,1,100,1.2,0,47]
[8,16.600000000000001,100,25,80,1,0.41,100,0.19,1,99,0.4,0,7]
[8,11.8,100,25,60,0.89,0.5,200,0.19,1,98,0.8,0,23]
[8,9.5,100,25,1,0.54,0.54,300,0.19,0,2,1.2,0,47]
[8,12.4,100,25,99,1.52,0.5,300,0.19,1,100,1.2,0,47]
[8,17.3,100,26,80,1.0900000000000001,0.43,100,0.19,1,99,0.4,0,7]
[8,12.8,100,26,70,1.1299999999999999,0.52,200,0.19,1,99,0.8,0,23]
[8,10.4,100,26,50,0.84,0.55000000000000004,300,0.19,1,98,1.2,0,47]
[8,12.7,100,26,99,1.64,0.53,300,0.19,1,100,1.2,0,47]
[8,19.3,100,27,90,1.31,0.43,100,0.19,1,100,0.4,0,7]
[8,13.2,100,27,70,1.22,0.55000000000000004,200,0.19,1,99,0.8,0,23]
[8,14,100,27,80,1.39,0.54,200,0.19,1,99,0.8,0,23]
[8,11.1,100,27,60,1.0900000000000001,0.56999999999999995,300,0.19,1,98,1.2,0,47]
[8,12.9,170,21,1,0.56999999999999995,0.56999999999999995,100,0.33,1,2,0.4,0,7]
[8,17.5,170,21,99,1.1000000000000001,0.36,100,0.33,1,100,0.4,0,7]
[8,13.1,170,21,80,1.18,0.56000000000000005,200,0.33,1,98,0.8,0,23]
[8,10.6,170,21,60,0.92,0.63,300,0.33,1,96,1.2,0,47]
[8,13.2,170,22,50,0.61,0.61,100,0.33,1,100,0.4,0,7]
[8,18.399999999999999,170,22,99,1.21,0.39,100,0.33,1,100,0.4,0,7]
[8,14.4,170,22,90,1.49,0.56999999999999995,200,0.33,1,99,0.8,0,23]
[8,11.5,170,22,70,1.23,0.66,300,0.33,1,97,1.2,0,47]
[8,13.5,170,23,50,0.65,0.6,100,0.33,1,95,0.4,0,7]
[8,11.2,170,23,1,0.74,0.74,200,0.33,1,2,0.8,0,23]
[8,15,170,23,90,1.63,0.61,200,0.33,1,99,0.8,0,23]
[8,15.7,170,23,99,1.8,0.59,200,0.33,1,100,0.8,0,23]
[8,12.5,170,23,80,1.57,0.68,300,0.33,1,98,1.2,0,47]
[8,15.4,170,24,60,0.87,0.59,100,0.33,1,96,0.4,0,7]
[8,12.2,170,24,50,0.97,0.73,200,0.33,1,95,0.8,0,23]
[8,16.399999999999999,170,24,99,1.95,0.62,200,0.33,1,100,0.8,0,23]
[8,12.9,170,24,80,1.72,0.72,300,0.33,1,98,1.2,0,47]
[8,17.5,170,25,70,1.1000000000000001,0.56999999999999995,100,0.33,1,97,0.4,0,7]
[8,12.6,170,25,50,1.07,0.77,200,0.33,1,95,0.8,0,23]
[8,10.4,170,25,1,0.85,0.85,300,0.33,1,2,1.2,0,47]
[8,14,170,25,90,2.1,0.75,300,0.33,1,99,1.2,0,47]
[8,18.3,170,26,70,1.2,0.59,100,0.33,1,97,0.4,0,7]
[8,14,170,26,60,1.41,0.78,200,0.33,1,96,0.8,0,23]
[8,10.6,170,26,1,0.9,0.9,300,0.33,1,2,1.2,0,47]
[8,14.5,170,26,90,2.27,0.78,300,0.33,1,99,1.2,0,46]
[8,15.1,170,26,99,2.5,0.77,300,0.33,1,100,1.2,0,46]
[8,20.5,170,27,80,1.46,0.56999999999999995,100,0.33,1,98,0.4,0,7]
[8,15.6,170,27,70,1.77,0.79,200,0.33,1,97,0.8,0,23]
[8,12,170,27,50,1.4,0.9,300,0.33,1,95,1.2,0,47]
[8,15.7,170,27,99,2.68,0.8,300,0.33,1,100,1.2,0,46]
[8,17.399999999999999,240,21,90,1.0900000000000001,0.44,100,0.46,3,99,0.4,0,7]
[8,13.2,240,21,70,1.22,0.71,200,0.46,3,96,0.8,0,23]
[8,11.3,240,21,60,1.1499999999999999,0.8,300,0.46,3,94,1.2,0,47]
[8,14.4,240,22,1,0.75,0.75,100,0.46,2,1,0.4,0,7]
[8,18.3,240,22,90,1.2,0.46,100,0.46,3,99,0.4,0,7]
[8,14.7,240,22,80,1.57,0.72,200,0.46,3,97,0.8,0,23]
[8,11.7,240,22,60,1.3,0.86,300,0.46,3,94,1.2,0,47]
[8,14.9,240,23,1,0.8,0.8,100,0.46,2,1,0.4,0,7]
[8,14.8,240,23,50,0.8,0.8,100,0.46,2,94,0.4,0,7]
[8,20.3,240,23,99,1.43,0.43,100,0.46,3,100,0.4,0,7]
[8,16.399999999999999,240,23,90,1.95,0.72,200,0.46,3,99,0.8,0,23]
[8,12.9,240,23,70,1.7,0.88,300,0.46,3,95,1.2,0,47]
[8,15.3,240,24,50,0.85,0.85,100,0.46,2,99,0.4,0,7]
[8,12.3,240,24,1,1.01,1.01,200,0.46,2,2,0.8,0,23]
[8,17.100000000000001,240,24,90,2.12,0.75,200,0.46,3,99,0.8,0,23]
[8,13.4,240,24,70,1.87,0.93,300,0.46,3,95,1.2,0,47]
[8,17,240,25,60,1.04,0.74,100,0.46,3,94,0.4,0,7]
[8,12.6,240,25,1,1.07,1.07,200,0.46,2,2,0.8,0,23]
[8,18.899999999999999,240,25,99,2.5299999999999998,0.75,200,0.46,3,100,0.8,0,23]
[8,14.7,240,25,80,2.33,0.95,300,0.46,3,97,1.2,0,46]
[8,17.8,240,26,60,1.1399999999999999,0.77,100,0.46,3,94,0.4,0,7]
[8,19.2,240,26,70,1.31,0.69,100,0.46,3,96,0.4,0,7]
[8,14.1,240,26,50,1.42,1.02,200,0.46,3,92,0.8,0,23]
[8,11.4,240,26,1,1.18,1.18,300,0.46,2,2,1.2,0,47]
[8,16.100000000000001,240,26,90,2.84,0.96,300,0.46,3,99,1.2,0,46]
[8,20.100000000000001,240,27,70,1.41,0.71,100,0.46,3,96,0.4,0,7]
[8,15.9,240,27,60,1.83,1.01,200,0.46,3,94,0.8,0,23]
[8,11.6,240,27,1,1.24,1.24,300,0.46,2,2,1.2,0,47]
[8,16.8,240,27,90,3.06,1,300,0.46,3,99,1.2,0,46]
[8,16.7,310,21,80,1.01,0.55000000000000004,100,0.6,4,97,0.4,0,7]
[8,12.9,310,21,60,1.1399999999999999,0.87,200,0.6,4,92,0.8,0,23]
[8,11,310,21,50,1.06,0.99,300,0.6,4,89,1.2,0,47]
[8,14.7,310,21,99,2.36,0.79,300,0.6,4,100,1.2,0,46]
[8,17.600000000000001,310,22,80,1.1100000000000001,0.57999999999999996,100,0.6,4,97,0.4,0,7]
[8,18.8,310,22,90,1.25,0.5,100,0.6,4,98,0.4,0,7]
[8,14.5,310,22,70,1.51,0.87,200,0.6,4,94,0.8,0,23]
[8,12.3,310,22,60,1.49,1.01,300,0.6,4,92,1.2,0,47]
[8,15.8,310,23,1,0.9,0.9,100,0.6,3,1,0.4,0,7]
[8,19.7,310,23,90,1.37,0.52,100,0.6,4,98,0.4,0,7]
[8,16.3,310,23,80,1.92,0.85,200,0.6,4,96,0.8,0,23]
[8,12.8,310,23,60,1.66,1.07,300,0.6,4,92,1.2,0,47]
[8,16.3,310,24,1,0.96,0.96,100,0.6,3,1,0.4,0,7]
[8,21.9,310,24,99,1.61,0.46,100,0.6,4,100,0.4,0,7]
[8,17,310,24,80,2.1,0.89,200,0.6,4,96,0.8,0,23]
[8,14.2,310,24,70,2.16,1.08,300,0.6,4,94,1.2,0,47]
[8,16.8,310,25,50,1.02,1.02,100,0.6,3,94,0.4,0,7]
[8,22.9,310,25,99,1.73,0.47,100,0.6,4,100,0.4,0,7]
[8,13.4,310,25,1,1.26,1.26,200,0.6,3,2,0.8,0,23]
[8,19,310,25,90,2.5499999999999998,0.87,200,0.6,4,98,0.8,0,23]
[8,14.7,310,25,70,2.35,1.1399999999999999,300,0.6,4,94,1.2,0,46]
[8,18.3,310,26,60,1.19,0.88,100,0.6,4,92,0.4,0,7]
[8,13.7,310,26,1,1.33,1.33,200,0.6,3,2,0.8,0,23]
[8,20.9,310,26,99,3.01,0.84,200,0.6,4,100,0.8,0,22]
[8,16.3,310,26,80,2.91,1.1299999999999999,300,0.6,4,96,1.2,0,46]
[8,19.100000000000001,310,27,60,1.29,0.9,100,0.6,4,93,0.4,0,7]
[8,15.4,310,27,50,1.73,1.24,200,0.6,4,89,0.8,0,23]
[8,21.9,310,27,99,3.23,0.87,200,0.6,4,100,0.8,0,22]
[8,18.100000000000001,310,27,90,3.52,1.1299999999999999,300,0.6,4,98,1.2,0,46]
[8,15.7,380,21,70,0.9,0.7,100,0.74,6,93,0.4,0,7]
[8,12.7,380,21,50,1.0900000000000001,1.0900000000000001,200,0.74,4,87,0.8,0,23]
[8,13.3,380,21,60,1.22,0.98,200,0.74,6,90,0.8,0,23]
[8,11.4,380,21,1,1.18,1.18,300,0.74,4,1,1.2,0,47]
[8,14.7,380,21,90,2.33,0.91,300,0.74,6,98,1.2,0,46]
[8,17.899999999999999,380,22,80,1.1499999999999999,0.62,100,0.74,6,96,0.4,0,7]
[8,13.9,380,22,60,1.38,1.04,200,0.74,6,90,0.8,0,23]
[8,11.8,380,22,50,1.34,1.21,300,0.74,6,87,1.2,0,47]
[8,16.100000000000001,380,22,99,2.84,0.92,300,0.74,6,100,1.2,0,46]
[8,18.8,380,23,80,1.25,0.65,100,0.74,6,96,0.4,0,7]
[8,15.7,380,23,70,1.8,1.01,200,0.74,6,93,0.8,0,23]
[8,12.3,380,23,50,1.51,1.27,300,0.74,6,87,1.2,0,47]
[8,16.899999999999999,380,23,99,3.1,0.96,300,0.74,6,100,1.2,0,46]
[8,21,380,24,90,1.52,0.56000000000000005,100,0.74,6,98,0.4,0,7]
[8,16.5,380,24,70,1.97,1.06,200,0.74,6,93,0.8,0,23]
[8,17.7,380,24,80,2.25,0.97,200,0.74,6,96,0.8,0,23]
[8,13.8,380,24,60,2.0299999999999998,1.27,300,0.74,6,90,1.2,0,47]
[8,17.600000000000001,380,25,1,1.1200000000000001,1.1200000000000001,100,0.74,4,1,0.4,0,7]
[8,23.3,380,25,99,1.77,0.48,100,0.74,6,100,0.4,0,7]
[8,18.5,380,25,80,2.44,1.01,200,0.74,6,96,0.8,0,23]
[8,15.4,380,25,70,2.59,1.26,300,0.74,6,93,1.2,0,46]
[8,18.100000000000001,380,26,50,1.18,1.18,100,0.74,4,90,0.4,0,7]
[8,24.3,380,26,99,1.89,0.49,100,0.74,6,100,0.4,0,7]
[8,20.6,380,26,90,2.94,0.95,200,0.74,6,98,0.8,0,22]
[8,16.100000000000001,380,26,70,2.82,1.32,300,0.74,6,93,1.2,0,46]
[8,18.7,380,27,50,1.24,1.24,100,0.74,4,93,0.4,0,7]
[8,14.8,380,27,1,1.59,1.59,200,0.74,4,2,0.8,0,23]
[8,21.5,380,27,90,3.15,0.99,200,0.74,6,98,0.8,0,22]
[8,22.8,380,27,99,3.43,0.9,200,0.74,6,100,0.8,0,22]
[8,17.899999999999999,380,27,80,3.46,1.3,300,0.74,6,95,1.2,0,46]
[9,12.8,100,21,60,0.44,0.33,100,0.19,1,99,0.4,0,7]
[9,10.7,100,21,50,0.4,0.37,200,0.19,1,98,0.8,0,23]
[9,13.2,100,21,99,0.98,0.34,200,0.19,1,100,0.8,0,23]
[9,11.6,100,21,90,0.91,0.36,300,0.19,1,100,1.2,0,47]
[9,14.2,100,22,70,0.6,0.34,100,0.19,1,99,0.4,0,7]
[9,11,100,22,50,0.47,0.4,200,0.19,1,98,0.8,0,23]
[9,10.199999999999999,100,22,1,0.42,0.42,300,0.19,0,2,1.2,0,47]
[9,11.9,100,22,90,1,0.39,300,0.19,1,100,1.2,0,47]
[9,14.8,100,23,70,0.67,0.36,100,0.19,1,99,0.4,0,7]
[9,11.9,100,23,60,0.67,0.42,200,0.19,1,99,0.8,0,23]
[9,10.3,100,23,1,0.45,0.45,300,0.19,0,2,1.2,0,47]
[9,10.6,100,23,50,0.56000000000000005,0.44,300,0.19,1,98,1.2,0,47]
[9,12.5,100,23,99,1.23,0.42,300,0.19,1,100,1.2,0,47]
[9,16.399999999999999,100,24,80,0.86,0.37,100,0.19,1,99,0.4,0,7]
[9,12.8,100,24,70,0.88,0.44,200,0.19,1,99,0.8,0,23]
[9,10.8,100,24,50,0.63,0.47,300,0.19,1,98,1.2,0,47]
[9,12.8,100,24,99,1.34,0.44,300,0.19,1,100,1.2,0,47]
[9,18.2,100,25,90,1.07,0.37,100,0.19,1,100,0.4,0,7]
[9,13.2,100,25,70,0.97,0.47,200,0.19,1,99,0.8,0,23]
[9,11.4,100,25,60,0.86,0.49,300,0.19,1,98,1.2,0,47]
[9,13.4,100,26,1,0.51,0.51,100,0.19,0,2,0.4,0,7]
[9,18.899999999999999,100,26,90,1.1599999999999999,0.39,100,0.19,1,100,0.4,0,7]
[9,14.2,100,26,80,1.22,0.49,200,0.19,1,99,0.8,0,23]
[9,11.7,100,26,60,0.94,0.52,300,0.19,1,98,1.2,0,47]
[9,12.2,100,26,70,1.1000000000000001,0.51,300,0.19,1,99,1.2,0,47]
[9,15,100,27,50,0.7,0.48,100,0.19,1,98,0.4,0,7]
[9,20.8,100,27,99,1.37,0.39,100,0.19,1,100,0.4,0,7]
[9,15.4,100,27,90,1.49,0.5,200,0.19,1,100,0.8,0,23]
[9,12.4,100,27,70,1.2,0.54,300,0.19,1,99,1.2,0,47]
[9,13.5,170,21,50,0.52,0.52,100,0.33,1,91,0.4,0,7]
[9,11.5,170,21,1,0.59,0.59,200,0.33,1,2,0.8,0,23]
[9,14.4,170,21,90,1.25,0.5,200,0.33,1,99,0.8,0,23]
[9,12.4,170,21,80,1.18,0.56000000000000005,300,0.33,1,98,1.2,0,47]
[9,14.4,170,22,60,0.63,0.5,100,0.33,1,96,0.4,0,7]
[9,11.7,170,22,1,0.64,0.64,200,0.33,1,2,0.8,0,23]
[9,15.7,170,22,99,1.55,0.51,200,0.33,1,100,0.8,0,23]
[9,12.8,170,22,80,1.32,0.6,300,0.33,1,98,1.2,0,47]
[9,13.3,170,22,90,1.52,0.57999999999999996,300,0.33,1,99,1.2,0,46]
[9,16.3,170,23,70,0.84,0.49,100,0.33,1,97,0.4,0,7]
[9,12.3,170,23,50,0.77,0.65,200,0.33,1,95,0.8,0,23]
[9,11,170,23,1,0.71,0.71,300,0.33,1,2,1.2,0,47]
[9,13.8,170,23,90,1.67,0.62,300,0.33,1,99,1.2,0,46]
[9,17,170,24,70,0.93,0.52,100,0.33,1,97,0.4,0,7]
[9,13.6,170,24,60,1.07,0.67,200,0.33,1,96,0.8,0,23]
[9,11.2,170,24,1,0.76,0.76,300,0.33,1,2,1.2,0,47]
[9,14.8,170,24,99,2.0299999999999998,0.65,300,0.33,1,100,1.2,0,46]
[9,19.100000000000001,170,25,80,1.17,0.5,100,0.33,1,98,0.4,0,7]
[9,14.1,170,25,60,1.19,0.71,200,0.33,1,96,0.8,0,23]
[9,12,170,25,50,1.06,0.77,300,0.33,1,95,1.2,0,47]
[9,15.3,170,25,99,2.2000000000000002,0.69,300,0.33,1,100,1.2,0,46]
[9,19.899999999999999,170,26,80,1.27,0.52,100,0.33,1,98,0.4,0,7]
[9,21.3,170,26,90,1.43,0.47,100,0.33,1,99,0.4,0,7]
[9,15.6,170,26,70,1.53,0.72,200,0.33,1,97,0.8,0,23]
[9,13.1,170,26,60,1.42,0.79,300,0.33,1,96,1.2,0,47]
[9,15.8,170,27,1,0.79,0.79,100,0.33,1,2,0.4,0,7]
[9,22.2,170,27,90,1.54,0.49,100,0.33,1,99,0.4,0,7]
[9,17.2,170,27,80,1.9,0.73,200,0.33,1,98,0.8,0,23]
[9,13.5,170,27,60,1.56,0.83,300,0.33,1,96,1.2,0,46]
[9,14.5,240,21,50,0.64,0.64,100,0.46,2,83,0.4,0,7]
[9,18.600000000000001,240,21,99,1.1200000000000001,0.36,100,0.46,3,100,0.4,0,7]
[9,14.6,240,21,80,1.3,0.63,200,0.46,3,97,0.8,0,23]
[9,12.6,240,21,70,1.25,0.72,300,0.46,3,96,1.2,0,47]
[9,14.9,240,22,50,0.69,0.69,100,0.46,2,87,0.4,0,7]
[9,19.600000000000001,240,22,99,1.23,0.38,100,0.46,3,100,0.4,0,7]
[9,12.5,240,22,1,0.82,0.82,200,0.46,2,1,0.8,0,23]
[9,16.100000000000001,240,22,90,1.66,0.63,200,0.46,3,99,0.8,0,23]
[9,13.7,240,22,80,1.65,0.75,300,0.46,3,97,1.2,0,46]
[9,15.7,240,23,60,0.78,0.65,100,0.46,3,94,0.4,0,7]
[9,12.8,240,23,1,0.88,0.88,200,0.46,2,2,0.8,0,23]
[9,17.7,240,23,99,2.0299999999999998,0.63,200,0.46,3,100,0.8,0,23]
[9,14.2,240,23,80,1.83,0.8,300,0.46,3,97,1.2,0,46]
[9,16.399999999999999,240,24,60,0.87,0.68,100,0.46,3,94,0.4,0,7]
[9,13.5,240,24,50,1.05,0.88,200,0.46,3,92,0.8,0,23]
[9,18.5,240,24,99,2.21,0.67,200,0.46,3,100,0.8,0,22]
[9,15.5,240,24,90,2.2799999999999998,0.81,300,0.46,3,99,1.2,0,46]
[9,18.600000000000001,240,25,70,1.1200000000000001,0.64,100,0.46,3,96,0.4,0,7]
[9,14,240,25,50,1.17,0.93,200,0.46,3,92,0.8,0,23]
[9,15.1,240,25,60,1.42,0.88,200,0.46,3,94,0.8,0,23]
[9,12,240,25,1,1.05,1.05,300,0.46,2,2,1.2,0,47]
[9,16.899999999999999,240,25,99,2.74,0.83,300,0.46,3,100,1.2,0,46]
[9,20.9,240,26,80,1.38,0.59,100,0.46,3,97,0.4,0,7]
[9,15.7,240,26,60,1.56,0.92,200,0.46,3,94,0.8,0,23]
[9,13.2,240,26,50,1.47,1.04,300,0.46,3,92,1.2,0,47]
[9,17.5,240,26,99,2.98,0.87,300,0.46,3,100,1.2,0,46]
[9,21.8,240,27,80,1.49,0.61,100,0.46,3,98,0.4,0,7]
[9,17.5,240,27,70,1.99,0.92,200,0.46,3,96,0.8,0,23]
[9,13.6,240,27,50,1.62,1.0900000000000001,300,0.46,3,92,1.2,0,46]
[9,15.2,310,21,1,0.73,0.73,100,0.6,3,1,0.4,0,7]
[9,18,310,21,90,1.05,0.44,100,0.6,4,98,0.4,0,7]
[9,14.3,310,21,70,1.22,0.77,200,0.6,4,94,0.8,0,23]
[9,15.2,310,21,80,1.44,0.71,200,0.6,4,96,0.8,0,23]
[9,12.4,310,21,60,1.17,0.89,300,0.6,4,92,1.2,0,47]
[9,15.7,310,22,50,0.78,0.78,100,0.6,3,81,0.4,0,7]
[9,20,310,22,99,1.28,0.39,100,0.6,4,100,0.4,0,7]
[9,15.9,310,22,80,1.61,0.76,200,0.6,4,96,0.8,0,23]
[9,13.6,310,22,70,1.62,0.91,300,0.6,4,94,1.2,0,46]
[9,16.2,310,23,50,0.84,0.84,100,0.6,3,84,0.4,0,7]
[9,21,310,23,99,1.4,0.41,100,0.6,4,100,0.4,0,7]
[9,17.7,310,23,90,2.02,0.74,200,0.6,4,98,0.8,0,23]
[9,14.2,310,23,70,1.8,0.96,300,0.6,4,94,1.2,0,46]
[9,16.8,310,24,60,0.91,0.78,100,0.6,4,93,0.4,0,7]
[9,13.8,310,24,1,1.1100000000000001,1.1100000000000001,200,0.6,3,2,0.8,0,23]
[9,18.5,310,24,90,2.21,0.78,200,0.6,4,98,0.8,0,22]
[9,19.5,310,24,99,2.44,0.72,200,0.6,4,100,0.8,0,22]
[9,15.6,310,24,80,2.31,0.97,300,0.6,4,96,1.2,0,46]
[9,17.600000000000001,310,25,60,1,0.81,100,0.6,4,93,0.4,0,7]
[9,14.6,310,25,50,1.3,1.0900000000000001,200,0.6,4,90,0.8,0,23]
[9,20.399999999999999,310,25,99,2.65,0.76,200,0.6,4,100,0.8,0,22]
[9,17.2,310,25,90,2.85,0.97,300,0.6,4,98,1.2,0,46]
[9,20,310,26,70,1.27,0.74,100,0.6,4,95,0.4,0,7]
[9,15.2,310,26,50,1.44,1.1399999999999999,200,0.6,4,90,0.8,0,23]
[9,12.8,310,26,1,1.34,1.34,300,0.6,3,2,1.2,0,47]
[9,17.899999999999999,310,26,90,3.09,1.02,300,0.6,4,98,1.2,0,46]
[9,22.4,310,27,80,1.56,0.66,100,0.6,4,97,0.4,0,7]
[9,17.2,310,27,60,1.9,1.1100000000000001,200,0.6,4,92,0.8,0,23]
[9,13.1,310,27,1,1.42,1.42,300,0.6,3,2,1.2,0,47]
[9,14.3,310,27,50,1.87,1.29,300,0.6,4,89,1.2,0,46]
[9,19.5,310,27,99,3.68,1.01,300,0.6,4,100,1.2,0,46]
[9,17.100000000000001,380,21,80,0.95,0.56000000000000005,100,0.74,6,96,0.4,0,7]
[9,14.6,380,21,70,1.31,0.85,200,0.74,6,93,0.8,0,23]
[9,12.1,380,21,50,1.08,1.08,300,0.74,4,86,1.2,0,47]
[9,16.3,380,22,1,0.85,0.85,100,0.74,4,1,0.4,0,7]
[9,19.3,380,22,90,1.19,0.49,100,0.74,6,98,0.4,0,7]
[9,15.3,380,22,70,1.48,0.9,200,0.74,6,93,0.8,0,23]
[9,13.2,380,22,60,1.47,1.08,300,0.74,6,90,1.2,0,47]
[9,16.899999999999999,380,23,1,0.92,0.92,100,0.74,4,1,0.4,0,7]
[9,20.2,380,23,90,1.31,0.51,100,0.74,6,98,0.4,0,7]
[9,17.2,380,23,80,1.91,0.87,200,0.74,6,96,0.8,0,23]
[9,13.8,380,23,60,1.66,1.1399999999999999,300,0.74,6,90,1.2,0,46]
[9,14.7,380,23,70,1.99,1.08,300,0.74,6,93,1.2,0,46]
[9,17.5,380,24,50,0.98,0.98,100,0.74,4,82,0.4,0,7]
[9,22.3,380,24,99,1.55,0.43,100,0.74,6,100,0.4,0,7]
[9,19.2,380,24,90,2.36,0.83,200,0.74,6,98,0.8,0,22]
[9,15.3,380,24,70,2.2000000000000002,1.1399999999999999,300,0.74,6,93,1.2,0,46]
[9,17.899999999999999,380,25,60,1.04,0.91,100,0.74,6,91,0.4,0,7]
[9,14.8,380,25,1,1.34,1.34,200,0.74,4,1,0.8,0,23]
[9,20,380,25,90,2.57,0.87,200,0.74,6,98,0.8,0,22]
[9,16.899999999999999,380,25,80,2.77,1.1299999999999999,300,0.74,6,95,1.2,0,46]
[9,18.7,380,26,60,1.1299999999999999,0.94,100,0.74,6,91,0.4,0,7]
[9,15.1,380,26,1,1.42,1.42,200,0.74,4,1,0.8,0,23]
[9,22.1,380,26,99,3.04,0.82,200,0.74,6,100,0.8,0,22]
[9,17.600000000000001,380,26,80,3.02,1.18,300,0.74,6,95,1.2,0,46]
[9,18.7,380,26,90,3.4,1.1100000000000001,300,0.74,6,98,1.2,0,46]
[9,21.2,380,27,70,1.42,0.84,100,0.74,6,94,0.4,0,7]
[9,16.3,380,27,50,1.7,1.34,200,0.74,6,87,0.8,0,23]
[9,13.6,380,27,1,1.62,1.62,300,0.74,4,2,1.2,0,46]
[9,19.5,380,27,90,3.67,1.1599999999999999,300,0.74,6,98,1.2,0,46]
[10,14.9,100,21,80,0.56999999999999995,0.28000000000000003,100,0.19,1,99,0.4,0,7]
[10,11.9,100,21,60,0.45,0.34,200,0.19,1,99,0.8,0,23]
[10,11,100,21,1,0.35,0.35,300,0.19,0,2,1.2,0,47]
[10,12.7,100,21,99,0.95,0.33,300,0.19,1,100,1.2,0,46]
[10,15.6,100,22,80,0.65,0.3,100,0.19,1,99,0.4,0,7]
[10,12.3,100,22,60,0.52,0.37,200,0.19,1,99,0.8,0,23]
[10,11.2,100,22,50,0.42,0.38,300,0.19,1,98,1.2,0,47]
[10,13,100,22,99,1.05,0.36,300,0.19,1,100,1.2,0,46]
[10,13.4,100,23,1,0.39,0.39,100,0.19,0,2,0.4,0,7]
[10,17.2,100,23,90,0.83,0.31,100,0.19,1,100,0.4,0,7]
[10,13.1,100,23,70,0.73,0.39,200,0.19,1,99,0.8,0,23]
[10,11.8,100,23,60,0.62,0.4,300,0.19,1,99,1.2,0,47]
[10,13.6,100,24,1,0.42,0.42,100,0.19,0,2,0.4,0,7]
[10,17.899999999999999,100,24,90,0.92,0.33,100,0.19,1,100,0.4,0,7]
[10,14.1,100,24,80,0.96,0.41,200,0.19,1,99,0.8,0,23]
[10,12,100,24,60,0.7,0.43,300,0.19,1,99,1.2,0,47]
[10,14.4,100,25,50,0.51,0.41,100,0.19,1,98,0.4,0,7]
[10,19.600000000000001,100,25,99,1.1100000000000001,0.33,100,0.19,1,100,0.4,0,7]
[10,14.5,100,25,80,1.05,0.43,200,0.19,1,99,0.8,0,23]
[10,12.7,100,25,70,0.94,0.45,300,0.19,1,99,1.2,0,46]
[10,14.9,100,26,50,0.56999999999999995,0.44,100,0.19,1,98,0.4,0,7]
[10,16,100,26,60,0.7,0.42,100,0.19,1,99,0.4,0,7]
[10,12.2,100,26,1,0.5,0.5,200,0.19,0,2,0.8,0,23]
[10,15.6,100,26,90,1.31,0.45,200,0.19,1,100,0.8,0,23]
[10,13.4,100,26,80,1.2,0.48,300,0.19,1,99,1.2,0,46]
[10,16.7,100,27,60,0.77,0.44,100,0.19,1,99,0.4,0,7]
[10,12.3,100,27,1,0.53,0.53,200,0.19,0,2,0.8,0,23]
[10,16.7,100,27,99,1.57,0.47,200,0.19,1,100,0.8,0,23]
[10,13.7,100,27,80,1.3,0.5,300,0.19,1,99,1.2,0,46]
[10,15.1,170,21,70,0.6,0.41,100,0.33,1,97,0.4,0,7]
[10,12.3,170,21,50,0.54,0.54,200,0.33,1,92,0.8,0,23]
[10,15.6,170,21,99,1.3,0.44,200,0.33,1,100,0.8,0,23]
[10,13.6,170,21,90,1.26,0.5,300,0.33,1,99,1.2,0,46]
[10,15.8,170,22,70,0.68,0.43,100,0.33,1,97,0.4,0,7]
[10,16.899999999999999,170,22,80,0.81,0.4,100,0.33,1,98,0.4,0,7]
[10,15.5,170,22,90,1.29,0.49,200,0.33,1,99,0.8,0,23]
[10,11.8,170,22,50,0.63,0.59,300,0.33,1,95,1.2,0,47]
[10,14.9,170,23,1,0.56999999999999995,0.56999999999999995,100,0.33,1,1,0.4,0,7]
[10,18.899999999999999,170,23,90,1.03,0.38,100,0.33,1,99,0.4,0,7]
[10,14.5,170,23,70,1.05,0.56999999999999995,200,0.33,1,97,0.8,0,23]
[10,12.7,170,23,60,0.94,0.62,300,0.33,1,96,1.2,0,46]
[10,15.3,170,24,1,0.62,0.62,100,0.33,1,1,0.4,0,7]
[10,20.8,170,24,99,1.26,0.37,100,0.33,1,100,0.4,0,7]
[10,15.9,170,24,80,1.37,0.57999999999999996,200,0.33,1,98,0.8,0,23]
[10,13,170,24,60,1.06,0.67,300,0.33,1,96,1.2,0,46]
[10,15.5,170,25,50,0.64,0.6,100,0.33,1,95,0.4,0,7]
[10,21.7,170,25,99,1.36,0.39,100,0.33,1,100,0.4,0,7]
[10,16.5,170,25,80,1.51,0.62,200,0.33,1,98,0.8,0,23]
[10,17.399999999999999,170,25,90,1.72,0.6,200,0.33,1,99,0.8,0,23]
[10,14.1,170,25,70,1.42,0.69,300,0.33,1,97,1.2,0,46]
[10,17.5,170,26,60,0.88,0.57999999999999996,100,0.33,1,96,0.4,0,7]
[10,13.4,170,26,1,0.78,0.78,200,0.33,1,2,0.8,0,23]
[10,18,170,26,90,1.87,0.63,200,0.33,1,99,0.8,0,22]
[10,15.2,170,26,80,1.81,0.71,300,0.33,1,98,1.2,0,46]
[10,18.3,170,27,60,0.96,0.61,100,0.33,1,97,0.4,0,7]
[10,14.7,170,27,50,1.0900000000000001,0.77,200,0.33,1,95,0.8,0,23]
[10,19.600000000000001,170,27,99,2.2400000000000002,0.64,200,0.33,1,100,0.8,0,22]
[10,15.6,170,27,80,1.97,0.75,300,0.33,1,98,1.2,0,46]
[10,15.6,240,21,70,0.66,0.49,100,0.46,3,96,0.4,0,7]
[10,13,240,21,50,0.69,0.69,200,0.46,2,87,0.8,0,23]
[10,16.7,240,21,99,1.55,0.51,200,0.46,3,100,0.8,0,23]
[10,12.1,240,21,1,0.73,0.73,300,0.46,2,1,1.2,0,47]
[10,14.5,240,21,90,1.57,0.62,300,0.46,3,99,1.2,0,46]
[10,17.600000000000001,240,22,80,0.88,0.46,100,0.46,3,97,0.4,0,7]
[10,13.9,240,22,60,0.9,0.7,200,0.46,3,94,0.8,0,23]
[10,12.3,240,22,1,0.79,0.79,300,0.46,2,2,1.2,0,46]
[10,15.6,240,22,99,1.97,0.64,300,0.46,3,100,1.2,0,46]
[10,18.399999999999999,240,23,80,0.98,0.49,100,0.46,3,97,0.4,0,7]
[10,14.4,240,23,60,1.03,0.74,200,0.46,3,94,0.8,0,23]
[10,12.6,240,23,50,0.92,0.83,300,0.46,3,92,1.2,0,46]
[10,16.2,240,23,99,2.17,0.69,300,0.46,3,100,1.2,0,46]
[10,20.6,240,24,90,1.23,0.45,100,0.46,3,99,0.4,0,7]
[10,16,240,24,70,1.4,0.75,200,0.46,3,96,0.8,0,23]
[10,13,240,24,50,1.05,0.88,300,0.46,3,92,1.2,0,46]
[10,13.8,240,24,60,1.32,0.85,300,0.46,3,94,1.2,0,46]
[10,16.899999999999999,240,25,1,0.8,0.8,100,0.46,2,1,0.4,0,7]
[10,22.7,240,25,99,1.47,0.41,100,0.46,3,100,0.4,0,7]
[10,17.7,240,25,80,1.8,0.74,200,0.46,3,97,0.8,0,22]
[10,14.2,240,25,60,1.48,0.9,300,0.46,3,94,1.2,0,46]
[10,17.3,240,26,50,0.85,0.85,100,0.46,2,98,0.4,0,7]
[10,23.7,240,26,99,1.59,0.42,100,0.46,3,100,0.4,0,7]
[10,18.399999999999999,240,26,80,1.96,0.78,200,0.46,3,97,0.8,0,22]
[10,15.6,240,26,70,1.94,0.92,300,0.46,3,96,1.2,0,46]
[10,17.5,240,27,50,0.87,0.81,100,0.46,3,93,0.4,0,7]
[10,14.6,240,27,1,1.07,1.07,200,0.46,2,2,0.8,0,23]
[10,20.399999999999999,240,27,90,2.41,0.77,200,0.46,3,99,0.8,0,22]
[10,16.100000000000001,240,27,70,2.13,0.97,300,0.46,3,96,1.2,0,46]
[10,17,240,27,80,2.4500000000000002,0.93,300,0.46,3,97,1.2,0,46]
[10,15.7,310,21,60,0.66,0.66,100,0.6,3,90,0.4,0,7]
[10,13.5,310,21,50,0.82,0.82,200,0.6,3,83,0.8,0,23]
[10,17.399999999999999,310,21,99,1.71,0.56000000000000005,200,0.6,4,100,0.8,0,23]
[10,14.4,310,21,80,1.54,0.75,300,0.6,4,96,1.2,0,46]
[10,16.7,310,22,70,0.78,0.6,100,0.6,4,95,0.4,0,7]
[10,13.8,310,22,50,0.89,0.89,200,0.6,3,87,0.8,0,23]
[10,18.2,310,22,99,1.9,0.6,200,0.6,4,100,0.8,0,22]
[10,15.8,310,22,90,2.0099999999999998,0.76,300,0.6,4,98,1.2,0,46]
[10,17.600000000000001,310,23,70,0.88,0.63,100,0.6,4,95,0.4,0,7]
[10,14.9,310,23,60,1.1399999999999999,0.87,200,0.6,4,92,0.8,0,23]
[10,12.9,310,23,1,1.03,1.03,300,0.6,3,1,1.2,0,46]
[10,16.399999999999999,310,23,90,2.23,0.81,300,0.6,4,98,1.2,0,46]
[10,17.100000000000001,310,23,99,2.4900000000000002,0.77,300,0.6,4,100,1.2,0,46]
[10,19.7,310,24,80,1.1299999999999999,0.56999999999999995,100,0.6,4,97,0.4,0,7]
[10,15.5,310,24,60,1.29,0.92,200,0.6,4,92,0.8,0,23]
[10,13.5,310,24,50,1.21,1.05,300,0.6,4,90,1.2,0,46]
[10,17.8,310,24,99,2.73,0.82,300,0.6,4,100,1.2,0,46]
[10,22,310,25,90,1.4,0.5,100,0.6,4,98,0.4,0,7]
[10,17.399999999999999,310,25,70,1.72,0.9,200,0.6,4,94,0.8,0,23]
[10,13.9,310,25,50,1.37,1.1100000000000001,300,0.6,4,90,1.2,0,46]
[10,18.3,310,26,1,0.97,0.97,100,0.6,3,1,0.4,0,7]
[10,23,310,26,90,1.51,0.52,100,0.6,4,98,0.4,0,7]
[10,19.3,310,26,80,2.17,0.87,200,0.6,4,96,0.8,0,22]
[10,15.4,310,26,60,1.88,1.1200000000000001,300,0.6,4,92,1.2,0,46]
[10,18.899999999999999,310,27,1,1.03,1.03,100,0.6,3,1,0.4,0,7]
[10,18.8,310,27,50,1.03,1.03,100,0.6,3,94,0.4,0,7]
[10,25.2,310,27,99,1.77,0.44,100,0.6,4,100,0.4,0,7]
[10,20.100000000000001,310,27,80,2.36,0.91,200,0.6,4,96,0.8,0,22]
[10,17,310,27,70,2.44,1.1200000000000001,300,0.6,4,94,1.2,0,46]
[10,16.2,380,21,50,0.72,0.72,100,0.74,4,71,0.4,0,7]
[10,14,380,21,1,0.93,0.93,200,0.74,4,1,0.8,0,23]
[10,17,380,21,90,1.63,0.65,200,0.74,6,98,0.8,0,23]
[10,14,380,21,70,1.4,0.88,300,0.74,6,93,1.2,0,46]
[10,16.8,380,22,60,0.79,0.79,100,0.74,4,89,0.4,0,7]
[10,14.3,380,22,1,1.01,1.01,200,0.74,4,1,0.8,0,23]
[10,18.7,380,22,99,2.0299999999999998,0.63,200,0.74,6,100,0.8,0,22]
[10,15.5,380,22,80,1.9,0.89,300,0.74,6,96,1.2,0,46]
[10,17.3,380,23,60,0.85,0.85,100,0.74,4,92,0.4,0,7]
[10,17.8,380,23,70,0.91,0.69,100,0.74,6,94,0.4,0,7]
[10,14.7,380,23,50,1.0900000000000001,1.0900000000000001,200,0.74,4,86,0.8,0,23]
[10,19.600000000000001,380,23,99,2.23,0.67,200,0.74,6,100,0.8,0,22]
[10,17,380,23,90,2.4500000000000002,0.89,300,0.74,6,98,1.2,0,46]
[10,18.600000000000001,380,24,70,1.01,0.72,100,0.74,6,94,0.4,0,7]
[10,15.9,380,24,60,1.38,1.03,200,0.74,6,91,0.8,0,23]
[10,13.6,380,24,1,1.27,1.27,300,0.74,4,1,1.2,0,46]
[10,17.7,380,24,90,2.69,0.94,300,0.74,6,98,1.2,0,46]
[10,20.9,380,25,80,1.27,0.63,100,0.74,6,96,0.4,0,7]
[10,16.600000000000001,380,25,60,1.54,1.08,200,0.74,6,91,0.8,0,23]
[10,13.9,380,25,1,1.35,1.35,300,0.74,4,1,1.2,0,46]
[10,19.399999999999999,380,25,99,3.26,0.93,300,0.74,6,100,1.2,0,45]
[10,21.9,380,26,80,1.38,0.66,100,0.74,6,96,0.4,0,7]
[10,23.3,380,26,90,1.54,0.54,100,0.74,6,98,0.4,0,7]
[10,18.7,380,26,70,2.0099999999999998,1.04,200,0.74,6,93,0.8,0,22]
[10,14.8,380,26,50,1.69,1.34,300,0.74,6,87,1.2,0,46]
[10,19.7,380,27,1,1.1200000000000001,1.1200000000000001,100,0.74,4,1,0.4,0,7]
[10,24.3,380,27,90,1.66,0.55000000000000004,100,0.74,6,98,0.4,0,7]
[10,20.8,380,27,80,2.5099999999999998,0.99,200,0.74,6,96,0.8,0,22]
[10,16.5,380,27,60,2.2799999999999998,1.32,300,0.74,6,90,1.2,0,46]
[11,13.6,100,21,1,0.3,0.3,100,0.19,0,1,0.4,0,7]
[11,17,100,21,99,0.7,0.23,100,0.19,1,100,0.4,0,7]
[11,13.6,100,21,80,0.62,0.3,200,0.19,1,99,0.8,0,23]
[11,12.1,100,21,60,0.4,0.31,300,0.19,1,99,1.2,0,46]
[11,13.8,100,22,50,0.33,0.33,100,0.19,0,94,0.4,0,7]
[11,17.7,100,22,99,0.78,0.25,100,0.19,1,100,0.4,0,7]
[11,12.5,100,22,1,0.35,0.35,200,0.19,0,1,0.8,0,23]
[11,14.5,100,22,90,0.83,0.32,200,0.19,1,100,0.8,0,23]
[11,12.7,100,22,70,0.6,0.34,300,0.19,1,99,1.2,0,46]
[11,14.8,100,23,60,0.44,0.33,100,0.19,1,99,0.4,0,7]
[11,12.6,100,23,1,0.38,0.38,200,0.19,0,2,0.8,0,23]
[11,15,100,23,90,0.92,0.35,200,0.19,1,100,0.8,0,23]
[11,13.4,100,23,80,0.82,0.36,300,0.19,1,99,1.2,0,46]
[11,15.4,100,24,60,0.51,0.35,100,0.19,1,99,0.4,0,7]
[11,13,100,24,50,0.47,0.4,200,0.19,1,98,0.8,0,23]
[11,15.9,100,24,99,1.1499999999999999,0.37,200,0.19,1,100,0.8,0,23]
[11,13.6,100,24,80,0.92,0.39,300,0.19,1,99,1.2,0,46]
[11,17,100,25,70,0.7,0.36,100,0.19,1,99,0.4,0,7]
[11,13.3,100,25,50,0.54,0.43,200,0.19,1,98,0.8,0,23]
[11,13.9,100,25,60,0.69,0.42,200,0.19,1,99,0.8,0,23]
[11,12.3,100,25,1,0.44,0.44,300,0.19,0,2,1.2,0,46]
[11,14.4,100,25,90,1.17,0.42,300,0.19,1,100,1.2,0,46]
[11,18.7,100,26,80,0.9,0.36,100,0.19,1,99,0.4,0,7]
[11,14.3,100,26,60,0.77,0.44,200,0.19,1,99,0.8,0,23]
[11,12.4,100,26,1,0.48,0.48,300,0.19,0,2,1.2,0,46]
[11,15.1,100,26,99,1.43,0.44,300,0.19,1,100,1.2,0,46]
[11,19.5,100,27,80,0.99,0.38,100,0.19,1,99,0.4,0,7]
[11,15.4,100,27,70,1.02,0.46,200,0.19,1,99,0.8,0,23]
[11,13,100,27,50,0.71,0.49,300,0.19,1,98,1.2,0,46]
[11,15.5,100,27,99,1.56,0.46,300,0.19,1,100,1.2,0,46]
[11,17.5,170,21,90,0.76,0.31,100,0.33,1,99,0.4,0,7]
[11,14.1,170,21,70,0.71,0.45,200,0.33,1,97,0.8,0,23]
[11,14.8,170,21,80,0.88,0.43,200,0.33,1,98,0.8,0,23]
[11,12.7,170,21,60,0.6,0.49,300,0.33,1,96,1.2,0,46]
[11,15.2,170,22,1,0.49,0.49,100,0.33,1,1,0.4,0,7]
[11,19.3,170,22,99,0.96,0.3,100,0.33,1,100,0.4,0,7]
[11,15.3,170,22,80,1,0.47,200,0.33,1,98,0.8,0,23]
[11,13,170,22,60,0.71,0.54,300,0.33,1,96,1.2,0,46]
[11,15.5,170,23,50,0.53,0.53,100,0.33,1,90,0.4,0,7]
[11,20.2,170,23,99,1.07,0.32,100,0.33,1,100,0.4,0,7]
[11,16.7,170,23,90,1.32,0.49,200,0.33,1,99,0.8,0,22]
[11,14,170,23,70,1.03,0.56000000000000005,300,0.33,1,97,1.2,0,46]
[11,15.9,170,24,50,0.56999999999999995,0.56999999999999995,100,0.33,1,95,0.4,0,7]
[11,13.7,170,24,1,0.64,0.64,200,0.33,1,2,0.8,0,23]
[11,17.3,170,24,90,1.46,0.52,200,0.33,1,99,0.8,0,22]
[11,14.3,170,24,70,1.17,0.61,300,0.33,1,97,1.2,0,46]
[11,15,170,24,80,1.39,0.59,300,0.33,1,98,1.2,0,46]
[11,17.100000000000001,170,25,60,0.71,0.53,100,0.33,1,97,0.4,0,7]
[11,14.3,170,25,50,0.77,0.65,200,0.33,1,95,0.8,0,23]
[11,18.7,170,25,99,1.8,0.53,200,0.33,1,100,0.8,0,22]
[11,15.4,170,25,80,1.54,0.63,300,0.33,1,98,1.2,0,46]
[11,19.2,170,26,70,0.95,0.51,100,0.33,1,98,0.4,0,7]
[11,14.8,170,26,50,0.88,0.69,200,0.33,1,95,0.8,0,23]
[11,13.2,170,26,1,0.75,0.75,300,0.33,1,2,1.2,0,46]
[11,16.600000000000001,170,26,90,1.94,0.65,300,0.33,1,99,1.2,0,46]
[11,20,170,27,70,1.05,0.53,100,0.33,1,98,0.4,0,7]
[11,16.2,170,27,60,1.22,0.7,200,0.33,1,96,0.8,0,23]
[11,13.3,170,27,1,0.8,0.8,300,0.33,1,2,1.2,0,46]
[11,17.100000000000001,170,27,90,2.12,0.69,300,0.33,1,99,1.2,0,46]
[11,17.7,170,27,99,2.35,0.67,300,0.33,1,100,1.2,0,46]
[11,17,240,21,80,0.7,0.4,100,0.46,3,97,0.4,0,7]
[11,14.6,240,21,70,0.85,0.56999999999999995,200,0.46,3,96,0.8,0,23]
[11,12.9,240,21,50,0.66,0.66,300,0.46,2,85,1.2,0,46]
[11,15.7,240,21,99,1.63,0.54,300,0.46,3,100,1.2,0,46]
[11,19,240,22,90,0.93,0.37,100,0.46,3,99,0.4,0,7]
[11,15.2,240,22,70,0.99,0.61,200,0.46,3,96,0.8,0,23]
[11,13.1,240,22,50,0.72,0.72,300,0.46,2,89,1.2,0,46]
[11,16.5,240,23,1,0.65,0.65,100,0.46,2,1,0.4,0,7]
[11,19.899999999999999,240,23,90,1.03,0.4,100,0.46,3,99,0.4,0,7]
[11,16.8,240,23,80,1.35,0.62,200,0.46,3,97,0.8,0,22]
[11,14,240,23,60,1.03,0.74,300,0.46,3,94,1.2,0,46]
[11,17,240,24,1,0.7,0.7,100,0.46,2,1,0.4,0,7]
[11,17,240,24,50,0.69,0.69,100,0.46,2,87,0.4,0,7]
[11,21.9,240,24,99,1.27,0.36,100,0.46,3,100,0.4,0,7]
[11,18.5,240,24,90,1.74,0.61,200,0.46,3,99,0.8,0,22]
[11,15.2,240,24,70,1.45,0.77,300,0.46,3,96,1.2,0,46]
[11,17.399999999999999,240,25,50,0.75,0.75,100,0.46,2,90,0.4,0,7]
[11,14.8,240,25,1,0.88,0.88,200,0.46,2,2,0.8,0,23]
[11,19.2,240,25,90,1.91,0.65,200,0.46,3,99,0.8,0,22]
[11,15.7,240,25,70,1.62,0.82,300,0.46,3,96,1.2,0,46]
[11,18.5,240,26,60,0.87,0.68,100,0.46,3,95,0.4,0,7]
[11,15.1,240,26,1,0.94,0.94,200,0.46,2,2,0.8,0,23]
[11,21,240,26,99,2.3199999999999998,0.65,200,0.46,3,100,0.8,0,22]
[11,17,240,26,80,2.11,0.83,300,0.46,3,97,1.2,0,46]
[11,19.3,240,27,60,0.96,0.7,100,0.46,3,95,0.4,0,7]
[11,20.8,240,27,70,1.1399999999999999,0.63,100,0.46,3,96,0.4,0,7]
[11,16,240,27,50,1.17,0.92,200,0.46,3,92,0.8,0,23]
[11,14,240,27,1,1.05,1.05,300,0.46,2,2,1.2,0,46]
[11,18.5,240,27,90,2.63,0.84,300,0.46,3,99,1.2,0,45]
[11,16.100000000000001,310,21,70,0.6,0.53,100,0.6,4,95,0.4,0,7]
[11,14.2,310,21,60,0.74,0.74,200,0.6,3,95,0.8,0,23]
[11,13.3,310,21,1,0.8,0.8,300,0.6,3,1,1.2,0,46]
[11,15.7,310,21,90,1.63,0.64,300,0.6,4,98,1.2,0,46]
[11,18.100000000000001,310,22,80,0.83,0.48,100,0.6,4,97,0.4,0,7]
[11,14.7,310,22,60,0.86,0.76,200,0.6,4,92,0.8,0,23]
[11,13.5,310,22,50,0.87,0.87,300,0.6,3,85,1.2,0,46]
[11,17,310,22,99,2.09,0.66,300,0.6,4,100,1.2,0,46]
[11,19,310,23,80,0.93,0.51,100,0.6,4,97,0.4,0,7]
[11,20.2,310,23,90,1.08,0.43,100,0.6,4,98,0.4,0,7]
[11,16.399999999999999,310,23,70,1.25,0.76,200,0.6,4,95,0.8,0,23]
[11,13.7,310,23,50,0.94,0.94,300,0.6,3,89,1.2,0,46]
[11,17.8,310,24,1,0.79,0.79,100,0.6,3,1,0.4,0,7]
[11,21.2,310,24,90,1.19,0.45,100,0.6,4,98,0.4,0,7]
[11,18.100000000000001,310,24,80,1.66,0.74,200,0.6,4,96,0.8,0,22]
[11,14.9,310,24,60,1.36,0.94,300,0.6,4,92,1.2,0,46]
[11,18.3,310,25,1,0.85,0.85,100,0.6,3,1,0.4,0,7]
[11,23.3,310,25,99,1.43,0.39,100,0.6,4,100,0.4,0,7]
[11,18.899999999999999,310,25,80,1.84,0.78,200,0.6,4,97,0.8,0,22]
[11,16.3,310,25,70,1.86,0.95,300,0.6,4,94,1.2,0,46]
[11,18.8,310,26,50,0.91,0.91,100,0.6,3,87,0.4,0,7]
[11,24.3,310,26,99,1.55,0.4,100,0.6,4,100,0.4,0,7]
[11,15.8,310,26,1,1.1100000000000001,1.1100000000000001,200,0.6,3,1,0.8,0,23]
[11,20.9,310,26,90,2.2999999999999998,0.75,200,0.6,4,98,0.8,0,22]
[11,16.899999999999999,310,26,70,2.06,1.01,300,0.6,4,94,1.2,0,46]
[11,19.600000000000001,310,27,60,1,0.81,100,0.6,4,93,0.4,0,7]
[11,16.100000000000001,310,27,1,1.19,1.19,200,0.6,3,1,0.8,0,23]
[11,22.9,310,27,99,2.76,0.72,200,0.6,4,100,0.8,0,22]
[11,18.600000000000001,310,27,80,2.64,1.01,300,0.6,4,96,1.2,0,45]
[11,16.7,380,21,60,0.66,0.66,100,0.74,4,83,0.4,0,7]
[11,14.6,380,21,50,0.84,0.84,200,0.74,4,76,0.8,0,23]
[11,18.2,380,21,99,1.67,0.53,200,0.74,6,100,0.8,0,22]
[11,16.100000000000001,380,21,90,1.79,0.71,300,0.74,6,98,1.2,0,46]
[11,17.100000000000001,380,22,70,0.71,0.63,100,0.74,6,94,0.4,0,7]
[11,15,380,22,50,0.92,0.92,200,0.74,4,79,0.8,0,23]
[11,15,380,22,60,0.92,0.86,200,0.74,6,91,0.8,0,23]
[11,13.9,380,22,1,1,1,300,0.74,4,1,1.2,0,46]
[11,16.8,380,22,90,2.02,0.77,300,0.74,6,98,1.2,0,46]
[11,19.2,380,23,80,0.96,0.55000000000000004,100,0.74,6,96,0.4,0,7]
[11,15.6,380,23,60,1.07,0.92,200,0.74,6,91,0.8,0,23]
[11,14.1,380,23,50,1.08,1.08,300,0.74,4,86,1.2,0,46]
[11,18.3,380,23,99,2.54,0.77,300,0.74,6,100,1.2,0,45]
[11,20.100000000000001,380,24,80,1.06,0.57999999999999996,100,0.74,6,96,0.4,0,7]
[11,17.5,380,24,70,1.5,0.89,200,0.74,6,93,0.8,0,22]
[11,14.3,380,24,50,1.17,1.17,300,0.74,4,90,1.2,0,46]
[11,19,380,24,99,2.8,0.82,300,0.74,6,100,1.2,0,45]
[11,22.4,380,25,90,1.33,0.49,100,0.74,6,98,0.4,0,7]
[11,18.2,380,25,70,1.68,0.94,200,0.74,6,93,0.8,0,22]
[11,19.399999999999999,380,25,80,1.96,0.85,200,0.74,6,96,0.8,0,22]
[11,15.8,380,25,60,1.68,1.1299999999999999,300,0.74,6,90,1.2,0,46]
[11,19.5,380,26,1,0.99,0.99,100,0.74,4,1,0.4,0,7]
[11,24.6,380,26,99,1.58,0.41,100,0.74,6,100,0.4,0,7]
[11,20.2,380,26,80,2.15,0.89,200,0.74,6,96,0.8,0,22]
[11,17.5,380,26,70,2.2599999999999998,1.1200000000000001,300,0.74,6,93,1.2,0,46]
[11,20.100000000000001,380,27,50,1.06,1.06,100,0.74,4,84,0.4,0,7]
[11,25.7,380,27,99,1.7,0.42,100,0.74,6,100,0.4,0,7]
[11,22.4,380,27,90,2.66,0.84,200,0.74,6,98,0.8,0,22]
[11,18.100000000000001,380,27,70,2.4900000000000002,1.18,300,0.74,6,93,1.2,0,46]
[12,14.3,100,21,50,0.27,0.27,100,0.19,0,84,0.4,0,7]
[12,13.2,100,21,1,0.28999999999999998,0.28999999999999998,200,0.19,0,1,0.8,0,23]
[12,14.8,100,21,90,0.66,0.26,200,0.19,1,100,0.8,0,23]
[12,15.3,100,21,99,0.76,0.26,200,0.19,1,100,0.8,0,23]
[12,13.6,100,21,80,0.56999999999999995,0.28000000000000003,300,0.19,1,99,1.2,0,46]
[12,14.7,100,22,60,0.32,0.28000000000000003,100,0.19,1,99,0.4,0,7]
[12,13.3,100,22,50,0.31,0.31,200,0.19,0,91,0.8,0,23]
[12,15.7,100,22,99,0.86,0.28000000000000003,200,0.19,1,100,0.8,0,22]
[12,13.9,100,22,80,0.66,0.31,300,0.19,1,99,1.2,0,46]
[12,16.2,100,23,70,0.49,0.28999999999999998,100,0.19,1,99,0.4,0,7]
[12,13.5,100,23,50,0.34,0.34,200,0.19,0,97,0.8,0,23]
[12,13,100,23,1,0.35,0.35,300,0.19,0,1,1.2,0,46]
[12,14.5,100,23,90,0.89,0.33,300,0.19,1,100,1.2,0,46]
[12,16.8,100,24,70,0.56000000000000005,0.31,100,0.19,1,99,0.4,0,7]
[12,14.3,100,24,60,0.53,0.36,200,0.19,1,99,0.8,0,23]
[12,13.1,100,24,1,0.38,0.38,300,0.19,0,2,1.2,0,46]
[12,13.2,100,24,50,0.41,0.38,300,0.19,1,98,1.2,0,46]
[12,15.2,100,24,99,1.1200000000000001,0.35,300,0.19,1,100,1.2,0,46]
[12,18.5,100,25,80,0.75,0.32,100,0.19,1,99,0.4,0,7]
[12,15.3,100,25,70,0.76,0.38,200,0.19,1,99,0.8,0,23]
[12,13.4,100,25,50,0.49,0.4,300,0.19,1,98,1.2,0,46]
[12,15.5,100,25,99,1.24,0.38,300,0.19,1,100,1.2,0,46]
[12,20.3,100,26,90,0.96,0.32,100,0.19,1,100,0.4,0,7]
[12,15.7,100,26,70,0.85,0.41,200,0.19,1,99,0.8,0,22]
[12,14.1,100,26,60,0.72,0.43,300,0.19,1,99,1.2,0,46]
[12,15.9,100,27,1,0.45,0.45,100,0.19,0,2,0.4,0,7]
[12,21.1,100,27,90,1.05,0.34,100,0.19,1,100,0.4,0,7]
[12,16.8,100,27,80,1.1100000000000001,0.43,200,0.19,1,99,0.8,0,22]
[12,14.3,100,27,60,0.81,0.46,300,0.19,1,99,1.2,0,46]
[12,14.8,100,27,70,0.98,0.45,300,0.19,1,99,1.2,0,46]
[12,15.4,170,21,50,0.4,0.4,100,0.33,1,78,0.4,0,7]
[12,18.7,170,21,99,0.78,0.25,100,0.33,1,100,0.4,0,7]
[12,16,170,21,90,0.94,0.37,200,0.33,1,99,0.8,0,22]
[12,13.9,170,21,70,0.67,0.43,300,0.33,1,97,1.2,0,46]
[12,15.8,170,22,50,0.44,0.44,100,0.33,1,82,0.4,0,7]
[12,14.1,170,22,1,0.49,0.49,200,0.33,1,1,0.8,0,23]
[12,16.600000000000001,170,22,90,1.07,0.41,200,0.33,1,99,0.8,0,22]
[12,14.8,170,22,80,0.98,0.46,300,0.33,1,98,1.2,0,46]
[12,16.100000000000001,170,23,60,0.47,0.44,100,0.33,1,97,0.4,0,7]
[12,14.3,170,23,1,0.54,0.54,200,0.33,1,1,0.8,0,23]
[12,17.899999999999999,170,23,99,1.38,0.43,200,0.33,1,100,0.8,0,22]
[12,15.2,170,23,80,1.1200000000000001,0.51,300,0.33,1,98,1.2,0,46]
[12,16.7,170,24,60,0.55000000000000004,0.47,100,0.33,1,97,0.4,0,7]
[12,17.899999999999999,170,24,70,0.69,0.43,100,0.33,1,98,0.4,0,7]
[12,14.5,170,24,50,0.57999999999999996,0.57999999999999996,200,0.33,1,96,0.8,0,23]
[12,13.7,170,24,1,0.61,0.61,300,0.33,1,1,1.2,0,46]
[12,16.3,170,24,90,1.49,0.53,300,0.33,1,99,1.2,0,46]
[12,18.7,170,25,70,0.78,0.46,100,0.33,1,98,0.4,0,7]
[12,15.8,170,25,60,0.87,0.59,200,0.33,1,96,0.8,0,22]
[12,13.9,170,25,1,0.65,0.65,300,0.33,1,2,1.2,0,46]
[12,17.3,170,25,99,1.86,0.56000000000000005,300,0.33,1,100,1.2,0,45]
[12,20.8,170,26,80,1.02,0.43,100,0.33,1,98,0.4,0,7]
[12,16.3,170,26,60,0.99,0.62,200,0.33,1,96,0.8,0,22]
[12,14.4,170,26,50,0.84,0.68,300,0.33,1,95,1.2,0,46]
[12,17.899999999999999,170,26,99,2.04,0.59,300,0.33,1,100,1.2,0,45]
[12,21.7,170,27,80,1.1200000000000001,0.46,100,0.33,1,98,0.4,0,7]
[12,23,170,27,90,1.28,0.41,100,0.33,1,99,0.4,0,7]
[12,17.8,170,27,70,1.34,0.63,200,0.33,1,97,0.8,0,22]
[12,15.5,170,27,60,1.22,0.7,300,0.33,1,96,1.2,0,46]
[12,16.2,240,21,1,0.49,0.49,100,0.46,2,1,0.4,0,7]
[12,18.3,240,21,90,0.73,0.32,100,0.46,3,99,0.4,0,7]
[12,15.9,240,21,80,0.92,0.48,200,0.46,3,97,0.8,0,22]
[12,13.7,240,21,60,0.59,0.59,300,0.46,2,96,1.2,0,46]
[12,16.600000000000001,240,22,50,0.54,0.54,100,0.46,2,76,0.4,0,7]
[12,20.2,240,22,99,0.95,0.28999999999999998,100,0.46,3,100,0.4,0,7]
[12,16.600000000000001,240,22,80,1.06,0.53,200,0.46,3,97,0.8,0,22]
[12,14.8,240,22,70,0.98,0.61,300,0.46,3,96,1.2,0,46]
[12,17.100000000000001,240,23,50,0.59,0.59,100,0.46,2,80,0.4,0,7]
[12,21.1,240,23,99,1.06,0.31,100,0.46,3,100,0.4,0,7]
[12,15,240,23,1,0.7,0.7,200,0.46,2,1,0.8,0,23]
[12,18.2,240,23,90,1.43,0.53,200,0.46,3,99,0.8,0,22]
[12,16,240,23,80,1.4,0.63,300,0.46,3,97,1.2,0,46]
[12,17.5,240,24,60,0.64,0.64,100,0.46,2,100,0.4,0,7]
[12,15.3,240,24,1,0.76,0.76,200,0.46,2,1,0.8,0,23]
[12,19.8,240,24,99,1.81,0.53,200,0.46,3,100,0.8,0,22]
[12,16.5,240,24,80,1.58,0.68,300,0.46,3,97,1.2,0,46]
[12,17.899999999999999,240,25,60,0.69,0.61,100,0.46,3,95,0.4,0,7]
[12,15.5,240,25,50,0.81,0.81,200,0.46,2,95,0.8,0,22]
[12,20.6,240,25,99,1.99,0.56999999999999995,200,0.46,3,100,0.8,0,22]
[12,17.899999999999999,240,25,90,2.0499999999999998,0.7,300,0.46,3,99,1.2,0,45]
[12,20.100000000000001,240,26,70,0.94,0.56999999999999995,100,0.46,3,96,0.4,0,7]
[12,15.9,240,26,50,0.92,0.83,200,0.46,3,92,0.8,0,22]
[12,17.100000000000001,240,26,60,1.18,0.78,200,0.46,3,94,0.8,0,22]
[12,14.6,240,26,1,0.92,0.92,300,0.46,2,2,1.2,0,46]
[12,19.2,240,26,99,2.5299999999999998,0.71,300,0.46,3,100,1.2,0,45]
[12,22.4,240,27,80,1.21,0.52,100,0.46,3,98,0.4,0,7]
[12,17.7,240,27,60,1.32,0.83,200,0.46,3,94,0.8,0,22]
[12,15.4,240,27,50,1.2,0.93,300,0.46,3,92,1.2,0,46]
[12,19.899999999999999,240,27,99,2.76,0.76,300,0.46,3,100,1.2,0,45]
[12,17.5,310,21,80,0.64,0.42,100,0.6,4,97,0.4,0,7]
[12,15.4,310,21,70,0.8,0.61,200,0.6,4,95,0.8,0,23]
[12,14,310,21,50,0.71,0.71,300,0.6,3,77,1.2,0,46]
[12,17.2,310,22,1,0.61,0.61,100,0.6,3,1,0.4,0,7]
[12,19.5,310,22,90,0.87,0.37,100,0.6,4,98,0.4,0,7]
[12,16.100000000000001,310,22,70,0.95,0.65,200,0.6,4,95,0.8,0,22]
[12,17.100000000000001,310,22,80,1.18,0.6,200,0.6,4,97,0.8,0,22]
[12,14.4,310,22,60,0.85,0.76,300,0.6,4,92,1.2,0,46]
[12,17.8,310,23,1,0.67,0.67,100,0.6,3,1,0.4,0,7]
[12,21.5,310,23,99,1.1000000000000001,0.32,100,0.6,4,100,0.4,0,7]
[12,17.8,310,23,80,1.34,0.65,200,0.6,4,97,0.8,0,22]
[12,15.7,310,23,70,1.31,0.78,300,0.6,4,94,1.2,0,46]
[12,18.3,310,24,50,0.73,0.73,100,0.6,3,78,0.4,0,7]
[12,22.5,310,24,99,1.22,0.34,100,0.6,4,100,0.4,0,7]
[12,19.600000000000001,310,24,90,1.76,0.63,200,0.6,4,98,0.8,0,22]
[12,16.3,310,24,70,1.5,0.84,300,0.6,4,94,1.2,0,46]
[12,18.8,310,25,60,0.79,0.79,100,0.6,3,97,0.4,0,7]
[12,16.2,310,25,1,0.97,0.97,200,0.6,3,1,0.8,0,22]
[12,20.399999999999999,310,25,90,1.95,0.67,200,0.6,4,98,0.8,0,22]
[12,21.4,310,25,99,2.19,0.61,200,0.6,4,100,0.8,0,22]
[12,17.8,310,25,80,2.02,0.84,300,0.6,4,96,1.2,0,45]
[12,19,310,26,60,0.81,0.75,100,0.6,4,93,0.4,0,7]
[12,16.399999999999999,310,26,50,1.03,1.03,200,0.6,3,94,0.8,0,22]
[12,22.3,310,26,99,2.39,0.64,200,0.6,4,100,0.8,0,22]
[12,19.399999999999999,310,26,90,2.58,0.84,300,0.6,4,98,1.2,0,45]
[12,21.3,310,27,70,1.08,0.67,100,0.6,4,95,0.4,0,7]
[12,17,310,27,50,1.1599999999999999,1.03,200,0.6,4,90,0.8,0,22]
[12,15.4,310,27,1,1.18,1.18,300,0.6,3,2,1.2,0,46]
[12,20.100000000000001,310,27,90,2.82,0.89,300,0.6,4,98,1.2,0,45]
[12,17.600000000000001,380,21,80,0.65,0.46,100,0.74,6,96,0.4,0,7]
[12,15.2,380,21,60,0.76,0.76,200,0.74,4,88,0.8,0,23]
[12,14.3,380,21,1,0.82,0.82,300,0.74,4,1,1.2,0,46]
[12,14.3,380,21,50,0.81,0.81,300,0.74,4,75,1.2,0,46]
[12,17.3,380,21,99,1.85,0.6,300,0.74,6,100,1.2,0,45]
[12,18.5,380,22,80,0.76,0.49,100,0.74,6,96,0.4,0,7]
[12,16.399999999999999,380,22,70,1.01,0.73,200,0.74,6,93,0.8,0,22]
[12,14.6,380,22,50,0.9,0.9,300,0.74,4,78,1.2,0,46]
[12,18.3,380,23,1,0.73,0.73,100,0.74,4,1,0.4,0,7]
[12,20.6,380,23,90,1,0.42,100,0.74,6,98,0.4,0,7]
[12,17.100000000000001,380,23,70,1.18,0.79,200,0.74,6,93,0.8,0,22]
[12,15.2,380,23,60,1.1200000000000001,0.94,300,0.74,6,91,1.2,0,46]
[12,18.8,380,24,1,0.8,0.8,100,0.74,4,1,0.4,0,7]
[12,21.6,380,24,90,1.1100000000000001,0.44,100,0.74,6,98,0.4,0,7]
[12,18.899999999999999,380,24,80,1.61,0.76,200,0.74,6,96,0.8,0,22]
[12,15.7,380,24,60,1.3,1,300,0.74,6,91,1.2,0,46]
[12,16.7,380,24,70,1.64,0.94,300,0.74,6,93,1.2,0,46]
[12,19.399999999999999,380,25,50,0.86,0.86,100,0.74,4,76,0.4,0,7]
[12,23.7,380,25,99,1.36,0.36,100,0.74,6,100,0.4,0,7]
[12,20.9,380,25,90,2.0699999999999998,0.71,200,0.74,6,98,0.8,0,22]
[12,17.3,380,25,70,1.85,1,300,0.74,6,93,1.2,0,45]
[12,20,380,26,60,0.92,0.92,100,0.74,4,95,0.4,0,7]
[12,17.100000000000001,380,26,1,1.18,1.18,200,0.74,4,1,0.8,0,22]
[12,21.8,380,26,90,2.2799999999999998,0.75,200,0.74,6,98,0.8,0,22]
[12,19,380,26,80,2.4500000000000002,0.99,300,0.74,6,96,1.2,0,45]
[12,20,380,27,60,0.93,0.87,100,0.74,6,91,0.4,0,7]
[12,17.399999999999999,380,27,1,1.26,1.26,200,0.74,4,1,0.8,0,22]
[12,23.9,380,27,99,2.75,0.7,200,0.74,6,100,0.8,0,22]
[12,19.7,380,27,80,2.69,1.04,300,0.74,6,96,1.2,0,45]
[12,20.8,380,27,90,3.08,0.96,300,0.74,6,98,1.2,0,45]
[13,15.5,100,21,70,0.28999999999999998,0.22,100,0.19,1,99,0.4,0,7]
[13,14.1,100,21,50,0.25,0.25,200,0.19,0,81,0.8,0,23]
[13,13.7,100,21,1,0.26,0.26,300,0.19,0,1,1.2,0,46]
[13,14.7,100,21,90,0.61,0.24,300,0.19,1,100,1.2,0,46]
[13,16.100000000000001,100,22,70,0.36,0.24,100,0.19,1,99,0.4,0,7]
[13,14.3,100,22,60,0.31,0.28000000000000003,200,0.19,1,99,0.8,0,23]
[13,13.8,100,22,1,0.28999999999999998,0.28999999999999998,300,0.19,0,1,1.2,0,46]
[13,15.4,100,22,99,0.82,0.27,300,0.19,1,100,1.2,0,46]
[13,17.600000000000001,100,23,80,0.53,0.25,100,0.19,1,99,0.4,0,7]
[13,14.6,100,23,60,0.38,0.31,200,0.19,1,99,0.8,0,22]
[13,13.9,100,23,50,0.32,0.32,300,0.19,0,92,1.2,0,46]
[13,15.7,100,23,99,0.93,0.3,300,0.19,1,100,1.2,0,46]
[13,15.8,100,24,1,0.33,0.33,100,0.19,0,1,0.4,0,7]
[13,19.2,100,24,90,0.72,0.26,100,0.19,1,100,0.4,0,7]
[13,15.6,100,24,70,0.6,0.33,200,0.19,1,99,0.8,0,22]
[13,14.4,100,24,60,0.48,0.34,300,0.19,1,99,1.2,0,46]
[13,16.100000000000001,100,25,1,0.36,0.36,100,0.19,0,2,0.4,0,7]
[13,19.899999999999999,100,25,90,0.81,0.28000000000000003,100,0.19,1,100,0.4,0,7]
[13,16.600000000000001,100,25,80,0.83,0.35,200,0.19,1,99,0.8,0,22]
[13,14.6,100,25,60,0.56000000000000005,0.37,300,0.19,1,99,1.2,0,46]
[13,16.3,100,26,50,0.39,0.37,100,0.19,1,98,0.4,0,7]
[13,21.7,100,26,99,1.01,0.28000000000000003,100,0.19,1,100,0.4,0,7]
[13,17,100,26,80,0.93,0.37,200,0.19,1,99,0.8,0,22]
[13,15.3,100,26,70,0.81,0.39,300,0.19,1,99,1.2,0,46]
[13,16.8,100,27,50,0.45,0.39,100,0.19,1,98,0.4,0,7]
[13,18,100,27,60,0.57999999999999996,0.37,100,0.19,1,99,0.4,0,7]
[13,14.9,100,27,1,0.44,0.44,200,0.19,0,2,0.8,0,22]
[13,18.2,100,27,90,1.2,0.39,200,0.19,1,100,0.8,0,22]
[13,16.100000000000001,100,27,80,1.08,0.42,300,0.19,1,99,1.2,0,46]
[13,16,170,21,60,0.35,0.35,100,0.33,1,89,0.4,0,7]
[13,14.7,170,21,1,0.4,0.4,200,0.33,1,1,0.8,0,22]
[13,17.2,170,21,99,0.97,0.32,200,0.33,1,100,0.8,0,22]
[13,15.1,170,21,80,0.73,0.38,300,0.33,1,98,1.2,0,46]
[13,16.8,170,22,70,0.44,0.35,100,0.33,1,98,0.4,0,7]
[13,14.9,170,22,50,0.44,0.44,200,0.33,1,82,0.8,0,22]
[13,17.8,170,22,99,1.1200000000000001,0.35,200,0.33,1,100,0.8,0,22]
[13,16,170,22,90,1.06,0.41,300,0.33,1,99,1.2,0,46]
[13,17.5,170,23,70,0.52,0.37,100,0.33,1,98,0.4,0,7]
[13,15.1,170,23,50,0.49,0.49,200,0.33,1,86,0.8,0,22]
[13,15.3,170,23,60,0.54,0.47,200,0.33,1,97,0.8,0,22]
[13,14.4,170,23,1,0.51,0.51,300,0.33,1,1,1.2,0,46]
[13,17,170,23,99,1.4,0.44,300,0.33,1,100,1.2,0,45]
[13,19.399999999999999,170,24,80,0.74,0.36,100,0.33,1,98,0.4,0,7]
[13,15.8,170,24,60,0.65,0.51,200,0.33,1,97,0.8,0,22]
[13,14.6,170,24,50,0.55000000000000004,0.55000000000000004,300,0.33,1,93,1.2,0,46]
[13,17.5,170,24,99,1.56,0.47,300,0.33,1,100,1.2,0,45]
[13,21.4,170,25,90,0.98,0.34,100,0.33,1,99,0.4,0,7]
[13,17.2,170,25,70,0.97,0.52,200,0.33,1,97,0.8,0,22]
[13,14.7,170,25,50,0.6,0.6,300,0.33,1,98,1.2,0,46]
[13,17.899999999999999,170,26,1,0.56999999999999995,0.56999999999999995,100,0.33,1,1,0.4,0,7]
[13,22.3,170,26,90,1.08,0.36,100,0.33,1,99,0.4,0,7]
[13,17.7,170,26,70,1.1000000000000001,0.56000000000000005,200,0.33,1,97,0.8,0,22]
[13,18.7,170,26,80,1.32,0.54,200,0.33,1,98,0.8,0,22]
[13,15.8,170,26,60,0.97,0.62,300,0.33,1,96,1.2,0,46]
[13,18.3,170,27,50,0.61,0.61,100,0.33,1,99,0.4,0,7]
[13,24.4,170,27,99,1.33,0.34,100,0.33,1,100,0.4,0,6]
[13,19.3,170,27,80,1.46,0.56999999999999995,200,0.33,1,98,0.8,0,22]
[13,16.899999999999999,170,27,70,1.36,0.64,300,0.33,1,97,1.2,0,45]
[13,16.7,240,21,50,0.43,0.43,100,0.46,2,70,0.4,0,7]
[13,15.2,240,21,1,0.51,0.51,200,0.46,2,1,0.8,0,22]
[13,17.2,240,21,90,0.98,0.4,200,0.46,3,99,0.8,0,22]
[13,14.9,240,21,70,0.68,0.5,300,0.46,3,96,1.2,0,46]
[13,17.2,240,22,60,0.48,0.48,100,0.46,2,88,0.4,0,7]
[13,15.5,240,22,1,0.56999999999999995,0.56999999999999995,200,0.46,2,1,0.8,0,22]
[13,17.899999999999999,240,22,90,1.1399999999999999,0.44,200,0.46,3,99,0.8,0,22]
[13,18.7,240,22,99,1.32,0.41,200,0.46,3,100,0.8,0,22]
[13,16.100000000000001,240,22,80,1.07,0.53,300,0.46,3,97,1.2,0,46]
[13,17.899999999999999,240,23,70,0.56999999999999995,0.46,100,0.46,3,96,0.4,0,7]
[13,15.7,240,23,50,0.63,0.63,200,0.46,2,82,0.8,0,22]
[13,19.399999999999999,240,23,99,1.49,0.45,200,0.46,3,100,0.8,0,22]
[13,17.3,240,23,90,1.5,0.55000000000000004,300,0.46,3,99,1.2,0,45]
[13,18.7,240,24,70,0.66,0.49,100,0.46,3,96,0.4,0,7]
[13,16,240,24,50,0.69,0.69,200,0.46,2,86,0.8,0,22]
[13,15.1,240,24,1,0.73,0.73,300,0.46,2,1,1.2,0,46]
[13,17.899999999999999,240,24,90,1.69,0.6,300,0.46,3,99,1.2,0,45]
[13,20.8,240,25,80,0.91,0.45,100,0.46,3,98,0.4,0,7]
[13,16.899999999999999,240,25,60,0.91,0.69,200,0.46,3,94,0.8,0,22]
[13,15.3,240,25,1,0.79,0.79,300,0.46,2,1,1.2,0,46]
[13,15.2,240,25,50,0.78,0.78,300,0.46,2,93,1.2,0,46]
[13,19.2,240,25,99,2.15,0.62,300,0.46,3,100,1.2,0,45]
[13,23,240,26,90,1.1599999999999999,0.4,100,0.46,3,99,0.4,0,7]
[13,18.600000000000001,240,26,70,1.3,0.69,200,0.46,3,96,0.8,0,22]
[13,15.6,240,26,50,0.9,0.82,300,0.46,3,93,1.2,0,46]
[13,19.5,240,27,1,0.75,0.75,100,0.46,2,1,0.4,0,7]
[13,24,240,27,90,1.28,0.42,100,0.46,3,99,0.4,0,6]
[13,19.3,240,27,70,1.46,0.73,200,0.46,3,96,0.8,0,22]
[13,16.899999999999999,240,27,60,1.37,0.84,300,0.46,3,94,1.2,0,45]
[13,17.2,310,21,1,0.49,0.49,100,0.6,3,1,0.4,0,7]
[13,19.7,310,21,99,0.78,0.25,100,0.6,4,100,0.4,0,7]
[13,16.7,310,21,80,0.87,0.5,200,0.6,4,97,0.8,0,22]
[13,14.8,310,21,60,0.63,0.63,300,0.6,3,88,1.2,0,46]
[13,15.2,310,21,70,0.77,0.6,300,0.6,4,95,1.2,0,46]
[13,17.7,310,22,50,0.55000000000000004,0.55000000000000004,100,0.6,3,70,0.4,0,7]
[13,20.7,310,22,99,0.89,0.27,100,0.6,4,100,0.4,0,7]
[13,18.399999999999999,310,22,90,1.25,0.49,200,0.6,4,98,0.8,0,22]
[13,15.7,310,22,70,0.95,0.66,300,0.6,4,95,1.2,0,46]
[13,18.2,310,23,60,0.61,0.61,100,0.6,3,87,0.4,0,7]
[13,16.2,310,23,1,0.75,0.75,200,0.6,3,1,0.8,0,22]
[13,19.100000000000001,310,23,90,1.43,0.54,200,0.6,4,98,0.8,0,22]
[13,17.100000000000001,310,23,80,1.42,0.67,300,0.6,4,97,1.2,0,45]
[13,18.8,310,24,60,0.67,0.67,100,0.6,3,90,0.4,0,7]
[13,16.5,310,24,50,0.82,0.82,200,0.6,3,82,0.8,0,22]
[13,20.9,310,24,99,1.83,0.53,200,0.6,4,100,0.8,0,22]
[13,17.7,310,24,80,1.63,0.73,300,0.6,4,97,1.2,0,45]
[13,18.5,310,24,90,1.93,0.68,300,0.6,4,98,1.2,0,45]
[13,19.8,310,25,70,0.79,0.59,100,0.6,4,95,0.4,0,7]
[13,16.8,310,25,50,0.89,0.89,200,0.6,3,86,0.8,0,22]
[13,15.7,310,25,1,0.95,0.95,300,0.6,3,1,1.2,0,46]
[13,19.2,310,25,90,2.16,0.74,300,0.6,4,98,1.2,0,45]
[13,22,310,26,80,1.05,0.52,100,0.6,4,97,0.4,0,7]
[13,18,310,26,60,1.1499999999999999,0.86,200,0.6,4,93,0.8,0,22]
[13,15.9,310,26,1,1.03,1.03,300,0.6,3,1,1.2,0,46]
[13,20.7,310,26,99,2.7,0.74,300,0.6,4,100,1.2,0,45]
[13,23,310,27,80,1.1599999999999999,0.55000000000000004,100,0.6,4,97,0.4,0,7]
[13,19.899999999999999,310,27,70,1.6,0.84,200,0.6,4,95,0.8,0,22]
[13,16.399999999999999,310,27,50,1.2,1.05,300,0.6,4,90,1.2,0,45]
[13,21.5,310,27,99,2.96,0.78,300,0.6,4,100,1.2,0,45]
[13,17.600000000000001,380,21,1,0.53,0.53,100,0.74,4,1,0.4,0,7]
[13,18.899999999999999,380,21,90,0.69,0.34,100,0.74,6,98,0.4,0,7]
[13,16,380,21,70,0.7,0.62,200,0.74,6,94,0.8,0,22]
[13,15.1,380,21,60,0.72,0.72,300,0.74,4,86,1.2,0,46]
[13,18.2,380,22,1,0.6,0.6,100,0.74,4,1,0.4,0,7]
[13,20.9,380,22,99,0.92,0.28000000000000003,100,0.74,6,100,0.4,0,7]
[13,17.7,380,22,80,1.0900000000000001,0.61,200,0.74,6,96,0.8,0,22]
[13,15.3,380,22,60,0.81,0.81,300,0.74,4,90,1.2,0,46]
[13,18.7,380,23,50,0.66,0.66,100,0.74,4,69,0.4,0,7]
[13,21.8,380,23,99,1.03,0.3,100,0.74,6,100,0.4,0,7]
[13,18.5,380,23,80,1.27,0.66,200,0.74,6,96,0.8,0,22]
[13,16.600000000000001,380,23,70,1.24,0.81,300,0.74,6,93,1.2,0,45]
[13,19.3,380,24,50,0.73,0.73,100,0.74,4,71,0.4,0,7]
[13,19.3,380,24,60,0.73,0.73,100,0.74,4,86,0.4,0,7]
[13,17,380,24,1,0.93,0.93,200,0.74,4,1,0.8,0,22]
[13,20.399999999999999,380,24,90,1.71,0.62,200,0.74,6,98,0.8,0,22]
[13,18.100000000000001,380,24,80,1.78,0.81,300,0.74,6,96,1.2,0,45]
[13,19.8,380,25,60,0.8,0.8,100,0.74,4,89,0.4,0,7]
[13,17.3,380,25,50,1,1,200,0.74,4,82,0.8,0,22]
[13,22.3,380,25,99,2.15,0.59,200,0.74,6,100,0.8,0,22]
[13,18.8,380,25,80,2.0099999999999998,0.87,300,0.74,6,96,1.2,0,45]
[13,20.8,380,26,70,0.91,0.69,100,0.74,6,94,0.4,0,7]
[13,17.7,380,26,50,1.0900000000000001,1.0900000000000001,200,0.74,4,86,0.8,0,22]
[13,23.2,380,26,99,2.36,0.62,200,0.74,6,100,0.8,0,22]
[13,20.5,380,26,90,2.61,0.85,300,0.74,6,98,1.2,0,45]
[13,21.7,380,27,70,1.01,0.72,100,0.74,6,94,0.4,0,7]
[13,23.2,380,27,80,1.18,0.59,100,0.74,6,96,0.4,0,7]
[13,19,380,27,60,1.39,1.02,200,0.74,6,91,0.8,0,22]
[13,16.600000000000001,380,27,1,1.26,1.26,300,0.74,4,1,1.2,0,45]
[13,22.2,380,27,99,3.22,0.84,300,0.74,6,100,1.2,0,45]
[14,16.8,100,21,80,0.32,0.19,100,0.19,1,99,0.4,0,7]
[14,14.9,100,21,60,0.22,0.22,200,0.19,0,91,0.8,0,22]
[14,14.6,100,21,50,0.22,0.22,300,0.19,0,76,1.2,0,46]
[14,15.8,100,21,99,0.64,0.21,300,0.19,1,100,1.2,0,45]
[14,18.2,100,22,90,0.49,0.19,100,0.19,1,100,0.4,0,7]
[14,15.5,100,22,70,0.35,0.24,200,0.19,1,99,0.8,0,22]
[14,14.7,100,22,50,0.25,0.25,300,0.19,0,81,1.2,0,46]
[14,16.3,100,23,1,0.27,0.27,100,0.19,0,1,0.4,0,7]
[14,18.899999999999999,100,23,90,0.56999999999999995,0.22,100,0.19,1,100,0.4,0,7]
[14,19.7,100,23,99,0.67,0.2,100,0.19,1,100,0.4,0,7]
[14,16.399999999999999,100,23,80,0.56999999999999995,0.27,200,0.19,1,99,0.8,0,22]
[14,14.9,100,23,60,0.32,0.28000000000000003,300,0.19,1,99,1.2,0,46]
[14,16.600000000000001,100,24,50,0.3,0.3,100,0.19,0,88,0.4,0,7]
[14,20.5,100,24,99,0.75,0.22,100,0.19,1,100,0.4,0,7]
[14,16.8,100,24,80,0.66,0.28999999999999998,200,0.19,1,99,0.8,0,22]
[14,15.6,100,24,70,0.54,0.31,300,0.19,1,99,1.2,0,45]
[14,16.8,100,25,50,0.33,0.33,100,0.19,0,93,0.4,0,7]
[14,15.5,100,25,1,0.35,0.35,200,0.19,0,1,0.8,0,22]
[14,17.899999999999999,100,25,90,0.9,0.31,200,0.19,1,100,0.8,0,22]
[14,15.8,100,25,70,0.64,0.34,300,0.19,1,99,1.2,0,45]
[14,17.8,100,26,60,0.45,0.33,100,0.19,1,99,0.4,0,7]
[14,15.6,100,26,1,0.38,0.38,200,0.19,0,2,0.8,0,22]
[14,15.7,100,26,50,0.39,0.37,200,0.19,1,98,0.8,0,22]
[14,18.899999999999999,100,26,99,1.1499999999999999,0.33,200,0.19,1,100,0.8,0,22]
[14,16.600000000000001,100,26,80,0.89,0.36,300,0.19,1,99,1.2,0,45]
[14,19.600000000000001,100,27,70,0.65,0.33,100,0.19,1,99,0.4,0,7]
[14,16,100,27,50,0.46,0.39,200,0.19,1,98,0.8,0,22]
[14,19.5,100,27,99,1.27,0.36,200,0.19,1,100,0.8,0,22]
[14,17.399999999999999,100,27,90,1.17,0.38,300,0.19,1,100,1.2,0,45]
[14,16.7,170,21,70,0.31,0.31,100,0.33,1,99,0.4,0,7]
[14,15.5,170,21,60,0.34,0.34,200,0.33,1,88,0.8,0,22]
[14,15,170,21,1,0.36,0.36,300,0.33,1,1,1.2,0,46]
[14,16.3,170,21,90,0.79,0.32,300,0.33,1,99,1.2,0,45]
[14,18.100000000000001,170,22,80,0.48,0.28000000000000003,100,0.33,1,98,0.4,0,7]
[14,15.7,170,22,60,0.39,0.39,200,0.33,1,93,0.8,0,22]
[14,15.2,170,22,1,0.41,0.41,300,0.33,1,1,1.2,0,46]
[14,15.2,170,22,50,0.4,0.4,300,0.33,1,78,1.2,0,46]
[14,17.2,170,22,99,1.1100000000000001,0.35,300,0.33,1,100,1.2,0,45]
[14,20,170,23,90,0.7,0.27,100,0.33,1,99,0.4,0,7]
[14,16.600000000000001,170,23,70,0.62,0.41,200,0.33,1,98,0.8,0,22]
[14,15.3,170,23,50,0.45,0.45,300,0.33,1,83,1.2,0,45]
[14,17.8,170,24,1,0.44,0.44,100,0.33,1,1,0.4,0,7]
[14,20.8,170,24,90,0.79,0.3,100,0.33,1,99,0.4,0,7]
[14,18,170,24,80,0.93,0.42,200,0.33,1,98,0.8,0,22]
[14,15.7,170,24,60,0.6,0.49,300,0.33,1,97,1.2,0,45]
[14,18.2,170,25,1,0.49,0.49,100,0.33,1,1,0.4,0,7]
[14,22.8,170,25,99,1.02,0.28000000000000003,100,0.33,1,100,0.4,0,7]
[14,18.600000000000001,170,25,80,1.07,0.46,200,0.33,1,98,0.8,0,22]
[14,16.100000000000001,170,25,60,0.72,0.53,300,0.33,1,97,1.2,0,45]
[14,16.7,170,25,70,0.95,0.51,300,0.33,1,98,1.2,0,45]
[14,18.5,170,26,50,0.53,0.53,100,0.33,1,90,0.4,0,7]
[14,16.5,170,26,1,0.59,0.59,200,0.33,1,1,0.8,0,22]
[14,20.100000000000001,170,26,90,1.42,0.47,200,0.33,1,99,0.8,0,22]
[14,17.100000000000001,170,26,70,1.0900000000000001,0.56000000000000005,300,0.33,1,97,1.2,0,45]
[14,19.399999999999999,170,27,60,0.63,0.49,100,0.33,1,97,0.4,0,7]
[14,16.7,170,27,1,0.63,0.63,200,0.33,1,1,0.8,0,22]
[14,21.7,170,27,99,1.79,0.48,200,0.33,1,100,0.8,0,22]
[14,18.3,170,27,80,1.49,0.57999999999999996,300,0.33,1,98,1.2,0,45]
[14,17.2,240,21,60,0.38,0.38,100,0.46,2,81,0.4,0,7]
[14,15.9,240,21,50,0.44,0.44,200,0.46,2,71,0.8,0,22]
[14,18.399999999999999,240,21,99,1.01,0.32,200,0.46,3,100,0.8,0,22]
[14,16.2,240,21,80,0.75,0.42,300,0.46,3,97,1.2,0,45]
[14,16.8,240,21,90,0.97,0.4,300,0.46,3,99,1.2,0,45]
[14,17.7,240,22,70,0.43,0.43,100,0.46,2,98,0.4,0,7]
[14,16.2,240,22,60,0.5,0.5,200,0.46,2,89,0.8,0,22]
[14,15.5,240,22,1,0.53,0.53,300,0.46,2,1,1.2,0,45]
[14,17.3,240,22,90,1.1499999999999999,0.45,300,0.46,3,99,1.2,0,45]
[14,19.3,240,23,80,0.62,0.37,100,0.46,3,98,0.4,0,7]
[14,16.399999999999999,240,23,60,0.56999999999999995,0.56999999999999995,200,0.46,2,94,0.8,0,22]
[14,15.7,240,23,1,0.6,0.6,300,0.46,2,1,1.2,0,45]
[14,18.5,240,23,99,1.57,0.48,300,0.46,3,100,1.2,0,45]
[14,20.100000000000001,240,24,80,0.71,0.39,100,0.46,3,98,0.4,0,7]
[14,17.7,240,24,70,0.87,0.56000000000000005,200,0.46,3,96,0.8,0,22]
[14,15.9,240,24,50,0.66,0.66,300,0.46,2,84,1.2,0,45]
[14,19.100000000000001,240,24,99,1.78,0.52,300,0.46,3,100,1.2,0,45]
[14,19.100000000000001,240,25,1,0.59,0.59,100,0.46,2,1,0.4,0,7]
[14,22.3,240,25,90,0.96,0.35,100,0.46,3,99,0.4,0,7]
[14,19.399999999999999,240,25,80,1.26,0.56000000000000005,200,0.46,3,97,0.8,0,22]
[14,16.600000000000001,240,25,60,0.89,0.69,300,0.46,3,94,1.2,0,45]
[14,19.600000000000001,240,26,1,0.65,0.65,100,0.46,2,1,0.4,0,7]
[14,24.4,240,26,99,1.2,0.31,100,0.46,3,100,0.4,0,6]
[14,20.100000000000001,240,26,80,1.42,0.6,200,0.46,3,97,0.8,0,22]
[14,17,240,26,60,1.05,0.74,300,0.46,3,94,1.2,0,45]
[14,20,240,27,50,0.7,0.7,100,0.46,2,86,0.4,0,7]
[14,25.4,240,27,99,1.32,0.33,100,0.46,3,100,0.4,0,6]
[14,22,240,27,90,1.85,0.59,200,0.46,3,99,0.8,0,22]
[14,18.399999999999999,240,27,70,1.53,0.75,300,0.46,3,96,1.2,0,45]
[14,17.7,310,21,50,0.43,0.43,100,0.6,3,64,0.4,0,7]
[14,17.7,310,21,60,0.43,0.43,100,0.6,3,78,0.4,0,7]
[14,16.3,310,21,1,0.53,0.53,200,0.6,3,1,0.8,0,22]
[14,18,310,21,90,0.93,0.4,200,0.6,4,98,0.8,0,22]
[14,16.5,310,21,80,0.86,0.5,300,0.6,4,97,1.2,0,45]
[14,18.2,310,22,60,0.49,0.49,100,0.6,3,81,0.4,0,7]
[14,16.600000000000001,310,22,50,0.6,0.6,200,0.6,3,72,0.8,0,22]
[14,19.600000000000001,310,22,99,1.3,0.4,200,0.6,4,100,0.8,0,22]
[14,17,310,22,80,1.05,0.56000000000000005,300,0.6,4,97,1.2,0,45]
[14,18.7,310,23,70,0.55000000000000004,0.55000000000000004,100,0.6,3,98,0.4,0,7]
[14,16.899999999999999,310,23,50,0.67,0.67,200,0.6,3,75,0.8,0,22]
[14,16.100000000000001,310,23,1,0.72,0.72,300,0.6,3,1,1.2,0,45]
[14,18.399999999999999,310,23,90,1.53,0.56999999999999995,300,0.6,4,98,1.2,0,45]
[14,19.100000000000001,310,24,70,0.59,0.53,100,0.6,4,95,0.4,0,7]
[14,20.399999999999999,310,24,80,0.74,0.44,100,0.6,4,97,0.4,0,7]
[14,17.2,310,24,60,0.74,0.74,200,0.6,3,94,0.8,0,22]
[14,16.3,310,24,1,0.79,0.79,300,0.6,3,1,1.2,0,45]
[14,19.8,310,24,99,2.02,0.57999999999999996,300,0.6,4,100,1.2,0,45]
[14,21.3,310,25,80,0.85,0.47,100,0.6,4,97,0.4,0,7]
[14,18.8,310,25,70,1.1200000000000001,0.7,200,0.6,4,95,0.8,0,22]
[14,16.5,310,25,50,0.86,0.86,300,0.6,3,85,1.2,0,45]
[14,20.5,310,25,99,2.2599999999999998,0.63,300,0.6,4,100,1.2,0,45]
[14,23.5,310,26,90,1.1100000000000001,0.4,100,0.6,4,98,0.4,0,6]
[14,19.5,310,26,70,1.28,0.74,200,0.6,4,95,0.8,0,22]
[14,17.399999999999999,310,26,60,1.2,0.88,300,0.6,4,92,1.2,0,45]
[14,20.9,310,27,1,0.8,0.8,100,0.6,3,1,0.4,0,7]
[14,24.5,310,27,90,1.22,0.42,100,0.6,4,98,0.4,0,6]
[14,25.7,310,27,99,1.36,0.34,100,0.6,4,100,0.4,0,6]
[14,22.7,310,27,90,2.02,0.65,200,0.6,4,98,0.8,0,22]
[14,19,310,27,70,1.74,0.88,300,0.6,4,95,1.2,0,45]
[14,18,380,21,60,0.47,0.47,100,0.74,4,75,0.4,0,7]
[14,16.5,380,21,1,0.59,0.59,200,0.74,4,1,0.8,0,22]
[14,19.100000000000001,380,21,99,1.18,0.37,200,0.74,6,100,0.8,0,22]
[14,16.7,380,21,80,0.94,0.56000000000000005,300,0.74,6,96,1.2,0,45]
[14,18.600000000000001,380,22,60,0.53,0.53,100,0.74,4,78,0.4,0,7]
[14,16.899999999999999,380,22,50,0.67,0.67,200,0.74,4,70,0.8,0,22]
[14,19.899999999999999,380,22,99,1.38,0.42,200,0.74,6,100,0.8,0,22]
[14,17.3,380,22,80,1.1399999999999999,0.62,300,0.74,6,96,1.2,0,45]
[14,19.100000000000001,380,23,70,0.6,0.6,100,0.74,4,94,0.4,0,7]
[14,17.3,380,23,50,0.76,0.76,200,0.74,4,72,0.8,0,22]
[14,17.2,380,23,60,0.76,0.76,200,0.74,4,87,0.8,0,22]
[14,16.3,380,23,1,0.82,0.82,300,0.74,4,1,1.2,0,45]
[14,18.8,380,23,90,1.67,0.63,300,0.74,6,98,1.2,0,45]
[14,20.5,380,24,80,0.76,0.49,100,0.74,6,96,0.4,0,7]
[14,17.600000000000001,380,24,60,0.84,0.84,200,0.74,4,91,0.8,0,22]
[14,16.600000000000001,380,24,50,0.9,0.9,300,0.74,4,78,1.2,0,45]
[14,20.3,380,24,99,2.2000000000000002,0.63,300,0.74,6,100,1.2,0,45]
[14,21.4,380,25,80,0.87,0.52,100,0.74,6,96,0.4,0,7]
[14,19.100000000000001,380,25,70,1.19,0.78,200,0.74,6,94,0.8,0,22]
[14,16.8,380,25,50,0.99,0.99,300,0.74,4,82,1.2,0,45]
[14,21.1,380,25,99,2.46,0.68,300,0.74,6,100,1.2,0,45]
[14,23.7,380,26,90,1.1299999999999999,0.43,100,0.74,6,98,0.4,0,6]
[14,19.899999999999999,380,26,70,1.36,0.83,200,0.74,6,94,0.8,0,22]
[14,21.1,380,26,80,1.65,0.74,200,0.74,6,96,0.8,0,22]
[14,17.8,380,26,60,1.31,1,300,0.74,6,91,1.2,0,45]
[14,21.5,380,27,1,0.87,0.87,100,0.74,4,1,0.4,0,7]
[14,25.9,380,27,99,1.38,0.34,100,0.74,6,100,0.4,0,6]
[14,21.9,380,27,80,1.84,0.78,200,0.74,6,96,0.8,0,22]
[14,19.5,380,27,70,1.9,0.99,300,0.74,6,93,1.2,0,45]
[15,16.600000000000001,100,21,50,0.18,0.18,100,0.19,0,70,0.4,0,7]
[15,18.7,100,21,99,0.43,0.14000000000000001,100,0.19,1,100,0.4,0,7]
[15,16.8,100,21,90,0.42,0.18,200,0.19,1,100,0.8,0,22]
[15,15.6,100,21,70,0.2,0.19,300,0.19,1,99,1.2,0,45]
[15,16.8,100,22,50,0.21,0.21,100,0.19,0,74,0.4,0,7]
[15,16,100,22,1,0.22,0.22,200,0.19,0,1,0.8,0,22]
[15,17.2,100,22,90,0.52,0.2,200,0.19,1,100,0.8,0,22]
[15,17.7,100,22,99,0.63,0.2,200,0.19,1,100,0.8,0,22]
[15,16.2,100,22,80,0.42,0.22,300,0.19,1,99,1.2,0,45]
[15,17.100000000000001,100,23,60,0.24,0.24,100,0.19,0,95,0.4,0,7]
[15,16.100000000000001,100,23,50,0.25,0.25,200,0.19,0,80,0.8,0,22]
[15,18.2,100,23,99,0.73,0.23,200,0.19,1,100,0.8,0,22]
[15,16.5,100,23,80,0.51,0.25,300,0.19,1,99,1.2,0,45]
[15,18.100000000000001,100,24,70,0.36,0.24,100,0.19,1,99,0.4,0,7]
[15,16.2,100,24,50,0.28000000000000003,0.28000000000000003,200,0.19,0,85,0.8,0,22]
[15,15.8,100,24,1,0.28999999999999998,0.28999999999999998,300,0.19,0,1,1.2,0,45]
[15,17.2,100,24,90,0.75,0.27,300,0.19,1,100,1.2,0,45]
[15,18.7,100,25,70,0.43,0.26,100,0.19,1,99,0.4,0,7]
[15,16.600000000000001,100,25,60,0.38,0.3,200,0.19,1,99,0.8,0,22]
[15,15.9,100,25,1,0.32,0.32,300,0.19,0,1,1.2,0,45]
[15,15.9,100,25,50,0.31,0.31,300,0.19,0,91,1.2,0,45]
[15,17.899999999999999,100,25,99,1,0.28999999999999998,300,0.19,1,100,1.2,0,45]
[15,20.399999999999999,100,26,80,0.63,0.27,100,0.19,1,99,0.4,0,7]
[15,17.7,100,26,70,0.62,0.32,200,0.19,1,99,0.8,0,22]
[15,16,100,26,50,0.34,0.34,300,0.19,0,96,1.2,0,45]
[15,18.2,100,26,99,1.1200000000000001,0.32,300,0.19,1,100,1.2,0,45]
[15,22.3,100,27,90,0.84,0.27,100,0.19,1,100,0.4,0,6]
[15,18.100000000000001,100,27,70,0.71,0.35,200,0.19,1,99,0.8,0,22]
[15,16.600000000000001,100,27,60,0.56999999999999995,0.37,300,0.19,1,99,1.2,0,45]
[15,17.3,170,21,1,0.27,0.27,100,0.33,1,1,0.4,0,7]
[15,18.600000000000001,170,21,90,0.42,0.2,100,0.33,1,99,0.4,0,7]
[15,16.899999999999999,170,21,80,0.43,0.27,200,0.33,1,98,0.8,0,22]
[15,15.9,170,21,60,0.3,0.3,300,0.33,1,84,1.2,0,45]
[15,17.7,170,22,1,0.31,0.31,100,0.33,1,1,0.4,0,7]
[15,17.7,170,22,50,0.31,0.31,100,0.33,1,70,0.4,0,7]
[15,20.3,170,22,99,0.62,0.19,100,0.33,1,100,0.4,0,7]
[15,18.100000000000001,170,22,90,0.73,0.28999999999999998,200,0.33,1,99,0.8,0,22]
[15,16.2,170,22,70,0.43,0.34,300,0.33,1,98,1.2,0,45]
[15,18,170,23,50,0.35,0.35,100,0.33,1,74,0.4,0,7]
[15,16.7,170,23,1,0.39,0.39,200,0.33,1,1,0.8,0,22]
[15,18.7,170,23,90,0.87,0.33,200,0.33,1,99,0.8,0,22]
[15,17.2,170,23,80,0.76,0.37,300,0.33,1,98,1.2,0,45]
[15,18.399999999999999,170,24,60,0.4,0.4,100,0.33,1,93,0.4,0,7]
[15,16.899999999999999,170,24,1,0.44,0.44,200,0.33,1,1,0.8,0,22]
[15,20.100000000000001,170,24,99,1.18,0.34,200,0.33,1,100,0.8,0,22]
[15,17.600000000000001,170,24,80,0.9,0.41,300,0.33,1,98,1.2,0,45]
[15,18.8,170,25,60,0.44,0.44,100,0.33,1,98,0.4,0,7]
[15,19.5,170,25,70,0.53,0.37,100,0.33,1,98,0.4,0,7]
[15,17.100000000000001,170,25,50,0.49,0.49,200,0.33,1,86,0.8,0,22]
[15,16.399999999999999,170,25,1,0.5,0.5,300,0.33,1,1,1.2,0,45]
[15,18.7,170,25,90,1.28,0.44,300,0.33,1,99,1.2,0,45]
[15,20.3,170,26,70,0.61,0.4,100,0.33,1,98,0.4,0,7]
[15,17.8,170,26,60,0.65,0.5,200,0.33,1,97,0.8,0,22]
[15,16.600000000000001,170,26,1,0.55000000000000004,0.55000000000000004,300,0.33,1,1,1.2,0,45]
[15,19.8,170,26,99,1.67,0.47,300,0.33,1,100,1.2,0,45]
[15,22.4,170,27,80,0.86,0.38,100,0.33,1,99,0.4,0,6]
[15,18.3,170,27,60,0.77,0.54,200,0.33,1,97,0.8,0,22]
[15,16.7,170,27,50,0.59,0.59,300,0.33,1,97,1.2,0,45]
[15,20.3,170,27,99,1.85,0.5,300,0.33,1,100,1.2,0,45]
[15,17.899999999999999,240,21,80,0.33,0.28000000000000003,100,0.46,3,98,0.4,0,7]
[15,18.899999999999999,240,21,90,0.46,0.23,100,0.46,3,99,0.4,0,7]
[15,16.600000000000001,240,21,70,0.38,0.38,200,0.46,2,94,0.8,0,22]
[15,16.100000000000001,240,21,60,0.4,0.4,300,0.46,2,82,1.2,0,45]
[15,18.3,240,22,1,0.38,0.38,100,0.46,2,1,0.4,0,7]
[15,19.8,240,22,90,0.56000000000000005,0.25,100,0.46,3,99,0.4,0,7]
[15,17.8,240,22,80,0.66,0.39,200,0.46,3,98,0.8,0,22]
[15,16.3,240,22,60,0.46,0.46,300,0.46,2,86,1.2,0,45]
[15,18.7,240,23,1,0.43,0.43,100,0.46,2,1,0.4,0,7]
[15,21.7,240,23,99,0.78,0.23,100,0.46,3,100,0.4,0,7]
[15,18.5,240,23,80,0.8,0.43,200,0.46,3,98,0.8,0,22]
[15,17,240,23,70,0.68,0.5,300,0.46,3,96,1.2,0,45]
[15,19.2,240,24,50,0.49,0.49,100,0.46,2,73,0.4,0,7]
[15,22.6,240,24,99,0.88,0.25,100,0.46,3,100,0.4,0,6]
[15,17.5,240,24,1,0.56999999999999995,0.56999999999999995,200,0.46,2,1,0.8,0,22]
[15,20.100000000000001,240,24,90,1.18,0.43,200,0.46,3,99,0.8,0,22]
[15,18.2,240,24,80,1.1100000000000001,0.52,300,0.46,3,97,1.2,0,45]
[15,19.600000000000001,240,25,60,0.54,0.54,100,0.46,2,92,0.4,0,7]
[15,17.7,240,25,1,0.63,0.63,200,0.46,2,1,0.8,0,22]
[15,21.7,240,25,99,1.56,0.43,200,0.46,3,100,0.8,0,22]
[15,18.7,240,25,80,1.3,0.56999999999999995,300,0.46,3,97,1.2,0,45]
[15,20.100000000000001,240,26,60,0.59,0.59,100,0.46,2,96,0.4,0,7]
[15,18,240,26,50,0.69,0.69,200,0.46,2,86,0.8,0,22]
[15,22.5,240,26,99,1.75,0.47,200,0.46,3,100,0.8,0,22]
[15,20.100000000000001,240,26,90,1.78,0.59,300,0.46,3,99,1.2,0,45]
[15,21.5,240,27,70,0.76,0.51,100,0.46,3,96,0.4,0,7]
[15,18.2,240,27,50,0.75,0.75,200,0.46,2,90,0.8,0,22]
[15,18.899999999999999,240,27,60,0.91,0.69,200,0.46,3,95,0.8,0,22]
[15,17.3,240,27,1,0.79,0.79,300,0.46,2,1,1.2,0,45]
[15,20.7,240,27,90,2,0.63,300,0.46,3,99,1.2,0,45]
[15,18,310,21,80,0.35,0.33,100,0.6,4,97,0.4,0,7]
[15,16.899999999999999,310,21,60,0.45,0.45,200,0.6,3,79,0.8,0,22]
[15,16.399999999999999,310,21,50,0.48,0.48,300,0.6,3,66,1.2,0,45]
[15,18.3,310,21,99,1.1499999999999999,0.37,300,0.6,4,100,1.2,0,45]
[15,18.8,310,22,80,0.45,0.36,100,0.6,4,97,0.4,0,7]
[15,17.2,310,22,70,0.52,0.52,200,0.6,3,96,0.8,0,22]
[15,16.600000000000001,310,22,50,0.55000000000000004,0.55000000000000004,300,0.6,3,70,1.2,0,45]
[15,19.2,310,23,1,0.49,0.49,100,0.6,3,1,0.4,0,7]
[15,20.9,310,23,90,0.68,0.31,100,0.6,4,98,0.4,0,7]
[15,17.8,310,23,70,0.65,0.55000000000000004,200,0.6,4,95,0.8,0,22]
[15,18.8,310,23,80,0.88,0.49,200,0.6,4,97,0.8,0,22]
[15,16.8,310,23,60,0.63,0.63,300,0.6,3,88,1.2,0,45]
[15,19.8,310,24,1,0.55000000000000004,0.55000000000000004,100,0.6,3,1,0.4,0,7]
[15,22.9,310,24,99,0.91,0.25,100,0.6,4,100,0.4,0,6]
[15,19.5,310,24,80,1.05,0.54,200,0.6,4,97,0.8,0,22]
[15,17.8,310,24,70,0.96,0.65,300,0.6,4,95,1.2,0,45]
[15,20.3,310,25,50,0.61,0.61,100,0.6,3,72,0.4,0,7]
[15,23.8,310,25,99,1.03,0.28000000000000003,100,0.6,4,100,0.4,0,6]
[15,21.4,310,25,90,1.48,0.52,200,0.6,4,98,0.8,0,22]
[15,18.3,310,25,70,1.1599999999999999,0.71,300,0.6,4,95,1.2,0,45]
[15,20.8,310,26,60,0.67,0.67,100,0.6,3,90,0.4,0,7]
[15,18.5,310,26,1,0.82,0.82,200,0.6,3,1,0.8,0,22]
[15,22.2,310,26,90,1.67,0.56000000000000005,200,0.6,4,98,0.8,0,22]
[15,23.2,310,26,99,1.91,0.5,200,0.6,4,100,0.8,0,22]
[15,19.8,310,26,80,1.69,0.72,300,0.6,4,97,1.2,0,45]
[15,21.3,310,27,60,0.73,0.73,100,0.6,3,94,0.4,0,7]
[15,18.8,310,27,50,0.89,0.89,200,0.6,3,86,0.8,0,22]
[15,24.1,310,27,99,2.11,0.54,200,0.6,4,100,0.8,0,22]
[15,21.5,310,27,90,2.2599999999999998,0.72,300,0.6,4,98,1.2,0,44]
[15,18.399999999999999,380,21,70,0.4,0.4,100,0.74,4,85,0.4,0,7]
[15,17.2,380,21,50,0.51,0.51,200,0.74,4,64,0.8,0,22]
[15,16.600000000000001,380,21,1,0.55000000000000004,0.55000000000000004,300,0.74,4,1,1.2,0,45]
[15,17.899999999999999,380,21,90,1.01,0.44,300,0.74,6,98,1.2,0,45]
[15,19,380,22,70,0.47,0.47,100,0.74,4,88,0.4,0,7]
[15,17.5,380,22,60,0.59,0.59,200,0.74,4,80,0.8,0,22]
[15,16.8,380,22,1,0.64,0.64,300,0.74,4,1,1.2,0,45]
[15,16.8,380,22,50,0.63,0.63,300,0.74,4,68,1.2,0,45]
[15,19.3,380,22,99,1.49,0.46,300,0.74,6,100,1.2,0,45]
[15,19.8,380,23,80,0.56000000000000005,0.43,100,0.74,6,96,0.4,0,7]
[15,18,380,23,70,0.69,0.62,200,0.74,6,94,0.8,0,22]
[15,17.100000000000001,380,23,50,0.72,0.72,300,0.74,4,71,1.2,0,45]
[15,20.2,380,24,1,0.6,0.6,100,0.74,4,1,0.4,0,7]
[15,21.9,380,24,90,0.81,0.35,100,0.74,6,98,0.4,0,6]
[15,18.7,380,24,70,0.85,0.68,200,0.74,6,94,0.8,0,22]
[15,17.3,380,24,60,0.81,0.81,300,0.74,4,90,1.2,0,45]
[15,20.8,380,25,1,0.67,0.67,100,0.74,4,1,0.4,0,7]
[15,22.9,380,25,90,0.92,0.38,100,0.74,6,98,0.4,0,6]
[15,20.6,380,25,80,1.3,0.64,200,0.74,6,96,0.8,0,22]
[15,17.600000000000001,380,25,60,0.91,0.87,300,0.74,6,91,1.2,0,45]
[15,18.600000000000001,380,25,70,1.26,0.8,300,0.74,6,94,1.2,0,45]
[15,21.3,380,26,50,0.73,0.73,100,0.74,4,71,0.4,0,7]
[15,25,380,26,99,1.1599999999999999,0.3,100,0.74,6,100,0.4,0,6]
[15,22.6,380,26,90,1.76,0.6,200,0.74,6,98,0.8,0,22]
[15,19.2,380,26,70,1.47,0.86,300,0.74,6,94,1.2,0,45]
[15,21.9,380,27,60,0.8,0.8,100,0.74,4,89,0.4,0,6]
[15,19.3,380,27,1,1.01,1.01,200,0.74,4,1,0.8,0,22]
[15,23.5,380,27,90,1.97,0.64,200,0.74,6,98,0.8,0,22]
[15,21,380,27,80,2.08,0.85,300,0.74,6,96,1.2,0,45]
[16,17.3,100,21,60,0.15,0.15,100,0.19,0,79,0.4,0,7]
[16,16.7,100,21,1,0.16,0.16,200,0.19,0,1,0.8,0,22]
[16,17.899999999999999,100,21,99,0.45,0.14000000000000001,200,0.19,1,100,0.8,0,22]
[16,16.7,100,21,80,0.24,0.16,300,0.19,1,99,1.2,0,45]
[16,17,100,21,90,0.36,0.15,300,0.19,1,100,1.2,0,45]
[16,17.5,100,22,70,0.18,0.18,100,0.19,0,98,0.4,0,7]
[16,16.8,100,22,50,0.19,0.19,200,0.19,0,71,0.8,0,22]
[16,16.600000000000001,100,22,1,0.19,0.19,300,0.19,0,1,1.2,0,45]
[16,17.3,100,22,90,0.46,0.18,300,0.19,1,100,1.2,0,45]
[16,17.899999999999999,100,23,70,0.22,0.2,100,0.19,1,99,0.4,0,7]
[16,16.899999999999999,100,23,60,0.22,0.22,200,0.19,0,91,0.8,0,22]
[16,16.600000000000001,100,23,1,0.22,0.22,300,0.19,0,1,1.2,0,45]
[16,18,100,23,99,0.68,0.21,300,0.19,1,100,1.2,0,45]
[16,19.5,100,24,80,0.4,0.2,100,0.19,1,99,0.4,0,7]
[16,17.100000000000001,100,24,60,0.25,0.25,200,0.19,0,96,0.8,0,22]
[16,16.7,100,24,50,0.25,0.25,300,0.19,0,80,1.2,0,45]
[16,18.3,100,24,99,0.8,0.24,300,0.19,1,100,1.2,0,45]
[16,18.3,100,25,1,0.27,0.27,100,0.19,0,1,0.4,0,7]
[16,21.1,100,25,90,0.6,0.21,100,0.19,1,100,0.4,0,6]
[16,17.899999999999999,100,25,70,0.45,0.27,200,0.19,1,99,0.8,0,22]
[16,16.899999999999999,100,25,60,0.31,0.28000000000000003,300,0.19,1,99,1.2,0,45]
[16,18.600000000000001,100,26,1,0.3,0.3,100,0.19,0,1,0.4,0,7]
[16,21.9,100,26,90,0.68,0.23,100,0.19,1,100,0.4,0,6]
[16,19,100,26,80,0.69,0.28999999999999998,200,0.19,1,99,0.8,0,22]
[16,17.100000000000001,100,26,60,0.4,0.31,300,0.19,1,99,1.2,0,45]
[16,18.8,100,27,50,0.33,0.33,100,0.19,0,93,0.4,0,7]
[16,23.7,100,27,99,0.89,0.23,100,0.19,1,100,0.4,0,6]
[16,19.399999999999999,100,27,80,0.79,0.31,200,0.19,1,99,0.8,0,22]
[16,17.899999999999999,100,27,70,0.66,0.33,300,0.19,1,99,1.2,0,45]
[16,17.899999999999999,170,21,50,0.22,0.22,100,0.33,1,63,0.4,0,7]
[16,19.8,170,21,99,0.44,0.14000000000000001,100,0.33,1,100,0.4,0,7]
[16,17.100000000000001,170,21,1,0.25,0.25,200,0.33,1,1,0.8,0,22]
[16,18.100000000000001,170,21,90,0.48,0.21,200,0.33,1,99,0.8,0,22]
[16,17,170,21,80,0.35,0.24,300,0.33,1,99,1.2,0,45]
[16,18.3,170,22,60,0.27,0.27,100,0.33,1,80,0.4,0,7]
[16,17.3,170,22,1,0.3,0.3,200,0.33,1,1,0.8,0,22]
[16,19.3,170,22,99,0.76,0.23,200,0.33,1,100,0.8,0,22]
[16,17.399999999999999,170,22,80,0.49,0.28999999999999998,300,0.33,1,98,1.2,0,45]
[16,18.7,170,23,70,0.31,0.31,100,0.33,1,99,0.4,0,7]
[16,17.5,170,23,50,0.34,0.34,200,0.33,1,73,0.8,0,22]
[16,19.899999999999999,170,23,99,0.91,0.27,200,0.33,1,100,0.8,0,22]
[16,18.399999999999999,170,23,90,0.83,0.32,300,0.33,1,99,1.2,0,45]
[16,19,170,24,70,0.35,0.32,100,0.33,1,98,0.4,0,7]
[16,17.7,170,24,50,0.39,0.39,200,0.33,1,77,0.8,0,22]
[16,17.7,170,24,60,0.39,0.39,200,0.33,1,93,0.8,0,22]
[16,17.2,170,24,1,0.4,0.4,300,0.33,1,1,1.2,0,45]
[16,19.399999999999999,170,24,99,1.18,0.34,300,0.33,1,100,1.2,0,45]
[16,21,170,25,80,0.57999999999999996,0.3,100,0.33,1,99,0.4,0,6]
[16,17.899999999999999,170,25,60,0.44,0.44,200,0.33,1,98,0.8,0,22]
[16,17.3,170,25,50,0.45,0.45,300,0.33,1,82,1.2,0,45]
[16,19.899999999999999,170,25,99,1.35,0.38,300,0.33,1,100,1.2,0,45]
[16,23,170,26,90,0.82,0.28000000000000003,100,0.33,1,99,0.4,0,6]
[16,19.2,170,26,70,0.75,0.44,200,0.33,1,98,0.8,0,22]
[16,17.399999999999999,170,26,50,0.5,0.5,300,0.33,1,87,1.2,0,45]
[16,20.2,170,27,1,0.49,0.49,100,0.33,1,1,0.4,0,7]
[16,23.9,170,27,90,0.92,0.31,100,0.33,1,99,0.4,0,6]
[16,19.8,170,27,70,0.88,0.48,200,0.33,1,98,0.8,0,22]
[16,20.8,170,27,80,1.1100000000000001,0.45,200,0.33,1,98,0.8,0,22]
[16,18.100000000000001,170,27,60,0.73,0.53,300,0.33,1,97,1.2,0,45]
[16,18.3,240,21,50,0.27,0.27,100,0.46,2,61,0.4,0,7]
[16,20.100000000000001,240,21,99,0.47,0.15,100,0.46,3,100,0.4,0,7]
[16,17.600000000000001,240,21,80,0.37,0.28999999999999998,200,0.46,3,98,0.8,0,22]
[16,16.899999999999999,240,21,70,0.33,0.33,300,0.46,2,91,1.2,0,45]
[16,18.8,240,22,50,0.33,0.33,100,0.46,2,64,0.4,0,7]
[16,20.9,240,22,99,0.56999999999999995,0.17,100,0.46,3,100,0.4,0,6]
[16,19.100000000000001,240,22,90,0.72,0.3,200,0.46,3,99,0.8,0,22]
[16,17.100000000000001,240,22,70,0.39,0.39,300,0.46,2,95,1.2,0,45]
[16,19.3,240,23,60,0.38,0.38,100,0.46,2,81,0.4,0,7]
[16,17.899999999999999,240,23,1,0.44,0.44,200,0.46,2,1,0.8,0,22]
[16,19.8,240,23,90,0.87,0.35,200,0.46,3,99,0.8,0,22]
[16,20.6,240,23,99,1.06,0.31,200,0.46,3,100,0.8,0,22]
[16,18.2,240,23,80,0.77,0.42,300,0.46,3,98,1.2,0,45]
[16,19.7,240,24,70,0.43,0.43,100,0.46,2,98,0.4,0,7]
[16,18.2,240,24,50,0.5,0.5,200,0.46,2,74,0.8,0,22]
[16,21.3,240,24,99,1.24,0.35,200,0.46,3,100,0.8,0,22]
[16,19.5,240,24,90,1.21,0.44,300,0.46,3,99,1.2,0,45]
[16,20.100000000000001,240,25,70,0.47,0.43,100,0.46,3,96,0.4,0,7]
[16,18.399999999999999,240,25,50,0.56000000000000005,0.56000000000000005,200,0.46,2,78,0.8,0,22]
[16,17.7,240,25,1,0.59,0.59,300,0.46,2,1,1.2,0,45]
[16,20,240,25,90,1.41,0.49,300,0.46,3,99,1.2,0,45]
[16,22.2,240,26,80,0.72,0.39,100,0.46,3,98,0.4,0,6]
[16,18.7,240,26,60,0.63,0.6,200,0.46,3,95,0.8,0,22]
[16,17.899999999999999,240,26,1,0.66,0.66,300,0.46,2,1,1.2,0,45]
[16,17.899999999999999,240,26,50,0.65,0.65,300,0.46,2,83,1.2,0,45]
[16,21.4,240,26,99,1.88,0.51,300,0.46,3,100,1.2,0,44]
[16,23.1,240,27,80,0.82,0.41,100,0.46,3,98,0.4,0,6]
[16,20.5,240,27,70,1.03,0.59,200,0.46,3,96,0.8,0,22]
[16,18.100000000000001,240,27,50,0.72,0.72,300,0.46,2,88,1.2,0,45]
[16,18.7,310,21,1,0.31,0.31,100,0.6,3,1,0.4,0,7]
[16,19.3,310,21,90,0.38,0.22,100,0.6,4,98,0.4,0,7]
[16,17.600000000000001,310,21,70,0.37,0.37,200,0.6,3,88,0.8,0,22]
[16,17.100000000000001,310,21,60,0.4,0.4,300,0.6,3,76,1.2,0,45]
[16,19.2,310,22,1,0.37,0.37,100,0.6,3,1,0.4,0,7]
[16,21.1,310,22,99,0.6,0.18,100,0.6,4,100,0.4,0,6]
[16,18.399999999999999,310,22,80,0.56999999999999995,0.4,200,0.6,4,97,0.8,0,22]
[16,17.399999999999999,310,22,60,0.47,0.47,300,0.6,3,80,1.2,0,45]
[16,17.399999999999999,310,22,70,0.47,0.47,300,0.6,3,93,1.2,0,45]
[16,19.7,310,23,50,0.43,0.43,100,0.6,3,64,0.4,0,7]
[16,22.1,310,23,99,0.7,0.21,100,0.6,4,100,0.4,0,6]
[16,20.100000000000001,310,23,90,0.96,0.39,200,0.6,4,98,0.8,0,22]
[16,17.7,310,23,70,0.59,0.53,300,0.6,4,95,1.2,0,45]
[16,20.2,310,24,60,0.49,0.49,100,0.6,3,80,0.4,0,7]
[16,18.600000000000001,310,24,1,0.6,0.6,200,0.6,3,1,0.8,0,22]
[16,20.9,310,24,90,1.1299999999999999,0.43,200,0.6,4,98,0.8,0,22]
[16,19.100000000000001,310,24,80,1.08,0.55000000000000004,300,0.6,4,97,1.2,0,45]
[16,20.7,310,25,60,0.55000000000000004,0.55000000000000004,100,0.6,3,84,0.4,0,7]
[16,18.899999999999999,310,25,50,0.67,0.67,200,0.6,3,75,0.8,0,22]
[16,22.6,310,25,99,1.54,0.42,200,0.6,4,100,0.8,0,22]
[16,19.7,310,25,80,1.28,0.61,300,0.6,4,97,1.2,0,45]
[16,20.6,310,25,90,1.6,0.56000000000000005,300,0.6,4,98,1.2,0,44]
[16,21.1,310,26,70,0.59,0.53,100,0.6,4,95,0.4,0,6]
[16,19.2,310,26,50,0.74,0.74,200,0.6,3,78,0.8,0,22]
[16,18.3,310,26,1,0.79,0.79,300,0.6,3,1,1.2,0,45]
[16,21.2,310,26,90,1.83,0.61,300,0.6,4,98,1.2,0,44]
[16,23.3,310,27,80,0.85,0.46,100,0.6,4,97,0.4,0,6]
[16,19.600000000000001,310,27,60,0.84,0.76,200,0.6,4,93,0.8,0,22]
[16,18.5,310,27,1,0.87,0.87,300,0.6,3,1,1.2,0,45]
[16,22.8,310,27,99,2.38,0.61,300,0.6,4,100,1.2,0,44]
[16,18.899999999999999,380,21,80,0.33,0.33,100,0.74,4,94,0.4,0,7]
[16,17.8,380,21,60,0.42,0.42,200,0.74,4,74,0.8,0,22]
[16,17.3,380,21,50,0.45,0.45,300,0.74,4,62,1.2,0,45]
[16,19,380,21,99,1.05,0.33,300,0.74,6,100,1.2,0,45]
[16,19.5,380,22,1,0.4,0.4,100,0.74,4,1,0.4,0,7]
[16,20.2,380,22,90,0.49,0.27,100,0.74,6,98,0.4,0,7]
[16,18.2,380,22,70,0.51,0.51,200,0.74,4,90,0.8,0,22]
[16,17.600000000000001,380,22,60,0.54,0.54,300,0.74,4,78,1.2,0,45]
[16,20,380,23,1,0.47,0.47,100,0.74,4,1,0.4,0,7]
[16,22.2,380,23,99,0.72,0.21,100,0.74,6,100,0.4,0,6]
[16,19.3,380,23,80,0.77,0.5,200,0.74,6,96,0.8,0,22]
[16,17.8,380,23,60,0.63,0.63,300,0.74,4,82,1.2,0,45]
[16,20.6,380,24,50,0.53,0.53,100,0.74,4,65,0.4,0,7]
[16,23.2,380,24,99,0.83,0.23,100,0.74,6,100,0.4,0,6]
[16,20.100000000000001,380,24,80,0.95,0.54,200,0.74,6,96,0.8,0,22]
[16,18.399999999999999,380,24,70,0.85,0.67,300,0.74,6,94,1.2,0,45]
[16,21.2,380,25,50,0.6,0.6,100,0.74,4,67,0.4,0,6]
[16,21.2,380,25,60,0.6,0.6,100,0.74,4,80,0.4,0,6]
[16,19.3,380,25,1,0.76,0.76,200,0.74,4,1,0.8,0,22]
[16,22,380,25,90,1.39,0.51,200,0.74,6,98,0.8,0,22]
[16,20,380,25,80,1.4,0.67,300,0.74,6,96,1.2,0,45]
[16,21.7,380,26,60,0.67,0.67,100,0.74,4,83,0.4,0,6]
[16,19.600000000000001,380,26,50,0.84,0.84,200,0.74,4,75,0.8,0,22]
[16,23.9,380,26,99,1.84,0.48,200,0.74,6,100,0.8,0,22]
[16,20.7,380,26,80,1.63,0.73,300,0.74,6,96,1.2,0,44]
[16,22,380,27,70,0.7,0.63,100,0.74,6,94,0.4,0,6]
[16,20,380,27,50,0.92,0.92,200,0.74,4,79,0.8,0,22]
[16,24.8,380,27,99,2.0499999999999998,0.51,200,0.74,6,100,0.8,0,22]
[16,22.4,380,27,90,2.2400000000000002,0.72,300,0.74,6,98,1.2,0,44]
[17,18,100,21,70,0.12,0.12,100,0.19,0,88,0.4,0,7]
[17,18,100,21,80,0.12,0.12,100,0.19,0,100,0.4,0,7]
[17,17.5,100,21,60,0.13,0.13,200,0.19,0,76,0.8,0,22]
[17,17.399999999999999,100,21,1,0.13,0.13,300,0.19,0,1,1.2,0,45]
[17,18.100000000000001,100,21,99,0.38,0.12,300,0.19,1,100,1.2,0,45]
[17,18.600000000000001,100,22,80,0.18,0.14000000000000001,100,0.19,1,99,0.4,0,7]
[17,17.7,100,22,60,0.16,0.16,200,0.19,0,80,0.8,0,22]
[17,17.5,100,22,50,0.16,0.16,300,0.19,0,67,1.2,0,45]
[17,18.399999999999999,100,22,99,0.48,0.15,300,0.19,1,100,1.2,0,45]
[17,20.100000000000001,100,23,90,0.36,0.15,100,0.19,1,100,0.4,0,6]
[17,17.8,100,23,70,0.19,0.19,200,0.19,0,100,0.8,0,22]
[17,17.5,100,23,50,0.19,0.19,300,0.19,0,71,1.2,0,45]
[17,18.8,100,24,1,0.21,0.21,100,0.19,0,1,0.4,0,7]
[17,20.8,100,24,90,0.44,0.17,100,0.19,1,100,0.4,0,6]
[17,21.7,100,24,99,0.54,0.15,100,0.19,1,100,0.4,0,6]
[17,18.8,100,24,80,0.41,0.21,200,0.19,1,99,0.8,0,22]
[17,17.600000000000001,100,24,60,0.22,0.22,300,0.19,0,91,1.2,0,45]
[17,19.100000000000001,100,25,50,0.24,0.24,100,0.19,0,78,0.4,0,7]
[17,22.4,100,25,99,0.63,0.17,100,0.19,1,100,0.4,0,6]
[17,19.2,100,25,80,0.51,0.23,200,0.19,1,99,0.8,0,22]
[17,18.100000000000001,100,25,70,0.38,0.25,300,0.19,1,99,1.2,0,45]
[17,19.3,100,26,50,0.27,0.27,100,0.19,0,83,0.4,0,7]
[17,18.2,100,26,1,0.28000000000000003,0.28000000000000003,200,0.19,0,1,0.8,0,22]
[17,20.3,100,26,90,0.76,0.25,200,0.19,1,100,0.8,0,22]
[17,18.399999999999999,100,26,70,0.47,0.27,300,0.19,1,99,1.2,0,45]
[17,19.7,100,27,60,0.31,0.28000000000000003,100,0.19,1,99,0.4,0,7]
[17,18.3,100,27,1,0.31,0.31,200,0.19,0,1,0.8,0,22]
[17,20.7,100,27,90,0.87,0.28000000000000003,200,0.19,1,100,0.8,0,22]
[17,21.4,100,27,99,1.02,0.27,200,0.19,1,100,0.8,0,22]
[17,19.100000000000001,100,27,80,0.74,0.3,300,0.19,1,99,1.2,0,45]
[17,18.5,170,21,70,0.18,0.18,100,0.33,1,85,0.4,0,7]
[17,17.8,170,21,50,0.2,0.2,200,0.33,1,62,0.8,0,22]
[17,19.2,170,21,99,0.5,0.16,200,0.33,1,100,0.8,0,22]
[17,18.100000000000001,170,21,90,0.4,0.19,300,0.33,1,99,1.2,0,45]
[17,18.899999999999999,170,22,70,0.22,0.22,100,0.33,1,89,0.4,0,7]
[17,18.100000000000001,170,22,60,0.24,0.24,200,0.33,1,78,0.8,0,22]
[17,17.7,170,22,1,0.25,0.25,300,0.33,1,1,1.2,0,45]
[17,18.600000000000001,170,22,90,0.55000000000000004,0.23,300,0.33,1,99,1.2,0,45]
[17,19.7,170,23,80,0.31,0.23,100,0.33,1,99,0.4,0,7]
[17,18.3,170,23,60,0.28999999999999998,0.28999999999999998,200,0.33,1,83,0.8,0,22]
[17,17.899999999999999,170,23,1,0.3,0.3,300,0.33,1,1,1.2,0,45]
[17,17.899999999999999,170,23,50,0.3,0.3,300,0.33,1,69,1.2,0,45]
[17,19.5,170,23,99,0.88,0.26,300,0.33,1,100,1.2,0,44]
[17,21.6,170,24,90,0.53,0.21,100,0.33,1,99,0.4,0,6]
[17,18.600000000000001,170,24,70,0.38,0.33,200,0.33,1,98,0.8,0,22]
[17,18,170,24,50,0.35,0.35,300,0.33,1,73,1.2,0,45]
[17,20.100000000000001,170,25,1,0.36,0.36,100,0.33,1,1,0.4,0,6]
[17,22.4,170,25,90,0.63,0.24,100,0.33,1,99,0.4,0,6]
[17,20,170,25,80,0.71,0.34,200,0.33,1,99,0.8,0,22]
[17,18.100000000000001,170,25,60,0.4,0.4,300,0.33,1,93,1.2,0,45]
[17,20.399999999999999,170,26,1,0.4,0.4,100,0.33,1,1,0.4,0,6]
[17,24.3,170,26,99,0.85,0.22,100,0.33,1,100,0.4,0,6]
[17,20.6,170,26,80,0.84,0.38,200,0.33,1,99,0.8,0,22]
[17,18.3,170,26,60,0.45,0.45,300,0.33,1,99,1.2,0,45]
[17,19,170,26,70,0.7,0.42,300,0.33,1,98,1.2,0,45]
[17,20.8,170,27,50,0.44,0.44,100,0.33,1,81,0.4,0,6]
[17,19.100000000000001,170,27,1,0.49,0.49,200,0.33,1,1,0.8,0,22]
[17,22.2,170,27,90,1.21,0.39,200,0.33,1,99,0.8,0,22]
[17,19.399999999999999,170,27,70,0.85,0.47,300,0.33,1,98,1.2,0,45]
[17,18.899999999999999,240,21,60,0.22,0.22,100,0.46,2,71,0.4,0,7]
[17,18.100000000000001,240,21,1,0.26,0.26,200,0.46,2,1,0.8,0,22]
[17,18.8,240,21,90,0.42,0.22,200,0.46,3,99,0.8,0,22]
[17,17.8,240,21,80,0.26,0.26,300,0.46,2,98,1.2,0,45]
[17,19.3,240,22,60,0.27,0.27,100,0.46,2,74,0.4,0,7]
[17,18.399999999999999,240,22,50,0.32,0.32,200,0.46,2,64,0.8,0,22]
[17,20.2,240,22,99,0.75,0.23,200,0.46,3,100,0.8,0,22]
[17,18.2,240,22,80,0.43,0.31,300,0.46,3,98,1.2,0,45]
[17,18.899999999999999,240,22,90,0.67,0.28999999999999998,300,0.46,3,99,1.2,0,45]
[17,19.8,240,23,70,0.32,0.32,100,0.46,2,90,0.4,0,7]
[17,18.600000000000001,240,23,60,0.38,0.38,200,0.46,2,81,0.8,0,22]
[17,18.100000000000001,240,23,1,0.4,0.4,300,0.46,2,1,1.2,0,45]
[17,19.399999999999999,240,23,90,0.85,0.34,300,0.46,3,99,1.2,0,45]
[17,20.7,240,24,80,0.43,0.31,100,0.46,3,98,0.4,0,6]
[17,18.899999999999999,240,24,60,0.44,0.44,200,0.46,2,84,0.8,0,22]
[17,18.3,240,24,1,0.46,0.46,300,0.46,2,1,1.2,0,45]
[17,20.7,240,24,99,1.28,0.36,300,0.46,3,100,1.2,0,44]
[17,21.5,240,25,80,0.53,0.33,100,0.46,3,98,0.4,0,6]
[17,19.5,240,25,70,0.59,0.46,200,0.46,3,96,0.8,0,22]
[17,18.5,240,25,50,0.52,0.52,300,0.46,2,75,1.2,0,45]
[17,21.3,240,25,99,1.49,0.41,300,0.46,3,100,1.2,0,44]
[17,21.2,240,26,1,0.49,0.49,100,0.46,2,1,0.4,0,6]
[17,23.7,240,26,90,0.77,0.28999999999999998,100,0.46,3,99,0.4,0,6]
[17,21.2,240,26,80,0.98,0.46,200,0.46,3,98,0.8,0,22]
[17,18.7,240,26,60,0.59,0.59,300,0.46,2,95,1.2,0,45]
[17,21.7,240,27,1,0.54,0.54,100,0.46,2,1,0.4,0,6]
[17,25.8,240,27,99,1.02,0.25,100,0.46,3,100,0.4,0,6]
[17,21.9,240,27,80,1.1499999999999999,0.5,200,0.46,3,98,0.8,0,22]
[17,19.100000000000001,240,27,60,0.73,0.63,300,0.46,3,95,1.2,0,45]
[17,19.100000000000001,310,21,50,0.25,0.25,100,0.6,3,57,0.4,0,7]
[17,20.399999999999999,310,21,99,0.39,0.13,100,0.6,4,100,0.4,0,6]
[17,19,310,21,90,0.46,0.25,200,0.6,4,98,0.8,0,22]
[17,17.899999999999999,310,21,70,0.32,0.32,300,0.6,3,84,1.2,0,45]
[17,19.600000000000001,310,22,50,0.31,0.31,100,0.6,3,60,0.4,0,7]
[17,19.600000000000001,310,22,60,0.31,0.31,100,0.6,3,72,0.4,0,7]
[17,18.600000000000001,310,22,1,0.38,0.38,200,0.6,3,1,0.8,0,22]
[17,19.7,310,22,90,0.62,0.28999999999999998,200,0.6,4,98,0.8,0,22]
[17,18.399999999999999,310,22,80,0.49,0.37,300,0.6,4,97,1.2,0,45]
[17,20.2,310,23,60,0.37,0.37,100,0.6,3,75,0.4,0,6]
[17,18.899999999999999,310,23,50,0.45,0.45,200,0.6,3,65,0.8,0,22]
[17,21.3,310,23,99,1,0.28999999999999998,200,0.6,4,100,0.8,0,22]
[17,19,310,23,80,0.69,0.43,300,0.6,4,97,1.2,0,45]
[17,20.7,310,24,70,0.43,0.43,100,0.6,3,91,0.4,0,6]
[17,19.2,310,24,50,0.52,0.52,200,0.6,3,68,0.8,0,22]
[17,18.600000000000001,310,24,1,0.56000000000000005,0.56000000000000005,300,0.6,3,1,1.2,0,45]
[17,20.399999999999999,310,24,90,1.18,0.45,300,0.6,4,98,1.2,0,44]
[17,21.2,310,25,70,0.49,0.49,100,0.6,3,94,0.4,0,6]
[17,21.7,310,25,80,0.55000000000000004,0.38,100,0.6,4,97,0.4,0,6]
[17,19.600000000000001,310,25,60,0.59,0.59,200,0.6,3,86,0.8,0,22]
[17,18.8,310,25,1,0.63,0.63,300,0.6,3,1,1.2,0,45]
[17,21.8,310,25,99,1.68,0.46,300,0.6,4,100,1.2,0,44]
[17,22.6,310,26,80,0.65,0.41,100,0.6,4,97,0.4,0,6]
[17,20.5,310,26,70,0.8,0.6,200,0.6,4,95,0.8,0,22]
[17,19,310,26,50,0.71,0.71,300,0.6,3,77,1.2,0,45]
[17,22.5,310,26,99,1.93,0.51,300,0.6,4,100,1.2,0,44]
[17,24.8,310,27,90,0.91,0.34,100,0.6,4,99,0.4,0,6]
[17,21.2,310,27,70,0.97,0.64,200,0.6,4,95,0.8,0,22]
[17,19.2,310,27,50,0.78,0.78,300,0.6,3,80,1.2,0,45]
[17,19.3,380,21,1,0.27,0.27,100,0.74,4,1,0.4,0,7]
[17,19.5,380,21,90,0.28999999999999998,0.21,100,0.74,6,98,0.4,0,7]
[17,20.399999999999999,380,21,99,0.4,0.13,100,0.74,6,100,0.4,0,6]
[17,18.5,380,21,80,0.34,0.34,200,0.74,4,94,0.8,0,22]
[17,18,380,21,60,0.36,0.36,300,0.74,4,71,1.2,0,45]
[17,19.899999999999999,380,22,50,0.34,0.34,100,0.74,4,58,0.4,0,6]
[17,21.4,380,22,99,0.51,0.16,100,0.74,6,100,0.4,0,6]
[17,19.899999999999999,380,22,90,0.66,0.32,200,0.74,6,98,0.8,0,22]
[17,18.3,380,22,70,0.45,0.45,300,0.74,4,87,1.2,0,45]
[17,20.5,380,23,50,0.4,0.4,100,0.74,4,61,0.4,0,6]
[17,19.2,380,23,1,0.51,0.51,200,0.74,4,1,0.8,0,22]
[17,20.6,380,23,90,0.84,0.37,200,0.74,6,98,0.8,0,22]
[17,18.600000000000001,380,23,70,0.54,0.54,300,0.74,4,91,1.2,0,45]
[17,21,380,24,60,0.47,0.47,100,0.74,4,75,0.4,0,6]
[17,19.600000000000001,380,24,1,0.59,0.59,200,0.74,4,1,0.8,0,22]
[17,19.5,380,24,50,0.59,0.59,200,0.74,4,66,0.8,0,22]
[17,22.4,380,24,99,1.25,0.35,200,0.74,6,100,0.8,0,22]
[17,19.8,380,24,80,0.96,0.55000000000000004,300,0.74,6,96,1.2,0,44]
[17,21.6,380,25,70,0.54,0.54,100,0.74,4,91,0.4,0,6]
[17,19.899999999999999,380,25,50,0.67,0.67,200,0.74,4,69,0.8,0,22]
[17,19.100000000000001,380,25,1,0.73,0.73,300,0.74,4,1,1.2,0,45]
[17,21.4,380,25,90,1.52,0.55000000000000004,300,0.74,6,98,1.2,0,44]
[17,22.2,380,26,70,0.6,0.6,100,0.74,4,94,0.4,0,6]
[17,20.2,380,26,60,0.75,0.75,200,0.74,4,87,0.8,0,22]
[17,19.3,380,26,1,0.82,0.82,300,0.74,4,1,1.2,0,45]
[17,22.1,380,26,90,1.77,0.6,300,0.74,6,98,1.2,0,44]
[17,23.6,380,27,80,0.77,0.48,100,0.74,6,96,0.4,0,6]
[17,20.6,380,27,60,0.84,0.84,200,0.74,4,91,0.8,0,22]
[17,21.4,380,27,70,1.03,0.72,200,0.74,6,94,0.8,0,22]
[17,19.600000000000001,380,27,50,0.9,0.9,300,0.74,4,78,1.2,0,44]
[17,23.8,380,27,99,2.36,0.59,300,0.74,6,100,1.2,0,44]
[18,19.2,100,21,90,0.14000000000000001,0.08,100,0.19,1,100,0.4,0,6]
[18,18.399999999999999,100,21,70,0.09,0.09,200,0.19,0,83,0.8,0,22]
[18,18.3,100,21,50,0.1,0.1,300,0.19,0,59,1.2,0,45]
[18,19,100,22,1,0.12,0.12,100,0.19,0,1,0.4,0,6]
[18,19.8,100,22,90,0.21,0.1,100,0.19,1,100,0.4,0,6]
[18,18.600000000000001,100,22,80,0.14000000000000001,0.12,200,0.19,1,99,0.8,0,22]
[18,18.399999999999999,100,22,60,0.13,0.13,300,0.19,0,76,1.2,0,45]
[18,19.3,100,23,1,0.15,0.15,100,0.19,0,1,0.4,0,6]
[18,21.3,100,23,99,0.38,0.11,100,0.19,1,100,0.4,0,6]
[18,19,100,23,80,0.23,0.15,200,0.19,1,99,0.8,0,22]
[18,19.5,100,23,90,0.36,0.15,200,0.19,1,100,0.8,0,22]
[18,18.5,100,23,70,0.16,0.16,300,0.19,0,94,1.2,0,45]
[18,19.5,100,24,50,0.18,0.18,100,0.19,0,70,0.4,0,6]
[18,18.8,100,24,1,0.19,0.19,200,0.19,0,1,0.8,0,22]
[18,20,100,24,90,0.46,0.17,200,0.19,1,100,0.8,0,22]
[18,18.5,100,24,70,0.19,0.19,300,0.19,0,100,1.2,0,44]
[18,19.8,100,25,60,0.21,0.21,100,0.19,0,89,0.4,0,6]
[18,18.899999999999999,100,25,1,0.22,0.22,200,0.19,0,1,0.8,0,22]
[18,21,100,25,99,0.69,0.19,200,0.19,1,100,0.8,0,22]
[18,19.3,100,25,80,0.44,0.21,300,0.19,1,99,1.2,0,44]
[18,20,100,26,60,0.24,0.24,100,0.19,0,94,0.4,0,6]
[18,19.100000000000001,100,26,50,0.25,0.25,200,0.19,0,80,0.8,0,22]
[18,21.5,100,26,99,0.81,0.22,200,0.19,1,100,0.8,0,22]
[18,19.600000000000001,100,26,80,0.54,0.24,300,0.19,1,99,1.2,0,44]
[18,20,100,26,90,0.71,0.24,300,0.19,1,100,1.2,0,44]
[18,21.2,100,27,70,0.37,0.24,100,0.19,1,99,0.4,0,6]
[18,19.3,100,27,60,0.28999999999999998,0.27,200,0.19,1,99,0.8,0,22]
[18,18.8,100,27,1,0.28000000000000003,0.28000000000000003,300,0.19,0,1,1.2,0,44]
[18,20.399999999999999,100,27,90,0.82,0.26,300,0.19,1,100,1.2,0,44]
[18,19.100000000000001,170,21,80,0.13,0.13,100,0.33,1,92,0.4,0,6]
[18,18.600000000000001,170,21,60,0.15,0.15,200,0.33,1,70,0.8,0,22]
[18,18.399999999999999,170,21,50,0.15,0.15,300,0.33,1,59,1.2,0,45]
[18,19.2,170,21,99,0.42,0.13,300,0.33,1,100,1.2,0,44]
[18,19.5,170,22,80,0.18,0.18,100,0.33,1,97,0.4,0,6]
[18,18.8,170,22,70,0.2,0.2,200,0.33,1,87,0.8,0,22]
[18,18.600000000000001,170,22,50,0.2,0.2,300,0.33,1,62,1.2,0,44]
[18,19.7,170,22,99,0.57999999999999996,0.18,300,0.33,1,100,1.2,0,44]
[18,19.899999999999999,170,23,1,0.22,0.22,100,0.33,1,1,0.4,0,6]
[18,21,170,23,90,0.34,0.16,100,0.33,1,99,0.4,0,6]
[18,19.399999999999999,170,23,80,0.32,0.23,200,0.33,1,99,0.8,0,22]
[18,18.7,170,23,60,0.25,0.25,300,0.33,1,79,1.2,0,44]
[18,20.3,170,24,1,0.27,0.27,100,0.33,1,1,0.4,0,6]
[18,22.8,170,24,99,0.55000000000000004,0.15,100,0.33,1,100,0.4,0,6]
[18,19.899999999999999,170,24,80,0.45,0.27,200,0.33,1,99,0.8,0,22]
[18,18.899999999999999,170,24,70,0.3,0.3,300,0.33,1,97,1.2,0,44]
[18,20.7,170,25,50,0.31,0.31,100,0.33,1,70,0.4,0,6]
[18,23.6,170,25,99,0.66,0.18,100,0.33,1,100,0.4,0,6]
[18,21.4,170,25,90,0.78,0.28000000000000003,200,0.33,1,99,0.8,0,22]
[18,19.2,170,25,70,0.42,0.34,300,0.33,1,98,1.2,0,44]
[18,21,170,26,50,0.35,0.35,100,0.33,1,73,0.4,0,6]
[18,21,170,26,60,0.35,0.35,100,0.33,1,88,0.4,0,6]
[18,19.7,170,26,1,0.39,0.39,200,0.33,1,1,0.8,0,22]
[18,22.8,170,26,99,1.1200000000000001,0.3,200,0.33,1,100,0.8,0,22]
[18,20.3,170,26,80,0.8,0.37,300,0.33,1,99,1.2,0,44]
[18,21.4,170,27,60,0.4,0.4,100,0.33,1,93,0.4,0,6]
[18,19.899999999999999,170,27,50,0.44,0.44,200,0.33,1,81,0.8,0,22]
[18,23.5,170,27,99,1.28,0.33,200,0.33,1,100,0.8,0,22]
[18,20.8,170,27,80,0.96,0.41,300,0.33,1,99,1.2,0,44]
[18,19.399999999999999,240,21,70,0.16,0.16,100,0.46,2,79,0.4,0,6]
[18,18.8,240,21,50,0.19,0.19,200,0.46,2,57,0.8,0,22]
[18,18.600000000000001,240,21,1,0.2,0.2,300,0.46,2,1,1.2,0,44]
[18,18.899999999999999,240,21,90,0.32,0.18,300,0.46,3,99,1.2,0,44]
[18,19.899999999999999,240,22,70,0.22,0.22,100,0.46,2,83,0.4,0,6]
[18,19.899999999999999,240,22,80,0.22,0.22,100,0.46,2,95,0.4,0,6]
[18,19.100000000000001,240,22,60,0.25,0.25,200,0.46,2,73,0.8,0,22]
[18,18.8,240,22,50,0.26,0.26,300,0.46,2,61,1.2,0,44]
[18,20,240,22,99,0.7,0.21,300,0.46,3,100,1.2,0,44]
[18,20.3,240,23,80,0.27,0.27,100,0.46,2,99,0.4,0,6]
[18,19.399999999999999,240,23,70,0.31,0.31,200,0.46,2,89,0.8,0,22]
[18,18.899999999999999,240,23,50,0.33,0.33,300,0.46,2,64,1.2,0,44]
[18,20.6,240,23,99,0.9,0.26,300,0.46,3,100,1.2,0,44]
[18,22,240,24,90,0.47,0.22,100,0.46,3,99,0.4,0,6]
[18,19.600000000000001,240,24,70,0.38,0.38,200,0.46,2,94,0.8,0,22]
[18,19.100000000000001,240,24,60,0.39,0.39,300,0.46,2,81,1.2,0,44]
[18,21.3,240,25,1,0.38,0.38,100,0.46,2,1,0.4,0,6]
[18,22.9,240,25,90,0.56999999999999995,0.24,100,0.46,3,99,0.4,0,6]
[18,24,240,25,99,0.7,0.19,100,0.46,3,100,0.4,0,6]
[18,20.9,240,25,80,0.68,0.38,200,0.46,3,98,0.8,0,22]
[18,19.5,240,25,70,0.52,0.44,300,0.46,3,96,1.2,0,44]
[18,21.7,240,26,50,0.43,0.43,100,0.46,2,70,0.4,0,6]
[18,25,240,26,99,0.81,0.21,100,0.46,3,100,0.4,0,6]
[18,22.6,240,26,90,1.08,0.38,200,0.46,3,99,0.8,0,22]
[18,20,240,26,70,0.69,0.49,300,0.46,3,96,1.2,0,44]
[18,22.2,240,27,50,0.49,0.49,100,0.46,2,73,0.4,0,6]
[18,20.399999999999999,240,27,1,0.56999999999999995,0.56999999999999995,200,0.46,2,1,0.8,0,22]
[18,23.4,240,27,90,1.25,0.41,200,0.46,3,99,0.8,0,22]
[18,21.4,240,27,80,1.17,0.51,300,0.46,3,98,1.2,0,44]
[18,19.600000000000001,310,21,60,0.18,0.18,100,0.6,3,67,0.4,0,6]
[18,19,310,21,1,0.23,0.23,200,0.6,3,1,0.8,0,22]
[18,19,310,21,50,0.22,0.22,200,0.6,3,57,0.8,0,22]
[18,20.100000000000001,310,21,99,0.48,0.15,200,0.6,4,100,0.8,0,22]
[18,18.7,310,21,80,0.24,0.24,300,0.6,3,92,1.2,0,44]
[18,20.100000000000001,310,22,70,0.25,0.25,100,0.6,3,81,0.4,0,6]
[18,19.3,310,22,50,0.3,0.3,200,0.6,3,59,0.8,0,22]
[18,18.899999999999999,310,22,1,0.32,0.32,300,0.6,3,1,1.2,0,44]
[18,19.600000000000001,310,22,90,0.56000000000000005,0.28000000000000003,300,0.6,4,98,1.2,0,44]
[18,20.6,310,23,70,0.31,0.31,100,0.6,3,84,0.4,0,6]
[18,19.600000000000001,310,23,60,0.37,0.37,200,0.6,3,75,0.8,0,22]
[18,19.100000000000001,310,23,1,0.4,0.4,300,0.6,3,1,1.2,0,44]
[18,20.9,310,23,99,1.02,0.3,300,0.6,4,100,1.2,0,44]
[18,21,310,24,80,0.34,0.33,100,0.6,4,97,0.4,0,6]
[18,19.899999999999999,310,24,60,0.45,0.45,200,0.6,3,78,0.8,0,22]
[18,19.899999999999999,310,24,70,0.45,0.45,200,0.6,3,92,0.8,0,22]
[18,19.399999999999999,310,24,50,0.47,0.47,300,0.6,3,66,1.2,0,44]
[18,21.6,310,24,99,1.24,0.35,300,0.6,4,100,1.2,0,44]
[18,23.1,310,25,90,0.59,0.27,100,0.6,4,99,0.4,0,6]
[18,20.2,310,25,70,0.52,0.52,200,0.6,3,96,0.8,0,22]
[18,19.600000000000001,310,25,60,0.55000000000000004,0.55000000000000004,300,0.6,3,84,1.2,0,44]
[18,22.3,310,26,1,0.49,0.49,100,0.6,3,1,0.4,0,6]
[18,24,310,26,90,0.7,0.28999999999999998,100,0.6,4,99,0.4,0,6]
[18,21.9,310,26,80,0.91,0.48,200,0.6,4,97,0.8,0,22]
[18,19.8,310,26,60,0.63,0.63,300,0.6,3,87,1.2,0,44]
[18,22.8,310,27,1,0.56000000000000005,0.56000000000000005,100,0.6,3,1,0.4,0,6]
[18,26.1,310,27,99,0.94,0.23,100,0.6,4,100,0.4,0,6]
[18,22.7,310,27,80,1.0900000000000001,0.53,200,0.6,4,97,0.8,0,22]
[18,23.9,310,27,90,1.36,0.46,200,0.6,4,98,0.8,0,22]
[18,20.8,310,27,70,0.98,0.64,300,0.6,4,95,1.2,0,44]
[18,19.7,380,21,50,0.2,0.2,100,0.74,4,55,0.4,0,6]
[18,19.100000000000001,380,21,1,0.26,0.26,200,0.74,4,1,0.8,0,22]
[18,19.399999999999999,380,21,90,0.32,0.22,200,0.74,6,98,0.8,0,22]
[18,18.8,380,21,80,0.27,0.27,300,0.74,4,91,1.2,0,44]
[18,20.3,380,22,60,0.27,0.27,100,0.74,4,68,0.4,0,6]
[18,19.5,380,22,1,0.34,0.34,200,0.74,4,1,0.8,0,22]
[18,21,380,22,99,0.69,0.21,200,0.74,6,100,0.8,0,22]
[18,19,380,22,80,0.36,0.36,300,0.74,4,96,1.2,0,44]
[18,20.9,380,23,60,0.34,0.34,100,0.74,4,70,0.4,0,6]
[18,19.8,380,23,50,0.42,0.42,200,0.74,4,61,0.8,0,22]
[18,21.8,380,23,99,0.88,0.26,200,0.74,6,100,0.8,0,22]
[18,19.3,380,23,1,0.46,0.46,300,0.74,4,1,1.2,0,44]
[18,20.399999999999999,380,23,90,0.84,0.37,300,0.74,6,98,1.2,0,44]
[18,21.5,380,24,70,0.4,0.4,100,0.74,4,85,0.4,0,6]
[18,20.2,380,24,60,0.51,0.51,200,0.74,4,77,0.8,0,22]
[18,19.600000000000001,380,24,1,0.55000000000000004,0.55000000000000004,300,0.74,4,1,1.2,0,44]
[18,21.9,380,24,99,1.35,0.38,300,0.74,6,100,1.2,0,44]
[18,21.9,380,25,80,0.45,0.4,100,0.74,6,96,0.4,0,6]
[18,20.5,380,25,60,0.59,0.59,200,0.74,4,80,0.8,0,22]
[18,19.8,380,25,50,0.63,0.63,300,0.74,4,68,1.2,0,44]
[18,22.6,380,25,99,1.6,0.43,300,0.74,6,100,1.2,0,44]
[18,22.8,380,26,80,0.56000000000000005,0.43,100,0.74,6,96,0.4,0,6]
[18,20.9,380,26,70,0.68,0.62,200,0.74,6,94,0.8,0,22]
[18,20.100000000000001,380,26,50,0.72,0.72,300,0.74,4,71,1.2,0,44]
[18,20.100000000000001,380,26,60,0.72,0.72,300,0.74,4,85,1.2,0,44]
[18,23.2,380,27,1,0.61,0.61,100,0.74,4,1,0.4,0,6]
[18,25.1,380,27,90,0.82,0.34,100,0.74,6,98,0.4,0,6]
[18,22.9,380,27,80,1.1399999999999999,0.57999999999999996,200,0.74,6,96,0.8,0,22]
[18,20.3,380,27,60,0.81,0.81,300,0.74,4,89,1.2,0,44]
[19,19.5,100,21,1,0.06,0.06,100,0.19,0,1,0.4,0,6]
[19,20.2,100,21,99,0.14000000000000001,0.05,100,0.19,1,100,0.4,0,6]
[19,19.3,100,21,80,0.06,0.06,200,0.19,0,90,0.8,0,22]
[19,19.2,100,21,70,0.06,0.06,300,0.19,0,79,1.2,0,44]
[19,19.8,100,22,50,0.09,0.09,100,0.19,0,59,0.4,0,6]
[19,20.9,100,22,99,0.22,7.0000000000000007E-2,100,0.19,1,100,0.4,0,6]
[19,19.7,100,22,90,0.17,0.09,200,0.19,1,100,0.8,0,22]
[19,19.3,100,22,70,0.09,0.09,300,0.19,0,83,1.2,0,44]
[19,19.3,100,22,80,0.09,0.09,300,0.19,0,95,1.2,0,44]
[19,20,100,23,60,0.12,0.12,100,0.19,0,75,0.4,0,6]
[19,19.5,100,23,1,0.13,0.13,200,0.19,0,1,0.8,0,22]
[19,20.7,100,23,99,0.38,0.11,200,0.19,1,100,0.8,0,22]
[19,19.399999999999999,100,23,80,0.15,0.12,300,0.19,1,99,1.2,0,44]
[19,20.3,100,24,60,0.15,0.15,100,0.19,0,79,0.4,0,6]
[19,19.7,100,24,50,0.16,0.16,200,0.19,0,67,0.8,0,22]
[19,21.1,100,24,99,0.49,0.14000000000000001,200,0.19,1,100,0.8,0,22]
[19,20.100000000000001,100,24,90,0.39,0.15,300,0.19,1,100,1.2,0,44]
[19,20.5,100,25,70,0.18,0.18,100,0.19,0,98,0.4,0,6]
[19,19.8,100,25,50,0.19,0.19,200,0.19,0,71,0.8,0,22]
[19,19.5,100,25,1,0.19,0.19,300,0.19,0,1,1.2,0,44]
[19,20.399999999999999,100,25,90,0.5,0.18,300,0.19,1,100,1.2,0,44]
[19,20.8,100,25,99,0.63,0.18,300,0.19,1,100,1.2,0,44]
[19,21.9,100,26,80,0.34,0.18,100,0.19,1,99,0.4,0,6]
[19,19.899999999999999,100,26,60,0.22,0.22,200,0.19,0,90,0.8,0,22]
[19,19.600000000000001,100,26,50,0.22,0.22,300,0.19,0,75,1.2,0,44]
[19,21.2,100,26,99,0.76,0.2,300,0.19,1,100,1.2,0,44]
[19,22.6,100,27,80,0.42,0.2,100,0.19,1,99,0.4,0,6]
[19,20.6,100,27,70,0.37,0.24,200,0.19,1,99,0.8,0,22]
[19,19.7,100,27,50,0.25,0.25,300,0.19,0,80,1.2,0,44]
[19,19.8,170,21,1,0.09,0.09,100,0.33,1,1,0.4,0,6]
[19,19.8,170,21,90,0.09,0.09,100,0.33,1,99,0.4,0,6]
[19,19.399999999999999,170,21,70,0.1,0.1,200,0.33,1,78,0.8,0,22]
[19,19.3,170,21,60,0.1,0.1,300,0.33,1,67,1.2,0,44]
[19,20.2,170,22,1,0.13,0.13,100,0.33,1,1,0.4,0,6]
[19,20.399999999999999,170,22,90,0.16,0.11,100,0.33,1,99,0.4,0,6]
[19,21.3,170,22,99,0.27,0.08,100,0.33,1,100,0.4,0,6]
[19,19.600000000000001,170,22,80,0.15,0.15,200,0.33,1,94,0.8,0,22]
[19,19.399999999999999,170,22,70,0.15,0.15,300,0.33,1,82,1.2,0,44]
[19,20.5,170,23,50,0.18,0.18,100,0.33,1,60,0.4,0,6]
[19,22.1,170,23,99,0.36,0.11,100,0.33,1,100,0.4,0,6]
[19,20.6,170,23,90,0.37,0.17,200,0.33,1,99,0.8,0,22]
[19,19.600000000000001,170,23,70,0.2,0.2,300,0.33,1,87,1.2,0,44]
[19,20.9,170,24,60,0.22,0.22,100,0.33,1,76,0.4,0,6]
[19,20.100000000000001,170,24,1,0.25,0.25,200,0.33,1,1,0.8,0,22]
[19,21.2,170,24,90,0.51,0.21,200,0.33,1,99,0.8,0,22]
[19,20,170,24,80,0.36,0.24,300,0.33,1,99,1.2,0,44]
[19,21.3,170,25,1,0.27,0.27,100,0.33,1,1,0.4,0,6]
[19,21.7,170,25,80,0.31,0.23,100,0.33,1,99,0.4,0,6]
[19,22.8,170,25,90,0.44,0.19,100,0.33,1,99,0.4,0,6]
[19,23.8,170,25,99,0.56000000000000005,0.15,100,0.33,1,100,0.4,0,6]
[19,20.3,170,25,1,0.3,0.3,200,0.33,1,1,0.8,0,22]
[19,20.3,170,25,50,0.28999999999999998,0.28999999999999998,200,0.33,1,68,0.8,0,22]
[19,20.3,170,25,60,0.28999999999999998,0.28999999999999998,200,0.33,1,82,0.8,0,22]
[19,20.3,170,25,70,0.28999999999999998,0.28999999999999998,200,0.33,1,97,0.8,0,22]
[19,20.9,170,25,80,0.45,0.27,200,0.33,1,99,0.8,0,22]
[19,21.8,170,25,90,0.65,0.24,200,0.33,1,99,0.8,0,22]
[19,22.6,170,25,99,0.83,0.22,200,0.33,1,100,0.8,0,22]
[19,19.899999999999999,170,25,1,0.3,0.3,300,0.33,1,1,1.2,0,44]
[19,19.899999999999999,170,25,50,0.3,0.3,300,0.33,1,69,1.2,0,44]
[19,19.899999999999999,170,25,60,0.3,0.3,300,0.33,1,83,1.2,0,44]
[19,19.899999999999999,170,25,70,0.3,0.3,300,0.33,1,97,1.2,0,44]
[19,20.5,170,25,80,0.51,0.28000000000000003,300,0.33,1,99,1.2,0,44]
[19,21.1,170,25,90,0.73,0.27,300,0.33,1,99,1.2,0,44]
[19,21.7,170,25,99,0.93,0.26,300,0.33,1,100,1.2,0,44]
[19,21.7,170,26,1,0.31,0.31,100,0.33,1,1,0.4,0,6]
[19,21.7,170,26,50,0.31,0.31,100,0.33,1,70,0.4,0,6]
[19,21.7,170,26,60,0.31,0.31,100,0.33,1,84,0.4,0,6]
[19,21.7,170,26,70,0.31,0.31,100,0.33,1,98,0.4,0,6]
[19,22.5,170,26,80,0.4,0.25,100,0.33,1,99,0.4,0,6]
[19,23.7,170,26,90,0.54,0.21,100,0.33,1,99,0.4,0,6]
[19,24.7,170,26,99,0.67,0.17,100,0.33,1,100,0.4,0,6]
[19,20.5,170,26,1,0.34,0.34,200,0.33,1,1,0.8,0,22]
[19,20.5,170,26,50,0.34,0.34,200,0.33,1,72,0.8,0,22]
[19,20.5,170,26,60,0.34,0.34,200,0.33,1,87,0.8,0,22]
[19,20.6,170,26,70,0.38,0.33,200,0.33,1,98,0.8,0,22]
[19,21.5,170,26,80,0.59,0.3,200,0.33,1,99,0.8,0,22]
[19,22.4,170,26,90,0.8,0.28000000000000003,200,0.33,1,99,0.8,0,22]
[19,23.3,170,26,99,0.99,0.26,200,0.33,1,100,0.8,0,22]
[19,20,170,26,1,0.35,0.35,300,0.33,1,1,1.2,0,44]
[19,20,170,26,50,0.35,0.35,300,0.33,1,73,1.2,0,44]
[19,20,170,26,60,0.35,0.35,300,0.33,1,88,1.2,0,44]
[19,20.2,170,26,70,0.42,0.34,300,0.33,1,98,1.2,0,44]
[19,20.9,170,26,80,0.66,0.32,300,0.33,1,99,1.2,0,44]
[19,21.6,170,26,90,0.9,0.31,300,0.33,1,99,1.2,0,44]
[19,22.2,170,26,99,1.1100000000000001,0.28999999999999998,300,0.33,1,100,1.2,0,44]
[19,22.1,170,27,1,0.36,0.36,100,0.33,1,1,0.4,0,6]
[19,22,170,27,50,0.35,0.35,100,0.33,1,73,0.4,0,6]
[19,22,170,27,60,0.35,0.35,100,0.33,1,88,0.4,0,6]
[19,22,170,27,70,0.35,0.32,100,0.33,1,98,0.4,0,6]
[19,23.3,170,27,80,0.5,0.27,100,0.33,1,99,0.4,0,6]
[19,24.5,170,27,90,0.64,0.23,100,0.33,1,99,0.4,0,6]
[19,25.7,170,27,99,0.77,0.19,100,0.33,1,100,0.4,0,6]
[19,20.7,170,27,1,0.39,0.39,200,0.33,1,1,0.8,0,22]
[19,20.7,170,27,50,0.39,0.39,200,0.33,1,76,0.8,0,22]
[19,20.7,170,27,60,0.39,0.39,200,0.33,1,92,0.8,0,22]
[19,21.2,170,27,70,0.5,0.36,200,0.33,1,98,0.8,0,22]
[19,22.1,170,27,80,0.73,0.34,200,0.33,1,99,0.8,0,22]
[19,23.1,170,27,90,0.95,0.31,200,0.33,1,99,0.8,0,22]
[19,24,170,27,99,1.1499999999999999,0.28999999999999998,200,0.33,1,100,0.8,0,21]
[19,20.2,170,27,1,0.4,0.4,300,0.33,1,1,1.2,0,44]
[19,20.100000000000001,170,27,50,0.4,0.4,300,0.33,1,77,1.2,0,44]
[19,20.100000000000001,170,27,60,0.4,0.4,300,0.33,1,93,1.2,0,44]
[19,20.6,170,27,70,0.56999999999999995,0.38,300,0.33,1,98,1.2,0,44]
[19,21.4,170,27,80,0.82,0.36,300,0.33,1,99,1.2,0,44]
[19,22.1,170,27,90,1.07,0.35,300,0.33,1,99,1.2,0,44]
[19,22.7,170,27,99,1.3,0.33,300,0.33,1,100,1.2,0,44]
[19,19.899999999999999,240,21,1,0.11,0.11,100,0.46,2,1,0.4,0,6]
[19,19.899999999999999,240,21,50,0.11,0.11,100,0.46,2,54,0.4,0,6]
[19,19.899999999999999,240,21,60,0.11,0.11,100,0.46,2,65,0.4,0,6]
[19,19.899999999999999,240,21,70,0.11,0.11,100,0.46,2,76,0.4,0,6]
[19,19.899999999999999,240,21,80,0.11,0.11,100,0.46,2,87,0.4,0,6]
[19,19.899999999999999,240,21,90,0.11,0.11,100,0.46,2,98,0.4,0,6]
[19,20.6,240,21,99,0.18,0.06,100,0.46,3,100,0.4,0,6]
[19,19.600000000000001,240,21,1,0.13,0.13,200,0.46,2,1,0.8,0,22]
[19,19.5,240,21,50,0.13,0.13,200,0.46,2,55,0.8,0,22]
[19,19.5,240,21,60,0.13,0.13,200,0.46,2,66,0.8,0,22]
[19,19.5,240,21,70,0.13,0.13,200,0.46,2,77,0.8,0,22]
[19,19.5,240,21,80,0.13,0.13,200,0.46,2,88,0.8,0,22]
[19,19.5,240,21,90,0.13,0.13,200,0.46,2,99,0.8,0,22]
[19,20.2,240,21,99,0.28999999999999998,0.1,200,0.46,3,100,0.8,0,22]
[19,19.399999999999999,240,21,1,0.13,0.13,300,0.46,2,1,1.2,0,44]
[19,19.399999999999999,240,21,50,0.13,0.13,300,0.46,2,55,1.2,0,44]
[19,19.399999999999999,240,21,60,0.13,0.13,300,0.46,2,66,1.2,0,44]
[19,19.399999999999999,240,21,70,0.13,0.13,300,0.46,2,77,1.2,0,44]
[19,19.399999999999999,240,21,80,0.13,0.13,300,0.46,2,88,1.2,0,44]
[19,19.399999999999999,240,21,90,0.15,0.13,300,0.46,3,99,1.2,0,44]
[19,20,240,21,99,0.34,0.11,300,0.46,3,100,1.2,0,44]
[19,20.399999999999999,240,22,1,0.16,0.16,100,0.46,2,1,0.4,0,6]
[19,20.399999999999999,240,22,50,0.16,0.16,100,0.46,2,56,0.4,0,6]
[19,20.399999999999999,240,22,60,0.16,0.16,100,0.46,2,68,0.4,0,6]
[19,20.399999999999999,240,22,70,0.16,0.16,100,0.46,2,79,0.4,0,6]
[19,20.399999999999999,240,22,80,0.16,0.16,100,0.46,2,91,0.4,0,6]
[19,20.5,240,22,90,0.17,0.14000000000000001,100,0.46,3,99,0.4,0,6]
[19,21.4,240,22,99,0.28000000000000003,0.09,100,0.46,3,100,0.4,0,6]
[19,19.8,240,22,1,0.19,0.19,200,0.46,2,1,0.8,0,22]
[19,19.8,240,22,50,0.19,0.19,200,0.46,2,58,0.8,0,22]
[19,19.8,240,22,60,0.19,0.19,200,0.46,2,69,0.8,0,22]
[19,19.8,240,22,70,0.19,0.19,200,0.46,2,81,0.8,0,22]
[19,19.8,240,22,80,0.19,0.19,200,0.46,2,93,0.8,0,22]
[19,20.2,240,22,90,0.27,0.17,200,0.46,3,99,0.8,0,22]
[19,20.9,240,22,99,0.45,0.14000000000000001,200,0.46,3,100,0.8,0,22]
[19,19.600000000000001,240,22,1,0.2,0.2,300,0.46,2,1,1.2,0,44]
[19,19.600000000000001,240,22,50,0.2,0.2,300,0.46,2,58,1.2,0,44]
[19,19.600000000000001,240,22,60,0.2,0.2,300,0.46,2,70,1.2,0,44]
[19,19.600000000000001,240,22,70,0.2,0.2,300,0.46,2,81,1.2,0,44]
[19,19.600000000000001,240,22,80,0.2,0.2,300,0.46,2,93,1.2,0,44]
[19,19.899999999999999,240,22,90,0.32,0.18,300,0.46,3,99,1.2,0,44]
[19,20.5,240,22,99,0.53,0.16,300,0.46,3,100,1.2,0,44]
[19,20.9,240,23,1,0.22,0.22,100,0.46,2,1,0.4,0,6]
[19,20.9,240,23,50,0.22,0.22,100,0.46,2,59,0.4,0,6]
[19,20.9,240,23,60,0.22,0.22,100,0.46,2,71,0.4,0,6]
[19,20.9,240,23,70,0.22,0.22,100,0.46,2,83,0.4,0,6]
[19,20.9,240,23,80,0.22,0.22,100,0.46,2,95,0.4,0,6]
[19,21.3,240,23,90,0.27,0.16,100,0.46,3,99,0.4,0,6]
[19,22.3,240,23,99,0.39,0.12,100,0.46,3,100,0.4,0,6]
[19,20.100000000000001,240,23,1,0.25,0.25,200,0.46,2,1,0.8,0,22]
[19,20.100000000000001,240,23,50,0.25,0.25,200,0.46,2,60,0.8,0,22]
[19,20.100000000000001,240,23,60,0.25,0.25,200,0.46,2,73,0.8,0,22]
[19,20.100000000000001,240,23,70,0.25,0.25,200,0.46,2,85,0.8,0,22]
[19,20.100000000000001,240,23,80,0.25,0.25,200,0.46,2,97,0.8,0,22]
[19,20.9,240,23,90,0.43,0.21,200,0.46,3,99,0.8,0,22]
[19,21.6,240,23,99,0.61,0.18,200,0.46,3,100,0.8,0,22]
[19,19.8,240,23,1,0.27,0.27,300,0.46,2,1,1.2,0,44]
[19,19.8,240,23,50,0.26,0.26,300,0.46,2,61,1.2,0,44]
[19,19.8,240,23,60,0.26,0.26,300,0.46,2,73,1.2,0,44]
[19,19.8,240,23,70,0.26,0.26,300,0.46,2,86,1.2,0,44]
[19,19.8,240,23,80,0.26,0.26,300,0.46,2,98,1.2,0,44]
[19,20.5,240,23,90,0.51,0.23,300,0.46,3,99,1.2,0,44]
[19,21.1,240,23,99,0.72,0.21,300,0.46,3,100,1.2,0,44]
[19,21.4,240,24,1,0.27,0.27,100,0.46,2,1,0.4,0,6]
[19,21.3,240,24,50,0.27,0.27,100,0.46,2,61,0.4,0,6]
[19,21.3,240,24,60,0.27,0.27,100,0.46,2,74,0.4,0,6]
[19,21.3,240,24,70,0.27,0.27,100,0.46,2,86,0.4,0,6]
[19,21.3,240,24,80,0.27,0.27,100,0.46,2,99,0.4,0,6]
[19,22.2,240,24,90,0.37,0.19,100,0.46,3,99,0.4,0,6]
[19,23.2,240,24,99,0.49,0.14000000000000001,100,0.46,3,100,0.4,0,6]
[19,20.399999999999999,240,24,1,0.32,0.32,200,0.46,2,1,0.8,0,22]
[19,20.399999999999999,240,24,50,0.32,0.32,200,0.46,2,63,0.8,0,22]
[19,20.399999999999999,240,24,60,0.31,0.31,200,0.46,2,76,0.8,0,22]
[19,20.399999999999999,240,24,70,0.31,0.31,200,0.46,2,89,0.8,0,22]
[19,20.6,240,24,80,0.37,0.28999999999999998,200,0.46,3,98,0.8,0,22]
[19,21.5,240,24,90,0.59,0.25,200,0.46,3,99,0.8,0,22]
[19,22.4,240,24,99,0.79,0.22,200,0.46,3,100,0.8,0,22]
[19,20,240,24,1,0.33,0.33,300,0.46,2,1,1.2,0,44]
[19,19.899999999999999,240,24,50,0.33,0.33,300,0.46,2,64,1.2,0,44]
[19,19.899999999999999,240,24,60,0.33,0.33,300,0.46,2,77,1.2,0,44]
[19,19.899999999999999,240,24,70,0.33,0.33,300,0.46,2,90,1.2,0,44]
[19,20.3,240,24,80,0.44,0.31,300,0.46,3,98,1.2,0,44]
[19,21,240,24,90,0.7,0.28000000000000003,300,0.46,3,99,1.2,0,44]
[19,21.7,240,24,99,0.93,0.26,300,0.46,3,100,1.2,0,44]
[19,21.8,240,25,1,0.33,0.33,100,0.46,2,1,0.4,0,6]
[19,21.8,240,25,50,0.33,0.33,100,0.46,2,64,0.4,0,6]
[19,21.8,240,25,60,0.33,0.33,100,0.46,2,77,0.4,0,6]
[19,21.8,240,25,70,0.33,0.33,100,0.46,2,90,0.4,0,6]
[19,21.9,240,25,80,0.33,0.28000000000000003,100,0.46,3,98,0.4,0,6]
[19,23.1,240,25,90,0.47,0.22,100,0.46,3,99,0.4,0,6]
[19,24.2,240,25,99,0.6,0.16,100,0.46,3,100,0.4,0,6]
[19,20.6,240,25,1,0.38,0.38,200,0.46,2,1,0.8,0,22]
[19,20.6,240,25,50,0.38,0.38,200,0.46,2,67,0.8,0,22]
[19,20.6,240,25,60,0.38,0.38,200,0.46,2,80,0.8,0,22]
[19,20.6,240,25,70,0.38,0.38,200,0.46,2,94,0.8,0,22]
[19,21.3,240,25,80,0.52,0.33,200,0.46,3,98,0.8,0,22]
[19,22.3,240,25,90,0.75,0.3,200,0.46,3,99,0.8,0,22]
[19,23.1,240,25,99,0.96,0.26,200,0.46,3,100,0.8,0,22]
[19,20.100000000000001,240,25,1,0.4,0.4,300,0.46,2,1,1.2,0,44]
[19,20.100000000000001,240,25,50,0.39,0.39,300,0.46,2,67,1.2,0,44]
[19,20.100000000000001,240,25,60,0.39,0.39,300,0.46,2,81,1.2,0,44]
[19,20.100000000000001,240,25,70,0.39,0.39,300,0.46,2,95,1.2,0,44]
[19,20.8,240,25,80,0.62,0.36,300,0.46,3,98,1.2,0,44]
[19,21.6,240,25,90,0.89,0.33,300,0.46,3,99,1.2,0,44]
[19,22.3,240,25,99,1.1399999999999999,0.31,300,0.46,3,100,1.2,0,44]
[19,22.3,240,26,1,0.38,0.38,100,0.46,2,1,0.4,0,6]
[19,22.3,240,26,50,0.38,0.38,100,0.46,2,67,0.4,0,6]
[19,22.3,240,26,60,0.38,0.38,100,0.46,2,80,0.4,0,6]
[19,22.3,240,26,70,0.38,0.38,100,0.46,2,94,0.4,0,6]
[19,22.7,240,26,80,0.43,0.3,100,0.46,3,98,0.4,0,6]
[19,24,240,26,90,0.57999999999999996,0.24,100,0.46,3,99,0.4,0,6]
[19,25.1,240,26,99,0.71,0.18,100,0.46,3,100,0.4,0,6]
[19,20.9,240,26,1,0.44,0.44,200,0.46,2,1,0.8,0,22]
[19,20.9,240,26,50,0.44,0.44,200,0.46,2,70,0.8,0,22]
[19,20.9,240,26,60,0.44,0.44,200,0.46,2,84,0.8,0,22]
[19,20.9,240,26,70,0.44,0.44,200,0.46,2,98,0.8,0,22]
[19,21.9,240,26,80,0.68,0.37,200,0.46,3,98,0.8,0,22]
[19,23,240,26,90,0.92,0.33,200,0.46,3,99,0.8,0,22]
[19,23.9,240,26,99,1.1399999999999999,0.3,200,0.46,3,100,0.8,0,21]
[19,20.3,240,26,1,0.46,0.46,300,0.46,2,1,1.2,0,44]
[19,20.3,240,26,50,0.46,0.46,300,0.46,2,71,1.2,0,44]
[19,20.3,240,26,60,0.46,0.46,300,0.46,2,86,1.2,0,44]
[19,20.5,240,26,70,0.51,0.44,300,0.46,3,96,1.2,0,44]
[19,21.3,240,26,80,0.8,0.41,300,0.46,3,98,1.2,0,44]
[19,22.1,240,26,90,1.0900000000000001,0.38,300,0.46,3,99,1.2,0,44]
[19,22.9,240,26,99,1.35,0.35,300,0.46,3,100,1.2,0,44]
[19,22.8,240,27,1,0.44,0.44,100,0.46,2,1,0.4,0,6]
[19,22.7,240,27,50,0.43,0.43,100,0.46,2,70,0.4,0,6]
[19,22.7,240,27,60,0.43,0.43,100,0.46,2,84,0.4,0,6]
[19,22.7,240,27,70,0.43,0.43,100,0.46,2,98,0.4,0,6]
[19,23.6,240,27,80,0.53,0.33,100,0.46,3,98,0.4,0,6]
[19,24.9,240,27,90,0.68,0.26,100,0.46,3,99,0.4,0,6]
[19,26,240,27,99,0.82,0.2,100,0.46,3,100,0.4,0,6]
[19,21.2,240,27,1,0.51,0.51,200,0.46,2,1,0.8,0,22]
[19,21.2,240,27,50,0.5,0.5,200,0.46,2,74,0.8,0,22]
[19,21.2,240,27,60,0.5,0.5,200,0.46,2,88,0.8,0,22]
[19,21.5,240,27,70,0.59,0.46,200,0.46,3,96,0.8,0,22]
[19,22.6,240,27,80,0.84,0.42,200,0.46,3,98,0.8,0,22]
[19,23.7,240,27,90,1.1000000000000001,0.37,200,0.46,3,99,0.8,0,21]
[19,24.7,240,27,99,1.33,0.33,200,0.46,3,100,0.8,0,21]
[19,20.5,240,27,1,0.53,0.53,300,0.46,2,1,1.2,0,44]
[19,20.5,240,27,50,0.52,0.52,300,0.46,2,75,1.2,0,44]
[19,20.5,240,27,60,0.52,0.52,300,0.46,2,90,1.2,0,44]
[19,21,240,27,70,0.69,0.49,300,0.46,3,96,1.2,0,44]
[19,21.9,240,27,80,1,0.46,300,0.46,3,98,1.2,0,44]
[19,22.7,240,27,90,1.3,0.43,300,0.46,3,99,1.2,0,44]
[19,23.5,240,27,99,1.58,0.4,300,0.46,3,100,1.2,0,44]
[19,20.100000000000001,310,21,1,0.12,0.12,100,0.6,3,1,0.4,0,6]
[19,20.100000000000001,310,21,50,0.12,0.12,100,0.6,3,53,0.4,0,6]
[19,20.100000000000001,310,21,60,0.12,0.12,100,0.6,3,64,0.4,0,6]
[19,20.100000000000001,310,21,70,0.12,0.12,100,0.6,3,75,0.4,0,6]
[19,20.100000000000001,310,21,80,0.12,0.12,100,0.6,3,86,0.4,0,6]
[19,20.100000000000001,310,21,90,0.12,0.12,100,0.6,3,97,0.4,0,6]
[19,20.6,310,21,99,0.19,7.0000000000000007E-2,100,0.6,4,100,0.4,0,6]
[19,19.7,310,21,1,0.15,0.15,200,0.6,3,1,0.8,0,22]
[19,19.600000000000001,310,21,50,0.15,0.15,200,0.6,3,54,0.8,0,22]
[19,19.600000000000001,310,21,60,0.15,0.15,200,0.6,3,65,0.8,0,22]
[19,19.600000000000001,310,21,70,0.15,0.15,200,0.6,3,76,0.8,0,22]
[19,19.600000000000001,310,21,80,0.15,0.15,200,0.6,3,87,0.8,0,22]
[19,19.600000000000001,310,21,90,0.15,0.15,200,0.6,3,98,0.8,0,22]
[19,20.399999999999999,310,21,99,0.32,0.11,200,0.6,4,100,0.8,0,22]
[19,19.5,310,21,1,0.16,0.16,300,0.6,3,1,1.2,0,44]
[19,19.5,310,21,50,0.16,0.16,300,0.6,3,55,1.2,0,44]
[19,19.5,310,21,60,0.16,0.16,300,0.6,3,66,1.2,0,44]
[19,19.5,310,21,70,0.16,0.16,300,0.6,3,77,1.2,0,44]
[19,19.5,310,21,80,0.16,0.16,300,0.6,3,88,1.2,0,44]
[19,19.5,310,21,90,0.16,0.15,300,0.6,4,98,1.2,0,44]
[19,20.100000000000001,310,21,99,0.38,0.13,300,0.6,4,100,1.2,0,44]
[19,20.6,310,22,1,0.19,0.19,100,0.6,3,1,0.4,0,6]
[19,20.6,310,22,50,0.19,0.19,100,0.6,3,55,0.4,0,6]
[19,20.6,310,22,60,0.19,0.19,100,0.6,3,67,0.4,0,6]
[19,20.6,310,22,70,0.18,0.18,100,0.6,3,78,0.4,0,6]
[19,20.6,310,22,80,0.18,0.18,100,0.6,3,89,0.4,0,6]
[19,20.6,310,22,90,0.18,0.16,100,0.6,4,98,0.4,0,6]
[19,21.5,310,22,99,0.28999999999999998,0.09,100,0.6,4,100,0.4,0,6]
[19,20,310,22,1,0.23,0.23,200,0.6,3,1,0.8,0,22]
[19,20,310,22,50,0.22,0.22,200,0.6,3,57,0.8,0,22]
[19,20,310,22,60,0.22,0.22,200,0.6,3,68,0.8,0,22]
[19,20,310,22,70,0.22,0.22,200,0.6,3,80,0.8,0,22]
[19,20,310,22,80,0.22,0.22,200,0.6,3,91,0.8,0,22]
[19,20.3,310,22,90,0.3,0.2,200,0.6,4,98,0.8,0,22]
[19,21.1,310,22,99,0.49,0.15,200,0.6,4,100,0.8,0,22]
[19,19.7,310,22,1,0.24,0.24,300,0.6,3,1,1.2,0,44]
[19,19.7,310,22,50,0.24,0.24,300,0.6,3,57,1.2,0,44]
[19,19.7,310,22,60,0.24,0.24,300,0.6,3,69,1.2,0,44]
[19,19.7,310,22,70,0.24,0.24,300,0.6,3,80,1.2,0,44]
[19,19.7,310,22,80,0.24,0.24,300,0.6,3,92,1.2,0,44]
[19,20,310,22,90,0.36,0.21,300,0.6,4,98,1.2,0,44]
[19,20.7,310,22,99,0.6,0.18,300,0.6,4,100,1.2,0,44]
[19,21.1,310,23,1,0.25,0.25,100,0.6,3,1,0.4,0,6]
[19,21.1,310,23,50,0.25,0.25,100,0.6,3,58,0.4,0,6]
[19,21.1,310,23,60,0.25,0.25,100,0.6,3,69,0.4,0,6]
[19,21.1,310,23,70,0.25,0.25,100,0.6,3,81,0.4,0,6]
[19,21.1,310,23,80,0.25,0.25,100,0.6,3,93,0.4,0,6]
[19,21.4,310,23,90,0.28000000000000003,0.19,100,0.6,4,99,0.4,0,6]
[19,22.4,310,23,99,0.4,0.12,100,0.6,4,100,0.4,0,6]
[19,20.3,310,23,1,0.3,0.3,200,0.6,3,1,0.8,0,22]
[19,20.3,310,23,50,0.3,0.3,200,0.6,3,59,0.8,0,22]
[19,20.3,310,23,60,0.3,0.3,200,0.6,3,72,0.8,0,22]
[19,20.3,310,23,70,0.3,0.3,200,0.6,3,83,0.8,0,22]
[19,20.3,310,23,80,0.3,0.3,200,0.6,3,96,0.8,0,22]
[19,21,310,23,90,0.47,0.24,200,0.6,4,98,0.8,0,22]
[19,21.9,310,23,99,0.67,0.19,200,0.6,4,100,0.8,0,22]
[19,19.899999999999999,310,23,1,0.32,0.32,300,0.6,3,1,1.2,0,44]
[19,19.899999999999999,310,23,50,0.32,0.32,300,0.6,3,60,1.2,0,44]
[19,19.899999999999999,310,23,60,0.32,0.32,300,0.6,3,72,1.2,0,44]
[19,19.899999999999999,310,23,70,0.32,0.32,300,0.6,3,84,1.2,0,44]
[19,19.899999999999999,310,23,80,0.31,0.31,300,0.6,3,97,1.2,0,44]
[19,20.6,310,23,90,0.56999999999999995,0.27,300,0.6,4,98,1.2,0,44]
[19,21.3,310,23,99,0.82,0.24,300,0.6,4,100,1.2,0,44]
[19,21.7,310,24,1,0.31,0.31,100,0.6,3,1,0.4,0,6]
[19,21.7,310,24,50,0.31,0.31,100,0.6,3,60,0.4,0,6]
[19,21.7,310,24,60,0.31,0.31,100,0.6,3,72,0.4,0,6]
[19,21.7,310,24,70,0.31,0.31,100,0.6,3,84,0.4,0,6]
[19,21.7,310,24,80,0.31,0.31,100,0.6,3,96,0.4,0,6]
[19,22.3,310,24,90,0.38,0.22,100,0.6,4,99,0.4,0,6]
[19,23.4,310,24,99,0.51,0.14000000000000001,100,0.6,4,100,0.4,0,6]
[19,20.6,310,24,1,0.38,0.38,200,0.6,3,1,0.8,0,22]
[19,20.6,310,24,50,0.37,0.37,200,0.6,3,62,0.8,0,22]
[19,20.6,310,24,60,0.37,0.37,200,0.6,3,75,0.8,0,22]
[19,20.6,310,24,70,0.37,0.37,200,0.6,3,87,0.8,0,22]
[19,20.7,310,24,80,0.41,0.34,200,0.6,4,97,0.8,0,22]
[19,21.8,310,24,90,0.64,0.28999999999999998,200,0.6,4,98,0.8,0,22]
[19,22.7,310,24,99,0.85,0.24,200,0.6,4,100,0.8,0,22]
[19,20.100000000000001,310,24,1,0.4,0.4,300,0.6,3,1,1.2,0,44]
[19,20.100000000000001,310,24,50,0.39,0.39,300,0.6,3,63,1.2,0,44]
[19,20.100000000000001,310,24,60,0.39,0.39,300,0.6,3,76,1.2,0,44]
[19,20.100000000000001,310,24,70,0.39,0.39,300,0.6,3,89,1.2,0,44]
[19,20.399999999999999,310,24,80,0.49,0.37,300,0.6,4,97,1.2,0,44]
[19,21.2,310,24,90,0.78,0.33,300,0.6,4,98,1.2,0,44]
[19,22,310,24,99,1.04,0.28999999999999998,300,0.6,4,100,1.2,0,44]
[19,22.2,310,25,1,0.37,0.37,100,0.6,3,1,0.4,0,6]
[19,22.2,310,25,50,0.37,0.37,100,0.6,3,62,0.4,0,6]
[19,22.2,310,25,60,0.37,0.37,100,0.6,3,75,0.4,0,6]
[19,22.2,310,25,70,0.37,0.37,100,0.6,3,87,0.4,0,6]
[19,22.2,310,25,80,0.37,0.37,100,0.6,3,100,0.4,0,6]
[19,23.2,310,25,90,0.49,0.24,100,0.6,4,99,0.4,0,6]
[19,24.3,310,25,99,0.62,0.17,100,0.6,4,100,0.4,0,6]
[19,20.9,310,25,1,0.45,0.45,200,0.6,3,1,0.8,0,22]
[19,20.9,310,25,50,0.45,0.45,200,0.6,3,65,0.8,0,22]
[19,20.9,310,25,60,0.45,0.45,200,0.6,3,78,0.8,0,22]
[19,20.9,310,25,70,0.45,0.45,200,0.6,3,92,0.8,0,22]
[19,21.5,310,25,80,0.56999999999999995,0.39,200,0.6,4,97,0.8,0,22]
[19,22.5,310,25,90,0.82,0.33,200,0.6,4,98,0.8,0,22]
[19,23.5,310,25,99,1.04,0.28000000000000003,200,0.6,4,100,0.8,0,21]
[19,20.399999999999999,310,25,1,0.48,0.48,300,0.6,3,1,1.2,0,44]
[19,20.399999999999999,310,25,50,0.47,0.47,300,0.6,3,66,1.2,0,44]
[19,20.399999999999999,310,25,60,0.47,0.47,300,0.6,3,79,1.2,0,44]
[19,20.399999999999999,310,25,70,0.47,0.47,300,0.6,3,93,1.2,0,44]
[19,21,310,25,80,0.7,0.43,300,0.6,4,97,1.2,0,44]
[19,21.9,310,25,90,1,0.38,300,0.6,4,98,1.2,0,44]
[19,22.7,310,25,99,1.28,0.34,300,0.6,4,100,1.2,0,44]
[19,22.7,310,26,1,0.43,0.43,100,0.6,3,1,0.4,0,6]
[19,22.7,310,26,50,0.43,0.43,100,0.6,3,64,0.4,0,6]
[19,22.7,310,26,60,0.43,0.43,100,0.6,3,77,0.4,0,6]
[19,22.7,310,26,70,0.43,0.43,100,0.6,3,91,0.4,0,6]
[19,22.8,310,26,80,0.44,0.35,100,0.6,4,97,0.4,0,6]
[19,24.1,310,26,90,0.59,0.26,100,0.6,4,99,0.4,0,6]
[19,25.3,310,26,99,0.73,0.19,100,0.6,4,100,0.4,0,6]
[19,21.3,310,26,1,0.52,0.52,200,0.6,3,1,0.8,0,22]
[19,21.2,310,26,50,0.52,0.52,200,0.6,3,68,0.8,0,22]
[19,21.2,310,26,60,0.52,0.52,200,0.6,3,82,0.8,0,22]
[19,21.2,310,26,70,0.52,0.52,200,0.6,3,96,0.8,0,22]
[19,22.2,310,26,80,0.74,0.43,200,0.6,4,97,0.8,0,22]
[19,23.3,310,26,90,1,0.37,200,0.6,4,98,0.8,0,22]
[19,24.3,310,26,99,1.23,0.32,200,0.6,4,100,0.8,0,21]
[19,20.6,310,26,1,0.55000000000000004,0.55000000000000004,300,0.6,3,1,1.2,0,44]
[19,20.6,310,26,50,0.55000000000000004,0.55000000000000004,300,0.6,3,69,1.2,0,44]
[19,20.6,310,26,60,0.55000000000000004,0.55000000000000004,300,0.6,3,83,1.2,0,44]
[19,20.7,310,26,70,0.57999999999999996,0.53,300,0.6,4,95,1.2,0,44]
[19,21.6,310,26,80,0.91,0.48,300,0.6,4,97,1.2,0,44]
[19,22.5,310,26,90,1.23,0.43,300,0.6,4,98,1.2,0,44]
[19,23.4,310,26,99,1.52,0.39,300,0.6,4,100,1.2,0,44]
[19,23.3,310,27,1,0.5,0.5,100,0.6,3,1,0.4,0,6]
[19,23.2,310,27,50,0.49,0.49,100,0.6,3,67,0.4,0,6]
[19,23.2,310,27,60,0.49,0.49,100,0.6,3,80,0.4,0,6]
[19,23.2,310,27,70,0.49,0.49,100,0.6,3,94,0.4,0,6]
[19,23.7,310,27,80,0.54,0.38,100,0.6,4,97,0.4,0,6]
[19,25.1,310,27,90,0.7,0.28999999999999998,100,0.6,4,99,0.4,0,6]
[19,26.2,310,27,99,0.84,0.21,100,0.6,4,100,0.4,0,6]
[19,21.6,310,27,1,0.6,0.6,200,0.6,3,1,0.8,0,22]
[19,21.6,310,27,50,0.59,0.59,200,0.6,3,71,0.8,0,22]
[19,21.6,310,27,60,0.59,0.59,200,0.6,3,86,0.8,0,22]
[19,21.8,310,27,70,0.64,0.55000000000000004,200,0.6,4,95,0.8,0,22]
[19,23,310,27,80,0.92,0.48,200,0.6,4,97,0.8,0,22]
[19,24.1,310,27,90,1.19,0.41,200,0.6,4,98,0.8,0,21]
[19,25.2,310,27,99,1.43,0.35,200,0.6,4,100,0.8,0,21]
[19,20.8,310,27,1,0.63,0.63,300,0.6,3,1,1.2,0,44]
[19,20.8,310,27,50,0.63,0.63,300,0.6,3,73,1.2,0,44]
[19,20.8,310,27,60,0.63,0.63,300,0.6,3,87,1.2,0,44]
[19,21.2,310,27,70,0.78,0.59,300,0.6,4,95,1.2,0,44]
[19,22.2,310,27,80,1.1200000000000001,0.54,300,0.6,4,97,1.2,0,44]
[19,23.2,310,27,90,1.46,0.49,300,0.6,4,98,1.2,0,44]
[19,24.1,310,27,99,1.77,0.44,300,0.6,4,100,1.2,0,44]
[19,20.2,380,21,1,0.14000000000000001,0.14000000000000001,100,0.74,4,1,0.4,0,6]
[19,20.2,380,21,50,0.13,0.13,100,0.74,4,53,0.4,0,6]
[19,20.2,380,21,60,0.13,0.13,100,0.74,4,64,0.4,0,6]
[19,20.2,380,21,70,0.13,0.13,100,0.74,4,74,0.4,0,6]
[19,20.2,380,21,80,0.13,0.13,100,0.74,4,85,0.4,0,6]
[19,20.2,380,21,90,0.13,0.13,100,0.74,4,96,0.4,0,6]
[19,20.7,380,21,99,0.19,7.0000000000000007E-2,100,0.74,6,100,0.4,0,6]
[19,19.7,380,21,1,0.17,0.17,200,0.74,4,1,0.8,0,22]
[19,19.7,380,21,50,0.17,0.17,200,0.74,4,54,0.8,0,22]
[19,19.7,380,21,60,0.17,0.17,200,0.74,4,65,0.8,0,22]
[19,19.7,380,21,70,0.17,0.17,200,0.74,4,76,0.8,0,22]
[19,19.7,380,21,80,0.17,0.17,200,0.74,4,87,0.8,0,22]
[19,19.7,380,21,90,0.17,0.17,200,0.74,4,98,0.8,0,22]
[19,20.399999999999999,380,21,99,0.33,0.11,200,0.74,6,100,0.8,0,22]
[19,19.5,380,21,1,0.18,0.18,300,0.74,4,1,1.2,0,44]
[19,19.5,380,21,50,0.18,0.18,300,0.74,4,54,1.2,0,44]
[19,19.5,380,21,60,0.18,0.18,300,0.74,4,65,1.2,0,44]
[19,19.5,380,21,70,0.18,0.18,300,0.74,4,76,1.2,0,44]
[19,19.5,380,21,80,0.18,0.18,300,0.74,4,87,1.2,0,44]
[19,19.5,380,21,90,0.18,0.18,300,0.74,4,98,1.2,0,44]
[19,20.2,380,21,99,0.42,0.14000000000000001,300,0.74,6,100,1.2,0,44]
[19,20.7,380,22,1,0.2,0.2,100,0.74,4,1,0.4,0,6]
[19,20.7,380,22,50,0.2,0.2,100,0.74,4,55,0.4,0,6]
[19,20.7,380,22,60,0.2,0.2,100,0.74,4,66,0.4,0,6]
[19,20.7,380,22,70,0.2,0.2,100,0.74,4,77,0.4,0,6]
[19,20.7,380,22,80,0.2,0.2,100,0.74,4,88,0.4,0,6]
[19,20.7,380,22,90,0.2,0.2,100,0.74,4,99,0.4,0,6]
[19,21.6,380,22,99,0.3,0.1,100,0.74,6,100,0.4,0,6]
[19,20.100000000000001,380,22,1,0.26,0.26,200,0.74,4,1,0.8,0,22]
[19,20.100000000000001,380,22,50,0.25,0.25,200,0.74,4,56,0.8,0,22]
[19,20.100000000000001,380,22,60,0.25,0.25,200,0.74,4,67,0.8,0,22]
[19,20.100000000000001,380,22,70,0.25,0.25,200,0.74,4,79,0.8,0,22]
[19,20.100000000000001,380,22,80,0.25,0.25,200,0.74,4,91,0.8,0,22]
[19,20.399999999999999,380,22,90,0.32,0.22,200,0.74,6,98,0.8,0,22]
[19,21.2,380,22,99,0.52,0.16,200,0.74,6,100,0.8,0,22]
[19,19.8,380,22,1,0.27,0.27,300,0.74,4,1,1.2,0,44]
[19,19.8,380,22,50,0.27,0.27,300,0.74,4,57,1.2,0,44]
[19,19.8,380,22,60,0.27,0.27,300,0.74,4,68,1.2,0,44]
[19,19.8,380,22,70,0.27,0.27,300,0.74,4,80,1.2,0,44]
[19,19.8,380,22,80,0.27,0.27,300,0.74,4,91,1.2,0,44]
[19,20.100000000000001,380,22,90,0.39,0.24,300,0.74,6,98,1.2,0,44]
[19,20.9,380,22,99,0.65,0.2,300,0.74,6,100,1.2,0,44]
[19,21.3,380,23,1,0.27,0.27,100,0.74,4,1,0.4,0,6]
[19,21.3,380,23,50,0.27,0.27,100,0.74,4,57,0.4,0,6]
[19,21.3,380,23,60,0.27,0.27,100,0.74,4,68,0.4,0,6]
[19,21.3,380,23,70,0.27,0.27,100,0.74,4,80,0.4,0,6]
[19,21.3,380,23,80,0.27,0.27,100,0.74,4,91,0.4,0,6]
[19,21.5,380,23,90,0.28999999999999998,0.21,100,0.74,6,98,0.4,0,6]
[19,22.5,380,23,99,0.41,0.12,100,0.74,6,100,0.4,0,6]
[19,20.5,380,23,1,0.34,0.34,200,0.74,4,1,0.8,0,22]
[19,20.5,380,23,50,0.34,0.34,200,0.74,4,59,0.8,0,22]
[19,20.5,380,23,60,0.34,0.34,200,0.74,4,70,0.8,0,22]
[19,20.5,380,23,70,0.34,0.34,200,0.74,4,82,0.8,0,22]
[19,20.5,380,23,80,0.34,0.34,200,0.74,4,94,0.8,0,22]
[19,21.1,380,23,90,0.49,0.27,200,0.74,6,98,0.8,0,22]
[19,22,380,23,99,0.71,0.21,200,0.74,6,100,0.8,0,22]
[19,20,380,23,1,0.36,0.36,300,0.74,4,1,1.2,0,44]
[19,20,380,23,50,0.36,0.36,300,0.74,4,59,1.2,0,44]
[19,20,380,23,60,0.36,0.36,300,0.74,4,71,1.2,0,44]
[19,20,380,23,70,0.36,0.36,300,0.74,4,83,1.2,0,44]
[19,20,380,23,80,0.36,0.36,300,0.74,4,95,1.2,0,44]
[19,20.8,380,23,90,0.62,0.3,300,0.74,6,98,1.2,0,44]
[19,21.5,380,23,99,0.88,0.26,300,0.74,6,100,1.2,0,44]
[19,21.9,380,24,1,0.34,0.34,100,0.74,4,1,0.4,0,6]
[19,21.9,380,24,50,0.34,0.34,100,0.74,4,59,0.4,0,6]
[19,21.9,380,24,60,0.34,0.34,100,0.74,4,70,0.4,0,6]
[19,21.9,380,24,70,0.34,0.34,100,0.74,4,82,0.4,0,6]
[19,21.9,380,24,80,0.34,0.34,100,0.74,4,94,0.4,0,6]
[19,22.4,380,24,90,0.39,0.24,100,0.74,6,98,0.4,0,6]
[19,23.5,380,24,99,0.52,0.15,100,0.74,6,100,0.4,0,6]
[19,20.8,380,24,1,0.42,0.42,200,0.74,4,1,0.8,0,22]
[19,20.8,380,24,50,0.42,0.42,200,0.74,4,61,0.8,0,22]
[19,20.8,380,24,60,0.42,0.42,200,0.74,4,73,0.8,0,22]
[19,20.8,380,24,70,0.42,0.42,200,0.74,4,86,0.8,0,22]
[19,20.8,380,24,80,0.43,0.39,200,0.74,6,96,0.8,0,22]
[19,21.9,380,24,90,0.68,0.31,200,0.74,6,98,0.8,0,22]
[19,22.9,380,24,99,0.9,0.25,200,0.74,6,100,0.8,0,22]
[19,20.3,380,24,1,0.45,0.45,300,0.74,4,1,1.2,0,44]
[19,20.3,380,24,50,0.45,0.45,300,0.74,4,62,1.2,0,44]
[19,20.3,380,24,60,0.45,0.45,300,0.74,4,75,1.2,0,44]
[19,20.3,380,24,70,0.45,0.45,300,0.74,4,87,1.2,0,44]
[19,20.5,380,24,80,0.53,0.42,300,0.74,6,96,1.2,0,44]
[19,21.4,380,24,90,0.85,0.37,300,0.74,6,98,1.2,0,44]
[19,22.2,380,24,99,1.1299999999999999,0.32,300,0.74,6,100,1.2,0,44]
[19,22.5,380,25,1,0.41,0.41,100,0.74,4,1,0.4,0,6]
[19,22.5,380,25,50,0.4,0.4,100,0.74,4,60,0.4,0,6]
[19,22.5,380,25,60,0.4,0.4,100,0.74,4,73,0.4,0,6]
[19,22.5,380,25,70,0.4,0.4,100,0.74,4,85,0.4,0,6]
[19,22.5,380,25,80,0.4,0.4,100,0.74,4,97,0.4,0,6]
[19,23.3,380,25,90,0.5,0.26,100,0.74,6,98,0.4,0,6]
[19,24.4,380,25,99,0.63,0.17,100,0.74,6,100,0.4,0,6]
[19,21.2,380,25,1,0.51,0.51,200,0.74,4,1,0.8,0,22]
[19,21.2,380,25,50,0.51,0.51,200,0.74,4,64,0.8,0,22]
[19,21.2,380,25,60,0.5,0.5,200,0.74,4,77,0.8,0,22]
[19,21.2,380,25,70,0.5,0.5,200,0.74,4,90,0.8,0,22]
[19,21.6,380,25,80,0.6,0.44,200,0.74,6,96,0.8,0,22]
[19,22.7,380,25,90,0.86,0.36,200,0.74,6,98,0.8,0,22]
[19,23.7,380,25,99,1.0900000000000001,0.28999999999999998,200,0.74,6,100,0.8,0,21]
[19,20.6,380,25,1,0.55000000000000004,0.55000000000000004,300,0.74,4,1,1.2,0,44]
[19,20.6,380,25,50,0.54,0.54,300,0.74,4,65,1.2,0,44]
[19,20.6,380,25,60,0.54,0.54,300,0.74,4,78,1.2,0,44]
[19,20.5,380,25,70,0.54,0.54,300,0.74,4,91,1.2,0,44]
[19,21.2,380,25,80,0.75,0.48,300,0.74,6,96,1.2,0,44]
[19,22.1,380,25,90,1.0900000000000001,0.42,300,0.74,6,98,1.2,0,44]
[19,23,380,25,99,1.38,0.37,300,0.74,6,100,1.2,0,44]
[19,23.1,380,26,1,0.47,0.47,100,0.74,4,1,0.4,0,6]
[19,23.1,380,26,50,0.47,0.47,100,0.74,4,62,0.4,0,6]
[19,23.1,380,26,60,0.47,0.47,100,0.74,4,75,0.4,0,6]
[19,23.1,380,26,70,0.47,0.47,100,0.74,4,88,0.4,0,6]
[19,22.9,380,26,80,0.45,0.4,100,0.74,6,96,0.4,0,6]
[19,24.2,380,26,90,0.6,0.28999999999999998,100,0.74,6,98,0.4,0,6]
[19,25.4,380,26,99,0.74,0.19,100,0.74,6,100,0.4,0,6]
[19,21.6,380,26,1,0.59,0.59,200,0.74,4,1,0.8,0,22]
[19,21.5,380,26,50,0.59,0.59,200,0.74,4,66,0.8,0,22]
[19,21.5,380,26,60,0.59,0.59,200,0.74,4,80,0.8,0,22]
[19,21.5,380,26,70,0.59,0.59,200,0.74,4,93,0.8,0,22]
[19,22.4,380,26,80,0.78,0.49,200,0.74,6,96,0.8,0,22]
[19,23.5,380,26,90,1.06,0.4,200,0.74,6,98,0.8,0,21]
[19,24.6,380,26,99,1.3,0.33,200,0.74,6,100,0.8,0,21]
[19,20.8,380,26,1,0.63,0.63,300,0.74,4,1,1.2,0,44]
[19,20.8,380,26,50,0.63,0.63,300,0.74,4,68,1.2,0,44]
[19,20.8,380,26,60,0.63,0.63,300,0.74,4,81,1.2,0,44]
[19,20.8,380,26,70,0.63,0.63,300,0.74,4,95,1.2,0,44]
[19,21.8,380,26,80,0.98,0.54,300,0.74,6,96,1.2,0,44]
[19,22.8,380,26,90,1.33,0.48,300,0.74,6,98,1.2,0,44]
[19,23.7,380,26,99,1.64,0.42,300,0.74,6,100,1.2,0,44]
[19,23.7,380,27,1,0.54,0.54,100,0.74,4,1,0.4,0,6]
[19,23.6,380,27,50,0.54,0.54,100,0.74,4,65,0.4,0,6]
[19,23.6,380,27,60,0.54,0.54,100,0.74,4,78,0.4,0,6]
[19,23.6,380,27,70,0.54,0.54,100,0.74,4,91,0.4,0,6]
[19,23.8,380,27,80,0.56000000000000005,0.43,100,0.74,6,96,0.4,0,6]
[19,25.2,380,27,90,0.71,0.31,100,0.74,6,98,0.4,0,6]
[19,26.4,380,27,99,0.85,0.21,100,0.74,6,100,0.4,0,6]
[19,21.9,380,27,1,0.68,0.68,200,0.74,4,1,0.8,0,22]
[19,21.9,380,27,50,0.67,0.67,200,0.74,4,69,0.8,0,22]
[19,21.9,380,27,60,0.67,0.67,200,0.74,4,83,0.8,0,22]
[19,21.9,380,27,70,0.67,0.62,200,0.74,6,94,0.8,0,22]
[19,23.2,380,27,80,0.97,0.53,200,0.74,6,96,0.8,0,22]
[19,24.4,380,27,90,1.25,0.45,200,0.74,6,98,0.8,0,21]
[19,25.5,380,27,99,1.5,0.37,200,0.74,6,100,0.8,0,21]
[19,21.1,380,27,1,0.72,0.72,300,0.74,4,1,1.2,0,44]
[19,21.1,380,27,50,0.72,0.72,300,0.74,4,71,1.2,0,44]
[19,21.1,380,27,60,0.72,0.72,300,0.74,4,85,1.2,0,44]
[19,21.4,380,27,70,0.84,0.67,300,0.74,6,94,1.2,0,44]
[19,22.5,380,27,80,1.21,0.6,300,0.74,6,96,1.2,0,44]
[19,23.5,380,27,90,1.58,0.53,300,0.74,6,98,1.2,0,44]
[19,24.5,380,27,99,1.91,0.47,300,0.74,6,100,1.2,0,44]

{"sheet":"Ausw_Vergleich_sf_vs_S5","index":10,"n_rows":58,"n_cols":21,"rows_kept":58,"cut":false,"hidden":true,"merged":[]}
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Baugröße 800"]
[]
["Schieberstellung","Primärdruck","Primär- volumenstrom","Primär- volumenstrom","Primärdruck","Sekundärvolumenstrom","LWA","LA18","QPK","QSK1","QKges1","QTotal2","QSensibel,K2","QKges2","QPH","QSH","Qhges"]
[null,"[Pa]","[m³/h]","[m³/h]","[Pa]","[m³/h]","[dB(A)]","[dB(A)]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]"]
[5,250,162.25076086206127,162.25076086206127,250,274.93215493703809,41.093038787341449,34.593038787341449,-430,-620.21647574210601,-1050.216475742106,-1604.9562811499327,-1116.6034441442205,-1546.6034441442205,-430,1649.7617516068519,1219.7617516068519]
[4.5,250,140.76265663814229,140.76265663814229,250,231.87046370302414,39.761837239080258,33.261837239080258,-380,-544.30416848819686,-924.30416848819686,-1458.965316023324,-990.72149108591316,-1370.7214910859132,-380,1447.8367369031116,1067.8367369031116]
[4,250,110.09071653442803,110.09071653442803,250,159.35944644200444,39.407674231528304,32.907674231528304,-290,-414.98949949556254,-704.98949949556254,-1183.6051501457566,-773.77532269344113,-1063.775322693441,-290,1103.8626517734265,813.86265177342648]
[3.5,250,89.125431355045251,89.125431355045251,250,128.27460700077256,37.86369210988552,31.36369210988552,-240,-332.40505176757642,-572.40505176757642,-973.534904983351,-627.11969332965282,-867.11969332965282,-240,884.18989481193728,644.18989481193728]
[3,250,75.568615419054666,75.568615419054666,250,137.62920666556522,39.260957470281681,32.760957470281681,-200,-353.4342482418698,-553.4342482418698,-1026.9496512268122,-664.39913995542997,-864.39913995542997,-200,940.12708024191727,740.12708024191727]
[2.5,250,74.833879205090852,74.833879205090852,250,129.15196295458193,36.541005975572276,30.041005975572276,-200,-327.29693259435101,-527.29693259435101,-957.86408340706714,-617.27319177321931,-817.27319177321931,-200,870.60241372389692,670.60241372389692]
[2,250,54.671978085075104,54.671978085075104,250,104.01504920638178,35.856060398476274,29.356060398476274,-150,-206.03008434505347,-356.03008434505347,-615.76929687534493,-392.41061410747318,-542.41061410747318,-150,548.0353491514436,398.0353491514436]
[]
[]
["Baugröße 800"]
[]
["Schieberstellung","Primär- volumenstrom","Primärdruck","Primär- volumenstrom","Primärdruck","Sekundärvolumenstrom","LWA","LA18","QPK","QSK1","QKges1","QTotal2","QSensibel,K2","QKges2","QPH","QSH","Qhges"]
[null,"[m³/h]","[Pa]","[m³/h]","[Pa]","[m³/h]","[dB(A)]","[dB(A)]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]"]
[5,162.25076086206127,249.9934128581975,162.25076086206127,249.9934128581975,272.28530417264045,41.092631379840618,34.592631379840618,-430,-631.34379085152,-1061.34379085152,-1637.1733985392586,-1137.2966827226694,-1567.2966827226694,-430,1679.3601572983857,1249.3601572983857,null,{"$f":"ABS(N45)","v":1567.2966827226694},null,{"$f":"100/N32*N45-100","v":1.337979600187623}]
[5,140.76265663814229,187.36296451285625,140.76265663814229,187.36296451285625,226.63972350620912,36.633587528398046,30.133587528398046,-380,-560.25045277201252,-940.25045277201252,-1508.3401753894066,-1021.306061378125,-1401.3060613781249,-380,1490.2534912471667,1110.2534912471667,null,{"$f":"ABS(N46)","v":1401.3060613781249},null,{"$f":"100/N33*N46-100","v":2.2312753167663715}]
[5,110.09071653442803,113.76700595870729,110.09071653442803,113.76700595870729,160.04541302077641,28.919659247956552,22.419659247956552,-290,-429.91063142280632,-719.91063142280632,-1225.4397409658786,-801.39460619275951,-1091.3946061927595,-290,1143.5525241116165,853.55252411161655,null,1091.3946061927595,null,2.5963455731786951]
[5,89.125431355045251,74.092251836621884,89.125431355045251,74.092251836621884,116.47741799779506,22.288901080688213,15.788901080688213,-240,-331.28480860996484,-571.28480860996478,-979.9228481969003,-627.88451649456977,-867.88451649456977,-240,881.21007343309441,641.21007343309441,null,867.88451649456977,null,8.820272112377836E-2]
[5,75.568615419054694,53.003937258054989,75.568615419054666,53.003937258054989,90.276304574413146,"<20","",-200,-267.24115522474187,-467.24115522474187,-807.74646327409073,-511.7802888361141,-711.7802888361141,-200,710.85540869819488,510.85540869819488,null,711.7802888361141,null,-17.656062351841896]
[5,74.833879205090852,51.963063579465484,74.833879205090852,51.963063579465484,88.914200891938066,"<20","",-200,-263.81090259791063,-463.81090259791063,-798.25947585240567,-505.48552445118503,-705.48552445118503,-200,701.73101454964535,501.73101454964535,null,705.48552445118503,null,-13.678127270942426]
[]
[]
[]
[]
["Auslegung Indkutionsgerät für 250 Pa --> Primärvolumenstrom = 162m³/h"]
[]
["Induktionsverhältnis bricht ab 46% Primärvolumenstrom ein (nur noch ein Primärdruck von 53Pa)"]
[{"$f":"100/B45*B49","v":46.575199412038465},"%"]

{"sheet":"Tabelle2","index":11,"n_rows":59,"n_cols":78,"rows_kept":59,"cut":false,"hidden":true,"merged":[]}
[]
[]
[]
[]
[]
[null,null,null,null,"Baugröße 630",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Baugröße 630"]
[]
["Gesamtkühl","Gesamtkühl","Sensibel","Sensibel","Schieberstellung","Primärdruck","Primär- volumenstrom","Primär- volumenstrom","Primärdruck","Sekundärvolumenstrom","LWA","LA18","QPK","QSK1","QKges1","QTotal2","QSensibel,K2","QKges2","QPH","QSH","Qhges",null,null,"Schieberstellung","Primär- volumenstrom","Primärdruck","Primär- volumenstrom","Primärdruck","Sekundärvolumenstrom","LWA","LA18","QPK","QSK1","QKges1","QTotal2","QSensibel,K2","QKges2","QPH","QSH","Qhges",null,null,"Schieberstellung","Primärdruck","Primär- volumenstrom","Primär- volumenstrom","Primärdruck","Sekundärvolumenstrom","LWA","LA18","QPK","QSK1","QKges1","QTotal2","QSensibel,K2","QKges2","QPH","QSH","Qhges",null,null,"Schieberstellung","Primärdruck","Primär- volumenstrom","Primär- volumenstrom","Primärdruck","Sekundärvolumenstrom","LWA","LA18","QPK","QSK1","QKges1","QTotal2","QSensibel,K2","QKges2","QPH","QSH","Qhges"]
["2)","1)","2)","1)",null,"[Pa]","[m³/h]","[m³/h]","[Pa]","[m³/h]","[dB(A)]","[dB(A)]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]",null,null,null,"[m³/h]","[Pa]","[m³/h]","[Pa]","[m³/h]","[dB(A)]","[dB(A)]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]",null,null,null,"[Pa]","[m³/h]","[m³/h]","[Pa]","[m³/h]","[dB(A)]","[dB(A)]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]",null,null,null,"[Pa]","[m³/h]","[m³/h]","[Pa]","[m³/h]","[dB(A)]","[dB(A)]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]"]
[{"$f":"100/R10*AK10-100","v":1.1076595329368786},{"$f":"100/O10*AH10-100","v":-0.26208092813236306},{"$f":"100/Q10*AJ10-100","v":1.5385266917251528},{"$f":"100/N10*AG10-100","v":-0.44985280208486245},5,150,90.769849064647957,90.769849064647957,150,139.626823769666,31.765023198913539,25.265023198913539,-240,334.97787196652666,574.97787196652666,927.28228767376334,616.98433608276912,856.98433608276912,240,571.99333797095846,331.99333797095846,null,null,5,90.769849064647957,148.52993880744302,90.769849064647957,148.52993880744302,139.27903448873624,21.43310887511231,14.93310887511231,-240,333.47096462312101,573.47096462312106,967.58469114074501,626.47680477716574,866.47680477716574,240,569.69916091928121,329.69916091928121,null,null,{"$f":"ABS(E10)","v":5},150,90.769849064647957,90.769849064647957,150,139.626823769666,31.765023198913539,25.265023198913539,240,334.97787196652666,574.97787196652666,927.28228767376334,616.98433608276912,856.98433608276912,240,571.99333797095846,331.99333797095846,null,null,{"$f":"ABS(X10)","v":5},90.769849064647957,148.52993880744302,90.769849064647957,148.52993880744302,139.27903448873624,21.43310887511231,14.93310887511231,240,333.47096462312101,{"$f":"ABS(AH10)","v":573.47096462312106},967.58469114074501,626.47680477716574,866.47680477716574,240,569.69916091928121,329.69916091928121]
[{"$f":"100/R11*AK11-100","v":-2.5100120002861104},{"$f":"100/O11*AH11-100","v":-3.395054183725307},{"$f":"100/Q11*AJ11-100","v":-3.4523397680589483},{"$f":"100/N11*AG11-100","v":-5.758479434878268},4.5,150,78.12739140058693,78.12739140058693,150,125.69086962916751,30.166861492684887,23.666861492684887,-210,301.66445003263823,511.66445003263823,849.11077878472906,559.36218594712091,769.36218594712091,210,525.6469414438717,315.6469414438717,null,null,5,78.12739140058693,109.54391943127199,78.12739140058693,109.54391943127199,110.67363019215398,"<20","",-210,284.29316471517012,494.29316471517012,845.00310869063867,540.05110275418463,750.05110275418463,210,507.007554954037,297.007554954037,null,null,{"$f":"ABS(E11)","v":4.5},{"$f":"ABS(F11)","v":150},78.12739140058693,78.12739140058693,150,125.69086962916751,30.166861492684887,23.666861492684887,210,301.66445003263823,511.66445003263823,849.11077878472906,559.36218594712091,769.36218594712091,210,525.6469414438717,315.6469414438717,null,null,5,78.12739140058693,109.54391943127199,78.12739140058693,109.54391943127199,110.67363019215398,{"$error":"#VALUE!"},{"$error":"#VALUE!"},210,284.29316471517012,494.29316471517012,845.00310869063867,540.05110275418463,750.05110275418463,210,507.007554954037,297.007554954037]
[-3.5701117202639523,-3.6840906972056757,-4.963057926635372,-6.4104659557946349,4,150,60.849132028465895,60.849132028465895,150,82.435958571942862,29.932937737454942,23.432937737454942,-160,216.2044677070551,376.20446770705507,640.54005657612311,410.07891950848204,570.07891950848204,160,404.19770639753153,244.19770639753153,null,null,5,60.849132028465895,65.954171518960237,60.849132028465895,65.954171518960237,75.926879149765796,"<20","",-160,202.34475390978733,362.3447539097873,618.68617866558418,389.72646518835563,549.72646518835563,160,382.64664663431756,222.64664663431756,null,null,4,150,60.849132028465895,60.849132028465895,150,82.435958571942862,29.932937737454942,23.432937737454942,160,216.2044677070551,376.20446770705507,640.54005657612311,410.07891950848204,570.07891950848204,160,404.19770639753153,244.19770639753153,null,null,5,60.849132028465895,65.954171518960237,60.849132028465895,65.954171518960237,75.926879149765796,{"$error":"#VALUE!"},{"$error":"#VALUE!"},160,202.34475390978733,362.3447539097873,618.68617866558418,389.72646518835563,549.72646518835563,160,382.64664663431756,222.64664663431756]
[-9.6371905226780115,-8.3662063773913928,-13.53326889563489,-14.833891423677173,3.5,150,49.060732633053433,49.060732633053433,150,67.605973785002831,29.583315032075156,23.083315032075156,-130,168.16014095885319,298.16014095885316,506.74920156181599,321.56303031381685,451.56303031381685,130,322.78740698185607,192.78740698185607,null,null,5,49.060732633053433,42.599364667943355,49.060732633053433,42.599364667943355,55.99140462081354,"<20","",-130,143.21544823111441,273.21544823111441,444.77394173169841,278.04504075249611,408.04504075249611,130,280.83909436224002,150.83909436224002,null,null,3.5,150,49.060732633053433,49.060732633053433,150,67.605973785002831,29.583315032075156,23.083315032075156,130,168.16014095885319,298.16014095885316,506.74920156181599,321.56303031381685,451.56303031381685,130,322.78740698185607,192.78740698185607,null,null,5,49.060732633053433,42.599364667943355,49.060732633053433,42.599364667943355,55.99140462081354,{"$error":"#VALUE!"},{"$error":"#VALUE!"},130,143.21544823111441,273.21544823111441,444.77394173169841,278.04504075249611,408.04504075249611,130,280.83909436224002,150.83909436224002]
[-29.890405165128371,-25.31719813465044,-39.450412767368022,-40.765141779696052,3,150,41.441045028538731,41.441045028538731,150,71.835916906189041,30.984299539401228,24.484299539401228,-110,180.275890358048,290.275890358048,540.65232546852576,343.92698258878409,453.92698258878409,110,343.41251227631147,233.41251227631147,null,null,5,41.441045028538731,30.241476321157393,41.441045028538731,30.241476321157393,44.771320450717454,"<20","",-110,106.78616805898032,216.78616805898031,334.47958400562533,208.2463683391548,318.2463683391548,110,213.87579661466401,103.87579661466401,null,null,3,{"$f":"ABS(F14)","v":150},{"$f":"ABS(G14)","v":41.441045028538731},{"$f":"ABS(H14)","v":41.441045028538731},{"$f":"ABS(I14)","v":150},{"$f":"ABS(J14)","v":71.835916906189041},{"$f":"ABS(K14)","v":30.984299539401228},{"$f":"ABS(L14)","v":24.484299539401228},{"$f":"ABS(M14)","v":110},{"$f":"ABS(N14)","v":180.275890358048},{"$f":"ABS(O14)","v":290.275890358048},{"$f":"ABS(P14)","v":540.65232546852576},{"$f":"ABS(Q14)","v":343.92698258878409},{"$f":"ABS(R14)","v":453.92698258878409},{"$f":"ABS(S14)","v":110},{"$f":"ABS(T14)","v":343.41251227631147},{"$f":"ABS(U14)","v":233.41251227631147},null,null,{"$f":"ABS(X14)","v":5},{"$f":"ABS(Y14)","v":41.441045028538731},{"$f":"ABS(Z14)","v":30.241476321157393},{"$f":"ABS(AA14)","v":41.441045028538731},{"$f":"ABS(AB14)","v":30.241476321157393},{"$f":"ABS(AC14)","v":44.771320450717454},{"$f":"ABS(AD14)","v":{"$error":"#VALUE!"}},{"$f":"ABS(AE14)","v":{"$error":"#VALUE!"}},{"$f":"ABS(AF14)","v":110},{"$f":"ABS(AG14)","v":106.78616805898032},{"$f":"ABS(AH14)","v":216.78616805898031},{"$f":"ABS(AI14)","v":334.47958400562533},{"$f":"ABS(AJ14)","v":208.2463683391548},{"$f":"ABS(AK14)","v":318.2463683391548},{"$f":"ABS(AL14)","v":110},{"$f":"ABS(AM14)","v":213.87579661466401},{"$f":"ABS(AN14)","v":103.87579661466401}]
[-26.101353053975814,-21.863819760358638,-35.199043465583145,-36.443179150375919,2.5,150,41.017447835138597,41.017447835138597,150,66.768327830621999,27.959813768757876,21.459813768757876,-110,164.96062064882008,274.96062064882005,497.57925217926118,315.59095836830983,425.59095836830983,110,317.12783464614625,207.12783464614625,null,null,5,41.017447835138597,29.61729158346937,41.017447835138597,29.61729158346937,44.184081635986878,"<20","",-110,104.84372613819858,214.84372613819858,328.54036347758603,204.50595975879804,314.50595975879804,110,210.22046250057755,100.22046250057755,null,null,2.5,150,41.017447835138597,41.017447835138597,150,66.768327830621999,27.959813768757876,21.459813768757876,110,164.96062064882008,274.96062064882005,497.57925217926118,315.59095836830983,425.59095836830983,110,317.12783464614625,207.12783464614625,null,null,5,41.017447835138597,29.61729158346937,41.017447835138597,29.61729158346937,44.184081635986878,{"$error":"#VALUE!"},{"$error":"#VALUE!"},110,104.84372613819858,214.84372613819858,328.54036347758603,204.50595975879804,314.50595975879804,110,210.22046250057755,100.22046250057755]
[-31.368682825870494,-25.307693169401986,-43.914112027303069,-44.837163537967605,2,150,29.567268444332935,29.567268444332935,150,51.394003112134882,25.828845965361189,19.328845965361189,-80,103.66975731256662,183.66975731256662,318.11046998003582,200.03258443984333,280.03258443984333,80,205.04826125649987,125.04826125649987,null,null,5,29.567268444332935,15.239708929115846,29.567268444332935,15.239708929115846,29.632407606208488,"<20","",-80,57.187178686916994,137.18717868691698,181.14210491250148,112.19005121782092,192.19005121782092,80,117.93156613562482,37.93156613562482,null,null,2,150,29.567268444332935,29.567268444332935,150,51.394003112134882,25.828845965361189,19.328845965361189,80,103.66975731256662,183.66975731256662,318.11046998003582,200.03258443984333,280.03258443984333,80,205.04826125649987,125.04826125649987,null,null,5,29.567268444332935,15.239708929115846,29.567268444332935,15.239708929115846,29.632407606208488,{"$error":"#VALUE!"},{"$error":"#VALUE!"},80,57.187178686916994,137.18717868691698,181.14210491250148,112.19005121782092,192.19005121782092,80,117.93156613562482,37.93156613562482]
[]
[]
[]
[null,null,null,null,"",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,null,null,null,"  Minimal",45,"Pa",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"  Minimal",15.085966929843767,"m³/h"]
[null,null,null,null,"  Maximal",305,"Pa",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"  Maximal",128.75555794011112,"m³/h"]
[]
[]
[null,null,null,null,"Baugröße 800",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Baugröße 800"]
[]
["Gesamtkühl","Gesamtkühl","Sensibel","Sensibel","Schieberstellung","Primärdruck","Primär- volumenstrom","Primär- volumenstrom","Primärdruck","Sekundärvolumenstrom","LWA","LA18","QPK","QSK1","QKges1","QTotal2","QSensibel,K2","QKges2","QPH","QSH","Qhges",null,null,"Schieberstellung","Primär- volumenstrom","Primärdruck","Primär- volumenstrom","Primärdruck","Sekundärvolumenstrom","LWA","LA18","QPK","QSK1","QKges1","QTotal2","QSensibel,K2","QKges2","QPH","QSH","Qhges",null,null,"Schieberstellung","Primärdruck","Primär- volumenstrom","Primär- volumenstrom","Primärdruck","Sekundärvolumenstrom","LWA","LA18","QPK","QSK1","QKges1","QTotal2","QSensibel,K2","QKges2","QPH","QSH","Qhges",null,null,"Schieberstellung","Primärdruck","Primär- volumenstrom","Primär- volumenstrom","Primärdruck","Sekundärvolumenstrom","LWA","LA18","QPK","QSK1","QKges1","QTotal2","QSensibel,K2","QKges2","QPH","QSH","Qhges"]
["2)","1)","2)","1)",null,"[Pa]","[m³/h]","[m³/h]","[Pa]","[m³/h]","[dB(A)]","[dB(A)]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]",null,null,null,"[m³/h]","[Pa]","[m³/h]","[Pa]","[m³/h]","[dB(A)]","[dB(A)]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]",null,null,null,"[Pa]","[m³/h]","[m³/h]","[Pa]","[m³/h]","[dB(A)]","[dB(A)]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]",null,null,null,"[Pa]","[m³/h]","[m³/h]","[Pa]","[m³/h]","[dB(A)]","[dB(A)]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]"]
[{"$f":"100/R29*AK29-100","v":0.20784427136291583},{"$f":"100/O29*AH29-100","v":3.7424341371661285E-5},{"$f":"100/Q29*AJ29-100","v":0.29120441920316864},{"$f":"100/N29*AG29-100","v":6.5070360406593863E-5},5,150,126.15470547968022,126.15470547968022,150,194.05761947648497,33.194641606329263,26.694641606329263,-340,460.25708300255809,800.25708300255815,1274.0789065831577,847.73184902225921,1187.7318490222592,340,785.72023167313182,445.72023167313182,null,null,5,126.15470547968022,150.00021487773256,126.15470547968022,150.00021487773256,185.52455953044088,33.194663755941995,26.694663755941995,-340,460.25738249350076,800.2573824935007,1283.4721150406835,850.20048162960484,1190.2004816296048,340,793.52417730507045,453.52417730507045,null,null,{"$f":"ABS(E29)","v":5},{"$f":"ABS(F29)","v":150},126.15470547968022,126.15470547968022,150,194.05761947648497,33.194641606329263,26.694641606329263,340,460.25708300255809,800.25708300255815,1274.0789065831577,847.73184902225921,1187.7318490222592,340,785.72023167313182,445.72023167313182,null,null,{"$f":"ABS(X29)","v":5},126.15470547968022,150.00021487773256,126.15470547968022,150.00021487773256,185.52455953044088,33.194663755941995,26.694663755941995,340,460.25738249350076,800.2573824935007,1283.4721150406835,850.20048162960484,1190.2004816296048,{"$f":"ABS(AL29)","v":340},793.52417730507045,453.52417730507045]
[{"$f":"100/R30*AK30-100","v":-3.269954291878534},{"$f":"100/O30*AH30-100","v":-3.082438481355382},{"$f":"100/Q30*AJ30-100","v":-4.5038516361261571},{"$f":"100/N30*AG30-100","v":-5.2391930951132224},4.5,150,108.58383211606997,108.58383211606997,150,174.68900524731754,31.596479900100611,25.096479900100611,-290,414.46864371629033,704.46864371629033,1166.6266701618738,768.52969095496394,1058.5296909549638,290,724.25544322136955,434.25544322136955,null,null,5,108.58383211606997,110.62827861621955,108.58383211606997,110.62827861621955,153.45963160147647,28.487081195976479,21.987081195976479,-290,392.75383115329703,682.75383115329703,1125.8724944368003,733.91625389477349,1023.9162538947735,290,706.68584894752144,416.68584894752144,null,null,{"$f":"ABS(E30)","v":4.5},150,108.58383211606997,108.58383211606997,150,174.68900524731754,31.596479900100611,25.096479900100611,290,414.46864371629033,704.46864371629033,1166.6266701618738,768.52969095496394,1058.5296909549638,290,724.25544322136955,434.25544322136955,null,null,5,108.58383211606997,110.62827861621955,108.58383211606997,110.62827861621955,153.45963160147647,28.487081195976479,21.987081195976479,290,392.75383115329703,682.75383115329703,1125.8724944368003,733.91625389477349,1023.9162538947735,290,706.68584894752144,416.68584894752144]
[-4.0418913219446893,-3.2596772184960514,-5.6967573370955336,-5.7910469506791031,4,150,84.569980107359385,84.569980107359385,150,114.57201021863247,31.362556144870666,24.862556144870666,-230,296.17394516585443,526.17394516585443,877.4623281603881,561.75847200688884,791.75847200688884,230,567.73065119879993,337.73065119879993,null,null,5,84.569980107359385,66.607042185296493,84.569980107359385,66.607042185296493,112.02624442967422,20.642185613926593,14.142185613926593,-230,279.02237294562121,509.02237294562121,828.40408014012996,529.75645503608064,759.75645503608064,230,537.29926863504124,307.29926863504124,null,null,4,150,84.569980107359385,84.569980107359385,150,114.57201021863247,31.362556144870666,24.862556144870666,230,296.17394516585443,526.17394516585443,877.4623281603881,561.75847200688884,791.75847200688884,230,567.73065119879993,337.73065119879993,null,null,5,84.569980107359385,66.607042185296493,84.569980107359385,66.607042185296493,112.02624442967422,20.642185613926593,14.142185613926593,230,279.02237294562121,509.02237294562121,828.40408014012996,529.75645503608064,759.75645503608064,230,537.29926863504124,307.29926863504124]
[-9.9391500267859669,-8.0134292150206932,{"$f":"100/Q32*AJ32-100","v":-14.013202331996112},{"$f":"100/N32*AG32-100","v":-14.2945740718568},3.5,150,68.186102981531889,68.186102981531889,150,93.960844921529358,31.01293343949088,24.51293343949088,-180,229.64241258245499,409.64241258245499,692.02552137110092,439.13206576497157,619.13206576497157,180,457.4016984759952,277.4016984759952,null,null,5,68.186102981531889,43.021049528138605,68.186102981531889,43.021049528138605,85.735933884411125,"<20","",-180,196.81600781545697,376.81600781545694,597.07299498261204,377.59560088465184,557.59560088465184,180,398.40386146776194,218.40386146776194,null,null,3.5,150,68.186102981531889,68.186102981531889,150,93.960844921529358,31.01293343949088,24.51293343949088,180,229.64241258245499,409.64241258245499,692.02552137110092,439.13206576497157,619.13206576497157,180,457.4016984759952,277.4016984759952,null,null,5,68.186102981531889,43.021049528138605,68.186102981531889,43.021049528138605,85.735933884411125,{"$error":"#VALUE!"},{"$error":"#VALUE!"},180,196.81600781545697,376.81600781545694,597.07299498261204,377.59560088465184,557.59560088465184,180,398.40386146776194,218.40386146776194]
[-30.245275589643839,-25.24512335888673,-39.896343445191825,-40.613355801008176,3,150,57.596028683731795,57.596028683731795,150,99.839748920466135,32.413917946816952,25.913917946816952,-150,246.40234445271585,396.40234445271585,738.96736976126817,470.08179885903178,620.08179885903178,150,485.29139839254543,335.29139839254543,null,null,5,57.596028683731795,30.540832257894671,57.596028683731795,30.540832257894671,69.746313079484324,"<20","",-150,146.33008359810862,296.33008359810862,449.60955024005352,282.53634991289664,432.53634991289664,150,306.0626725238605,156.0626725238605,null,null,3,150,57.596028683731795,57.596028683731795,150,99.839748920466135,32.413917946816952,25.913917946816952,150,246.40234445271585,396.40234445271585,738.96736976126817,470.08179885903178,620.08179885903178,150,485.29139839254543,335.29139839254543,null,null,5,57.596028683731795,30.540832257894671,57.596028683731795,30.540832257894671,69.746313079484324,{"$error":"#VALUE!"},{"$error":"#VALUE!"},150,146.33008359810862,296.33008359810862,449.60955024005352,282.53634991289664,432.53634991289664,150,306.0626725238605,156.0626725238605]
[-26.413418865929145,-21.740804012005995,-35.608725498667269,-36.220567524521911,2.5,150,57.007300381040082,57.007300381040082,150,92.796659018830582,29.389432176173599,22.889432176173599,-150,225.21918945582766,375.21918945582763,679.34028997393716,430.87337792340549,580.87337792340554,150,449.60567245264343,299.60567245264343,null,null,5,57.007300381040082,29.910468807075578,57.007300381040082,29.910468807075578,68.882401272698345,"<20","",-150,143.64352086079867,293.64352086079867,441.65492815729948,277.44485953182482,427.44485953182482,150,300.98952203509731,150.98952203509731,null,null,2.5,150,57.007300381040082,57.007300381040082,150,92.796659018830582,29.389432176173599,22.889432176173599,150,225.21918945582766,375.21918945582763,679.34028997393716,430.87337792340549,580.87337792340554,150,449.60567245264343,299.60567245264343,null,null,5,57.007300381040082,29.910468807075578,57.007300381040082,29.910468807075578,68.882401272698345,{"$error":"#VALUE!"},{"$error":"#VALUE!"},150,143.64352086079867,293.64352086079867,441.65492815729948,277.44485953182482,427.44485953182482,150,300.98952203509731,150.98952203509731]
[-31.36852311805481,-25.049399420355059,-44.071412125823706,-44.622265002410465,2,150,41.093491736191538,41.093491736191538,150,71.428953477882374,27.258464372776913,20.758464372776913,-110,140.77825879340136,250.77825879340136,431.97784222372741,271.63407795468669,381.63407795468669,110,293.41500801603974,183.41500801603974,null,null,5,41.093491736191538,15.390564571665506,41.093491736191538,15.390564571665506,46.600582089512564,"<20","",-110,77.959811088830591,187.95981108883058,243.85230301326624,151.92110398509547,261.92110398509544,110,171.45757432780181,61.457574327801808,null,null,2,150,41.093491736191538,41.093491736191538,150,71.428953477882374,27.258464372776913,20.758464372776913,110,140.77825879340136,250.77825879340136,431.97784222372741,271.63407795468669,381.63407795468669,110,293.41500801603974,183.41500801603974,null,null,5,41.093491736191538,15.390564571665506,41.093491736191538,15.390564571665506,46.600582089512564,{"$error":"#VALUE!"},{"$error":"#VALUE!"},110,77.959811088830591,187.95981108883058,243.85230301326624,151.92110398509547,261.92110398509544,110,171.45757432780181,61.457574327801808]
[]
[]
[]
[null,null,null,null,"",0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"",0]
[null,null,null,null,"  Minimal",45,"Pa",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"  Minimal",20.966937088935406,"m³/h"]
[null,null,null,null,"  Maximal",305,"Pa",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"  Maximal",178.94840256083239,"m³/h"]
[]
[]
[null,null,null,null,"Baugröße 1000",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Baugröße 1000"]
[]
["Gesamtkühl","Gesamtkühl","Sensibel","Sensibel","Schieberstellung","Primärdruck","Primär- volumenstrom","Primär- volumenstrom","Primärdruck","Sekundärvolumenstrom","LWA","LA18","QPK","QSK1","QKges1","QTotal2","QSensibel,K2","QKges2","QPH","QSH","Qhges",null,null,"Schieberstellung","Primär- volumenstrom","Primärdruck","Primär- volumenstrom","Primärdruck","Sekundärvolumenstrom","LWA","LA18","QPK","QSK1","QKges1","QTotal2","QSensibel,K2","QKges2","QPH","QSH","Qhges",null,null,"Schieberstellung","Primärdruck","Primär- volumenstrom","Primär- volumenstrom","Primärdruck","Sekundärvolumenstrom","LWA","LA18","QPK","QSK1","QKges1","QTotal2","QSensibel,K2","QKges2","QPH","QSH","Qhges",null,null,"Schieberstellung","Primärdruck","Primär- volumenstrom","Primär- volumenstrom","Primärdruck","Sekundärvolumenstrom","LWA","LA18","QPK","QSK1","QKges1","QTotal2","QSensibel,K2","QKges2","QPH","QSH","Qhges"]
["2)","1)","2)","1)",null,"[Pa]","[m³/h]","[m³/h]","[Pa]","[m³/h]","[dB(A)]","[dB(A)]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]",null,null,null,"[m³/h]","[Pa]","[m³/h]","[Pa]","[m³/h]","[dB(A)]","[dB(A)]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]",null,null,null,"[Pa]","[m³/h]","[m³/h]","[Pa]","[m³/h]","[dB(A)]","[dB(A)]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]",null,null,null,"[Pa]","[m³/h]","[m³/h]","[Pa]","[m³/h]","[dB(A)]","[dB(A)]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]","[W]"]
[{"$f":"100/R48*AK48-100","v":-0.87989774887763872},{"$f":"100/O48*AH48-100","v":0.16528131346827024},{"$f":"100/Q48*AJ48-100","v":-1.2330394936975182},{"$f":"100/N48*AG48-100","v":0.28746089305552402},5,150,156.92414584057784,156.92414584057784,150,241.3887461780667,34.142504800111269,27.642504800111269,-420,568.16492486870914,988.16492486870914,1572.7882806566249,1046.4836285982083,1466.4836285982083,420,967.73099233391099,547.73099233391099,null,null,5,156.92414584057784,150.98304968518443,156.92414584057784,150.98304968518443,244.12691558264186,40.992790105852507,34.492790105852507,-420,569.79817683576493,989.79817683576493,1511.7512636027525,1033.5800721625135,1453.5800721625135,420,968.51601493515898,548.51601493515898,null,null,{"$f":"ABS(E48)","v":5},{"$f":"ABS(F48)","v":150},156.92414584057784,156.92414584057784,150,241.3887461780667,34.142504800111269,27.642504800111269,420,568.16492486870914,988.16492486870914,1572.7882806566249,1046.4836285982083,1466.4836285982083,420,967.73099233391099,547.73099233391099,null,null,{"$f":"ABS(X48)","v":5},156.92414584057784,150.98304968518443,156.92414584057784,150.98304968518443,244.12691558264186,40.992790105852507,34.492790105852507,420,569.79817683576493,989.79817683576493,1511.7512636027525,1033.5800721625135,1453.5800721625135,{"$f":"ABS(AL48)","v":420},968.51601493515898,548.51601493515898]
[{"$f":"100/R49*AK49-100","v":-4.1080066729120688},{"$f":"100/O49*AH49-100","v":-2.8032678257828962},{"$f":"100/Q49*AJ49-100","v":-5.6625135533287363},{"$f":"100/N49*AG49-100","v":-4.770225756072378},4.5,150,135.06769360779435,135.06769360779435,150,217.29607969788279,32.544343093882617,26.044343093882617,-360,513.06456622248425,873.06456622248425,1444.1497940671775,951.35146770913764,1311.3514677091375,360,892.23378670312002,532.23378670312002,null,null,5,135.06769360779435,111.35313973059246,135.06769360779435,111.35313973059246,202.23192242442519,36.285207545886934,29.785207545886934,-360,488.59022813925833,848.59022813925833,1343.0479129322998,897.48106191031593,1257.4810619103159,360,862.95652578106274,502.95652578106274,null,null,{"$f":"ABS(E49)","v":4.5},150,135.06769360779435,135.06769360779435,150,217.29607969788279,32.544343093882617,26.044343093882617,360,513.06456622248425,873.06456622248425,1444.1497940671775,951.35146770913764,1311.3514677091375,360,892.23378670312002,532.23378670312002,null,null,5,135.06769360779435,111.35313973059246,135.06769360779435,111.35313973059246,202.23192242442519,36.285207545886934,29.785207545886934,360,488.59022813925833,848.59022813925833,1343.0479129322998,897.48106191031593,1257.4810619103159,360,862.95652578106274,502.95652578106274]
[-4.6189447653095641,-2.9991958607901807,-6.4684618521333874,-5.2770357162797268,4,150,105.1968045237885,105.1968045237885,150,142.51640295488428,32.310419338652672,25.810419338652672,-280,368.67158988258944,648.67158988258939,1092.2481091434781,699.26606436909026,979.26606436909026,280,706.46449101399696,426.46449101399696,null,null,5,105.1968045237885,67.043466356651749,105.1968045237885,67.043466356651749,147.43344949301107,28.440311963837093,21.940311963837093,-280,349.21665840870889,629.21665840870889,1006.2468247194154,654.03430575046116,934.03430575046116,280,663.8937055765615,383.8937055765615,null,null,4,150,105.1968045237885,105.1968045237885,150,142.51640295488428,32.310419338652672,25.810419338652672,280,368.67158988258944,648.67158988258939,1092.2481091434781,699.26606436909026,979.26606436909026,280,706.46449101399696,426.46449101399696,null,null,5,105.1968045237885,67.043466356651749,105.1968045237885,67.043466356651749,147.43344949301107,28.440311963837093,21.940311963837093,280,349.21665840870889,629.21665840870889,1006.2468247194154,654.03430575046116,934.03430575046116,280,663.8937055765615,383.8937055765615]
[-10.135640558015766,-7.6337054399527347,-14.391825681829715,-13.76352593128486,3.5,150,84.816859806295767,84.816859806295767,150,116.87812417068287,31.960796633272889,25.460796633272889,-230,286.42800448591322,516.42800448591322,863.14843547673149,547.71990891567282,777.71990891567282,230,574.07489064829372,344.07489064829372,null,null,5,84.816859806295767,43.302933023864398,84.816859806295767,43.302933023864398,112.43567512353356,21.681540555376021,15.181540555376021,-230,247.00541181403278,477.00541181403275,733.09728925230593,468.89301439985263,698.89301439985263,230,499.22467751707211,269.22467751707211,null,null,3.5,150,84.816859806295767,84.816859806295767,150,116.87812417068287,31.960796633272889,25.460796633272889,230,286.42800448591322,516.42800448591322,863.14843547673149,547.71990891567282,777.71990891567282,230,574.07489064829372,344.07489064829372,null,null,5,84.816859806295767,43.302933023864398,84.816859806295767,43.302933023864398,112.43567512353356,21.681540555376021,15.181540555376021,230,247.00541181403278,477.00541181403275,733.09728925230593,468.89301439985263,698.89301439985263,230,499.22467751707211,269.22467751707211]
[-30.164815232192268,-24.808038235962243,-39.944049367196762,-40.15156508370071,3,150,71.643840557812723,71.643840557812723,150,124.19090719375056,33.361781140598957,26.861781140598957,-190,307.19972739041879,497.19972739041879,921.30038391188805,586.0699125304144,776.0699125304144,190,607.50784664348589,417.50784664348589,null,null,5,71.643840557812723,30.740942591176925,71.643840557812723,30.740942591176925,91.133793461581604,"<20","",-190,183.85422891030362,373.85422891030362,555.31955353095486,351.9698573429788,541.9698573429788,190,387.72784943296426,197.72784943296426,null,null,3,150,71.643840557812723,71.643840557812723,150,124.19090719375056,33.361781140598957,26.861781140598957,190,307.19972739041879,497.19972739041879,921.30038391188805,586.0699125304144,776.0699125304144,190,607.50784664348589,417.50784664348589,null,null,5,71.643840557812723,30.740942591176925,71.643840557812723,30.740942591176925,91.133793461581604,{"$error":"#VALUE!"},{"$error":"#VALUE!"},190,183.85422891030362,373.85422891030362,555.31955353095486,351.9698573429788,541.9698573429788,190,387.72784943296426,197.72784943296426]
[-26.36400811815821,-21.330213851795946,-35.683793761536251,-35.755816547291062,2.5,150,70.911519986171811,70.911519986171811,150,115.42999048683804,30.337295369955608,23.837295369955608,-190,280.94081872273068,470.94081872273068,847.41632237357612,537.47604656650128,727.47604656650128,190,564.60548569846515,374.60548569846515,null,null,5,70.911519986171811,30.106448858669186,70.911519986171811,30.106448858669186,89.983566103877408,"<20","",-190,180.48813497377355,370.48813497377353,545.66177779169027,345.68420259205243,535.68420259205243,190,381.54561739313965,191.54561739313965,null,null,2.5,150,70.911519986171811,70.911519986171811,150,115.42999048683804,30.337295369955608,23.837295369955608,190,280.94081872273068,470.94081872273068,847.41632237357612,537.47604656650128,727.47604656650128,190,564.60548569846515,374.60548569846515,null,null,5,70.911519986171811,30.106448858669186,70.911519986171811,30.106448858669186,89.983566103877408,{"$error":"#VALUE!"},{"$error":"#VALUE!"},190,180.48813497377355,370.48813497377353,545.66177779169027,345.68420259205243,535.68420259205243,190,381.54561739313965,191.54561739313965]
[-31.143949430048821,-24.631494077416278,-43.992549994741658,-44.238964225997314,2,150,51.116294598677278,51.116294598677278,150,88.850649448097599,28.206327566558922,21.706327566558922,-140,175.87221322827486,315.87221322827486,539.6635803611922,339.34846820503316,479.34846820503316,140,372.67343071769261,232.67343071769261,null,null,5,51.116294598677278,15.491406977656034,51.116294598677278,15.491406977656034,60.389472650404464,"<20","",-140,98.068167734748613,238.06816773474861,303.53143441856383,190.06042367354394,330.06042367354394,140,221.36066838554848,81.360668385548479,null,null,2,150,51.116294598677278,51.116294598677278,150,88.850649448097599,28.206327566558922,21.706327566558922,140,175.87221322827486,315.87221322827486,539.6635803611922,339.34846820503316,479.34846820503316,140,372.67343071769261,232.67343071769261,null,null,5,51.116294598677278,15.491406977656034,51.116294598677278,15.491406977656034,60.389472650404464,{"$error":"#VALUE!"},{"$error":"#VALUE!"},140,98.068167734748613,238.06816773474861,303.53143441856383,190.06042367354394,330.06042367354394,140,221.36066838554848,81.360668385548479]
[]
[]
[]
[null,null,null,null,"",null,null,null,null,null,null,null,null,"DpK =",33.328818321761396,"[kPa]"]
[null,null,null,null,"  Minimal",45,"Pa",null,null,null,null,null,null,"DpH =",1.8,"[kPa]"]